## RTM
Alpilla 600 MW Combined Cycle Power Plant - Requirements Traceability Matrix
engine requirements_matrix v1.0.0 ¦ generated 2026-09-27T17:46:40Z by SETUP ¦ data b226b6c9cd57c954
ID | Section | Title | Requirement | Discipline | Verification | Acceptance | Guarantee | Guaranteed value | Traced by (database records) | Traced | Status
ER-01.01 | ER-01 General requirements and plant description | Purpose of the Works | The Contractor shall design, engineer, procure, manufacture, deliver, construct, erect, commission, test and hand over a complete, safe and fully operational natural-gas-fired combined cycle power plant of 600 MW net output at Site Reference Conditions (the Works), ready for commercial operation in the Turkish electricity market. | general | review | Taking-Over Certificate issued |  |  |  | no | contractual
ER-01.02 | ER-01 General requirements and plant description | Plant configuration | The plant shall be a 1x1 multi-shaft combined cycle block comprising one heavy-duty H-class (or equivalent advanced class) gas turbine with its own generator, one triple-pressure reheat heat recovery steam generator (HRSG) with selective catalytic reduction (SCR) and CO catalyst, and one reheat condensing steam turbine with its own generator, cooled by once-through seawater. | process | review | Configuration as described in the approved Basic Design Package |  |  |  | no | contractual
ER-01.03 | ER-01 General requirements and plant description | Design life and operating regime | All equipment and structures shall be designed for an economic life of 30 years, 8,000 equivalent operating hours per year and up to 250 starts per year (of which up to 50 cold, 100 warm and 100 hot starts), including daily cycling and load following. | general | analysis | Design life documented in design reports and OEM statements |  |  | design_parameter/DP-CASE-0034 design_parameter/DP-CASE-0035 design_parameter/DP-CASE-0036 | yes | contractual
ER-01.04 | ER-01 General requirements and plant description | Turnkey completeness | The Works shall include everything necessary for safe, reliable and efficient operation whether or not expressly mentioned in the Contract (fit-for-purpose obligation), except the items expressly allocated to the Owner in Appendix D (scope split). | general | review |  |  |  |  | no | contractual
ER-01.05 | ER-01 General requirements and plant description | Units and language | SI units shall be used throughout (pressure in bar(g)/bar(a), temperature in degC). All documents, drawings and labels shall be in English; operator-facing labels and safety signs shall be bilingual English/Turkish. | general | review |  |  |  |  | no | contractual
ER-01.06 | ER-01 General requirements and plant description | Plant identification system | All systems, equipment, instruments, cables and documents shall be identified according to KKS (VGB-B 105/106). The tag data shall be classified according to the AVEVA class library adopted by the Owner and delivered through the Owner's engineering database. | general | review | 100 % of delivered tags classified and validated in the Owner's database |  |  |  | no | contractual
ER-01.07 | ER-01 General requirements and plant description | Codes and standards hierarchy | The Works shall comply with (in order of precedence): Turkish laws and regulations; the Grid Code of the TSO; the Contract; the codes and standards listed in Appendix A.19; and good industry practice. Where codes conflict the more stringent requirement applies. | general | review |  |  |  |  | no | contractual
ER-01.08 | ER-01 General requirements and plant description | Proven technology | Major equipment (GT, ST, generators, HRSG, GSU transformers) shall be of a design with at least two units of the same frame in commercial operation for not less than 8,000 fired hours each at the date of the Contract, or supported by a validation programme accepted by the Owner. | general | review | Reference list accepted by the Owner |  |  |  | no | contractual
ER-01.09 | ER-01 General requirements and plant description | Design responsibility | The Contractor is fully responsible for the design, including the verification of all Owner-provided data. Review or approval of documents by the Owner or the Engineer does not relieve the Contractor of any obligation. | general | review |  |  |  |  | no | contractual
ER-01.10 | ER-01 General requirements and plant description | Engineering database and data handover | The Contractor shall deliver all engineering data (equipment, lines, instruments, cables, documents, design parameters) in the Owner's engineering database format, kept current at each document issue, and hand over native CAD/3D models (Plant 3D or E3D) and IFC4 exports. | general | review | Data handover accepted at Taking-Over |  |  |  | no | contractual
ER-02.01 | ER-02 Site conditions and design data | Site location and area | The Site is a 12.0 ha plot (400 m east-west x 300 m north-south) on the northern Marmara coast, levelled by the Owner to +15.0 m, plant grid origin at the south-west corner, plant north = true north. The usable area inside the 10 m stream-channel buffer on the west boundary and the 5 m landscaping strip is about 10.6 ha (E 20-395, N 12-295); the 60 m public coastal strip lies between the plot and the shoreline. A further 5.04 ha temporary construction area north of the plot (E 0-180, N 320-600) is provided by the Owner (tie-in TP-A1). Details and existing features per ALP-OWN-GEN-001 and drawings ALP-OWN-DWG-001 (external connections) and ALP-OWN-DWG-002 (site and construction area plan). | civil | inspection |  |  |  | design_parameter/DP-CASE-0001 design_parameter/DP-OWNR-0044 | yes | contractual
ER-02.02 | ER-02 Site conditions and design data | Ambient design range | Equipment shall operate at full capability between -8 degC and +40 degC dry bulb and 18 % to 100 % relative humidity, and survive -15 degC to +45 degC. Climatic data per ALP-OWN-MET-001 (10-year site record; extremes -11.4 degC / +39.6 degC). | process | analysis |  |  |  | design_parameter/DP-CASE-0007 design_parameter/DP-CASE-0008 design_parameter/DP-CASE-0009 | yes | contractual
ER-02.03 | ER-02 Site conditions and design data | Site Reference Conditions (SRC) | Guarantees refer to: ambient dry-bulb temperature 15.0 degC; relative humidity 70 %; barometric pressure 1011.5 mbar; seawater temperature at intake 16.0 degC (contractual reference; the measured annual mean of 15.4 degC in ALP-OWN-MAR-001 applies to the design range only); natural gas per ER-03.02 reference composition; grid frequency 50.0 Hz; power factor 0.85 lagging. | process | review |  |  |  | design_parameter/DP-CASE-0010 design_parameter/DP-CASE-0011 design_parameter/DP-CASE-0012 design_parameter/DP-CASE-0014 | yes | contractual
ER-02.04 | ER-02 Site conditions and design data | Seawater conditions | Seawater quality, temperature and marine conditions per ALP-OWN-MAR-001 (two-layer sea, pycnocline at 20 m to 25 m). Design range at the intake depth 6.9 degC to 27.0 degC, chloride up to 14,500 mg/l, TSS up to 140 mg/l in storms, occasional H2S in the lower layer, mussel settlement, jellyfish blooms up to 20 kg/m3 and mucilage events. | process | analysis |  |  |  | design_parameter/DP-CASE-0013 | yes | contractual
ER-02.05 | ER-02 Site conditions and design data | Wind, snow and rain | Basic wind speed 30 m/s (10 min mean, 10 m height, 50-year return); ground snow load 0.75 kN/m2; design rainfall intensity 110 mm/h (10 min, 25-year return) for drainage design. | civil | analysis |  |  |  | design_parameter/DP-CASE-0004 design_parameter/DP-CASE-0005 design_parameter/DP-CASE-0006 | yes | contractual
ER-02.06 | ER-02 Site conditions and design data | Seismic design | The Site is in a high seismic hazard region. Structures and equipment shall be designed per the Turkish Building Earthquake Code (TBDY 2018) with a site-specific hazard study; design earthquake DD-2 (475-year) peak ground acceleration 0.45 g; building importance factor 1.5 for power block structures; functional recovery of critical systems after DD-3 events. | structural | analysis | Seismic design report approved; site-specific hazard study delivered |  |  | design_parameter/DP-CASE-0002 | yes | contractual
ER-02.07 | ER-02 Site conditions and design data | Geotechnical conditions | Owner-provided baseline investigation indicates alluvial deposits over weathered rock at 18 m to 25 m depth, groundwater at +13.5 m and liquefaction potential in the upper sand layers. The Contractor shall perform confirmatory investigations and select foundation solutions (piling or ground improvement) accordingly. | civil | analysis |  |  |  |  | no | contractual
ER-02.08 | ER-02 Site conditions and design data | Corrosive coastal atmosphere | Outdoor equipment and structures shall be designed for corrosivity category C5 (ISO 12944-2) with a coating system of high durability (H, more than 15 years to first major maintenance). | mechanical | inspection |  |  |  | design_parameter/DP-CASE-0003 | yes | contractual
ER-02.09 | ER-02 Site conditions and design data | Flood protection | Finished floor levels of all buildings and equipment foundations shall be at least 0.5 m above the 100-year coastal flood level including a sea-level-rise allowance of 0.5 m. | civil | analysis |  |  |  |  | no | contractual
ER-02.10 | ER-02 Site conditions and design data | Airborne salt and dust | The plant shall be designed for the airborne contaminants in ALP-OWN-MET-001 section 6: sea-salt aerosol up to 165 ug/m3 (as NaCl) during lodos storms, chloride deposition up to 420 mg/m2 per day, PM10 up to 260 ug/m3. The gas turbine inlet air filtration shall keep sodium plus potassium at the compressor inlet within the OEM limit for all these conditions, including high-humidity and fog (coalescer/droplet separator stage upstream of the fine filters, hydrophobic final filters of class E12 or better). Outdoor electrical equipment: creepage distance for very heavy pollution (IEC 60815, 31 mm/kV). | mechanical | analysis | Filter design report with OEM confirmation (Na+K at compressor inlet below OEM limit at 165 ug/m3 NaCl); Na+K air sampler downstream of the filters with 12 months of data reported during the Defects Notification Period |  |  | design_parameter/DP-OWNR-0005 design_parameter/DP-OWNR-0007 design_parameter/DP-OWNR-0008 | yes | contractual
ER-02.11 | ER-02 Site conditions and design data | Design ambient points | HVAC and cooling design: summer 0.4 % 32.8 degC / 48 % RH; freeze protection and heating: winter 99.6 % -4.8 degC; performance test ambient range 5 degC to 30 degC (ALP-OWN-MET-001 sections 3 and 7). Heat tracing for all outdoor water-filled lines and instruments. | hvac | review |  |  |  | design_parameter/DP-OWNR-0001 design_parameter/DP-OWNR-0002 design_parameter/DP-OWNR-0010 | yes | contractual
ER-02.12 | ER-02 Site conditions and design data | Lightning | Lightning protection per IEC 62305 with a risk assessment based on 26 thunderstorm days per year and ground flash density 2.4 flashes/km2/year (ALP-OWN-MET-001 section 5). | electrical | analysis |  |  |  | design_parameter/DP-OWNR-0009 | yes | contractual
ER-02.13 | ER-02 Site conditions and design data | Existing features on the Site | The Contractor shall demolish and remove the abandoned warehouse foundations (E 300-360, N 20-60), protect the Owner's meteorological mast and groundwater wells, and keep clear of the buried 11 kV cable along the east boundary until the Owner has had it relocated (ALP-OWN-GEN-001 section 2). | civil | inspection |  |  |  |  | no | contractual
ER-02.14 | ER-02 Site conditions and design data | Access and transport | The Contractor is responsible for the transport of all plant to Site, including route surveys, permits for abnormal loads and temporary works, taking into account the 120 t bridge limits on the state road (ALP-OWN-GEN-001 section 3). Heavy components shall be landed through a temporary barge landing on the public coastal strip, designed, built, operated and removed by the Contractor; the Owner obtains the coastal permit (tie-in TP-M1). | civil | review |  |  |  | design_parameter/DP-OWNR-0045 | yes | contractual
ER-03.01 | ER-03 Fuel | Fuels | Primary fuel: pipeline natural gas per ALP-OWN-FUL-001. Secondary (back-up) fuel: light diesel oil (LDO) per ALP-OWN-FUL-002, for up to 500 hours per year. The gas turbine shall be dual-fuel with automatic transfer between fuels. | process | review |  |  |  |  | no | contractual
ER-03.02 | ER-03 Fuel | Natural gas specification | The plant shall operate on the full natural gas range of ALP-OWN-FUL-001 sections 2 to 4: CH4 85.0 to 98.5 mol %, C2H6 up to 7.0 %, C3H8 up to 2.5 %, C4 up to 1.0 %, C5+ up to 0.2 %, N2 up to 4.0 %, CO2 up to 2.5 %, O2 up to 0.02 %; LHV 44.2 MJ/kg to 50.0 MJ/kg (emission limits apply over the whole range; performance guarantees at the reference gas); Wobbe index (GCV) 47.2 MJ/Sm3 to 51.8 MJ/Sm3 with rate of change up to 1 %/min. Hydrogen admixture up to 5 vol % without modification and with all guarantees; provisions for 10 vol % by future OEM retrofit (fuel system materials, gas detection, control system capacity). Reference composition for guarantees: CH4 93.0, C2H6 3.5, C3H8 0.8, i-C4 0.15, n-C4 0.15, C5+ 0.05, N2 1.55, CO2 0.8 mol %; LHV 48.4 MJ/kg. | process | analysis | OEM fuel specification compliance statement for the full range |  |  | design_parameter/DP-CASE-0018 design_parameter/DP-CASE-0019 design_parameter/DP-CASE-0020 design_parameter/DP-CASE-0021 design_parameter/DP-OWNR-0024 | yes | contractual
ER-03.03 | ER-03 Fuel | Gas supply conditions at terminal point | Pressure at the terminal point TP-G1: normal 55-65 barg, minimum 45 barg for full load, exceptional 40 barg for up to 72 h/year; temperature 5-25 degC (ALP-OWN-FUL-001 section 6). No gas compressor is provided: between 40 and 45 barg the gas turbine operates on gas at the pressure-limited load (about 60 % GT load at 40 barg); below 40 barg the control system transfers automatically to LDO (ER-03.10). | process | analysis |  |  |  | design_parameter/DP-CASE-0022 design_parameter/DP-CASE-0023 | yes | contractual
ER-03.04 | ER-03 Fuel | Gas receiving and fiscal metering station | 2x100 % filtration/separation, 2x100 % water-bath or electric heaters, 2x100 % pressure-reduction streams with active/monitor regulators and slam-shut valves; fiscal metering with 2x100 % ultrasonic meters (OIML R137 accuracy class 0.5), on-line gas chromatograph and flow computers complying with the network operator's requirements. | mechanical | inspection |  |  |  |  | no | contractual
ER-03.05 | ER-03 Fuel | Performance fuel gas heating | The GT fuel gas shall be preheated with intermediate-pressure feedwater to the OEM-optimised temperature (about 200 degC) to maximise combined cycle efficiency; a start-up heater shall be provided. | process | review |  |  |  |  | no | contractual
ER-03.06 | ER-03 Fuel | Natural gas contaminant limits | At the gas turbine fuel skid inlet the gas shall meet the OEM limits and at least: total sulphur <= 30 mg S/Sm3; H2S + COS <= 5 mg/Sm3; mercury <= 1 ug/Sm3; sodium + potassium, lead, vanadium and calcium within the OEM trace-metal limits (network data below 0.005 mg/Sm3, not guaranteed by the network operator); no free liquids; particulates removed to the OEM limit (coalescing filter-separators, 3 um absolute final filtration); superheat at least 28 K above the hydrocarbon and water dew points at all loads. The Contractor shall provide continuous monitoring of H2S and total sulphur and periodic sampling points for trace metals and mercury. | process | test | Gas conditioning design and commissioning samples within limits |  |  | design_parameter/DP-OWNR-0025 design_parameter/DP-OWNR-0026 design_parameter/DP-OWNR-0027 design_parameter/DP-OWNR-0028 design_parameter/DP-OWNR-0029 | yes | contractual
ER-03.07 | ER-03 Fuel | Light diesel oil specification and burner limits | LDO as delivered per ALP-OWN-FUL-002 (TS EN 590 based: density 820-845 kg/m3, viscosity 2.0-4.5 mm2/s at 40 degC, flash point >= 55 degC, sulphur <= 10 mg/kg, water <= 200 mg/kg, ash <= 0.01 %, FAME <= 7 %, LHV 42.6-43.2 MJ/kg). At the gas turbine fuel inlet: Na + K <= 0.5 mg/kg, vanadium <= 0.5 mg/kg, lead <= 1.0 mg/kg, calcium <= 2.0 mg/kg, water <= 100 mg/kg, filtration to 5 um, or stricter OEM limits. | process | test | Fuel samples at GT inlet within limits during LDO tests |  |  | design_parameter/DP-OWNR-0034 design_parameter/DP-OWNR-0035 design_parameter/DP-OWNR-0036 design_parameter/DP-OWNR-0037 | yes | contractual
ER-03.08 | ER-03 Fuel | LDO unloading and storage | Road tanker unloading station with 4 bays (metering, strainers, spill containment, earthing), and two vertical fixed-roof storage tanks each of 3,500 m3 net working volume (together 72 hours of base-load operation on LDO; heel and fire-fighting reserves in addition), in a bund of 110 % of the largest tank, with foam fire protection per NFPA 11 and NFPA 30, level/leak monitoring and water draw-off. Operation beyond the storage autonomy is not required (resupply is limited to 25 trucks/day). | mechanical | inspection |  |  |  | design_parameter/DP-OWNR-0038 | yes | contractual
ER-03.09 | ER-03 Fuel | LDO forwarding and treatment | 2 x 100 % forwarding pumps, duplex filters, flow metering, and a mandatory fuel treatment system of 2 x 100 % centrifugal separators with water washing, sized to reduce Na+K from 1.8 mg/kg to below the ER-03.07 limit at the gas turbine inlet. | mechanical | test |  |  |  |  | no | contractual
ER-03.10 | ER-03 Fuel | Fuel transfer and LDO start | Automatic transfer from gas to LDO on loss of gas supply pressure, from any load between minimum environmental load and base load, without unit trip; manual on-load transfer back to gas; black start is not required but start-up on LDO with grid power shall be possible. Purging and liquid fuel system recirculation to avoid coking during gas operation. | i_and_c | demonstration | Automatic transfer demonstrated at 50 % and 100 % load | PG-18 | >= 100 % successful transfers |  | no | contractual
ER-03.11 | ER-03 Fuel | NOx control and SCR on LDO | NOx on LDO shall be controlled by water injection (demineralised water) and the SCR; the SCR and ammonia system shall be designed for LDO operation (sulphur 10 mg/kg, ammonium bisulphate risk at the cold end). | process | test |  | PG-17 | <= 50 mg/Nm3 |  | no | contractual
ER-04.01 | ER-04 Performance and operational requirements | Net electrical output | Guaranteed net electrical output at SRC: not less than 600.0 MW at the 380 kV terminal point. | process | test | >= 600.0 MW corrected to SRC | PG-01 | >= 600 MW | design_parameter/DP-CASE-0028 | yes | contractual
ER-04.02 | ER-04 Performance and operational requirements | Net heat rate | Guaranteed net heat rate at SRC: not more than 5,860 kJ/kWh (LHV), corresponding to a net efficiency of about 61.4 %. | process | test | <= 5,860 kJ/kWh corrected to SRC | PG-02 | <= 5860 kJ/kWh | design_parameter/DP-CASE-0029 | yes | contractual
ER-04.03 | ER-04 Performance and operational requirements | Part-load efficiency | Net heat rate at 60 % plant load shall not exceed 6,250 kJ/kWh (LHV) at SRC. | process | test | <= 6,250 kJ/kWh | PG-03 | <= 6250 kJ/kWh | design_parameter/DP-CASE-0030 | yes | contractual
ER-04.04 | ER-04 Performance and operational requirements | Start-up times | From GT ignition to base load: hot start (shutdown < 8 h) <= 45 min; warm start (8 h to 48 h) <= 90 min; cold start (> 48 h) <= 180 min, without exceeding the life consumption limits agreed with the OEM. | process | demonstration | Hot start <= 45 min demonstrated three times | PG-09 | <= 45 min | design_parameter/DP-CASE-0037 design_parameter/DP-CASE-0038 design_parameter/DP-CASE-0039 | yes | contractual
ER-04.05 | ER-04 Performance and operational requirements | Load ramp rate | Combined cycle load ramp rate of at least 35 MW/min between minimum environmental load and base load. | i_and_c | demonstration | >= 35 MW/min | PG-10 | >= 35 MW/min | design_parameter/DP-CASE-0032 | yes | contractual
ER-04.06 | ER-04 Performance and operational requirements | Minimum environmental load | Stable emissions-compliant operation shall be possible down to 40 % of plant net output or lower. | process | demonstration | <= 40 % | PG-11 | <= 40 % of plant net output | design_parameter/DP-CASE-0033 | yes | contractual
ER-04.07 | ER-04 Performance and operational requirements | Frequency and voltage support | The plant shall provide primary and secondary frequency control, fast frequency response and reactive power support as required by the Grid Code, including operation within 47.5 Hz to 52.5 Hz for the durations specified therein. | electrical | test | Grid Code compliance tests accepted by the TSO |  |  | design_parameter/DP-CASE-0026 | yes | contractual
ER-04.08 | ER-04 Performance and operational requirements | Reactive capability | Each generator shall be capable of power factor 0.85 lagging to 0.95 leading at rated active power at the generator terminals. | electrical | test |  |  |  | design_parameter/DP-CASE-0027 | yes | contractual
ER-04.09 | ER-04 Performance and operational requirements | House load and island operation | The unit shall survive a full load rejection to house load and remain in stable operation for at least 60 minutes. | i_and_c | demonstration |  |  |  |  | no | contractual
ER-04.10 | ER-04 Performance and operational requirements | Auxiliary power | Auxiliary power consumption at base load shall not exceed 2.2 % of gross output; the value is included in the net output guarantee. | electrical | test |  |  |  | design_parameter/DP-CASE-0031 | yes | contractual
ER-04.11 | ER-04 Performance and operational requirements | Degradation | The Contractor shall submit recoverable and non-recoverable degradation curves for output and heat rate over 48,000 EOH; they apply for test corrections. | process | review |  |  |  |  | no | contractual
ER-04.12 | ER-04 Performance and operational requirements | Availability target | The design shall support an equivalent availability factor of at least 93 % averaged over the first six years, considering the OEM maintenance programme. | general | analysis |  |  |  |  | no | contractual
ER-05.01 | ER-05 Gas turbine | Gas turbine type | Heavy-duty, single-shaft, 50 Hz, H-class (or equivalent) gas turbine with dry low-NOx combustion capable of the fuel range in ER-03.02. | mechanical | review |  |  |  |  | no | contractual
ER-05.02 | ER-05 Gas turbine | Inlet air system | Three-stage static air filtration (coastal environment, final stage EPA E12 per EN 1822), anti-icing, evaporative cooler provision, silencer. | mechanical | inspection |  |  |  |  | no | contractual
ER-05.03 | ER-05 Gas turbine | Combustion dynamics monitoring | On-line combustion dynamics monitoring with automatic tuning shall be provided. | i_and_c | demonstration |  |  |  |  | no | contractual
ER-05.04 | ER-05 Gas turbine | Enclosure and ventilation | Acoustic enclosure with ventilation, gas detection and fire suppression suitable for the hazardous area classification. | mechanical | inspection |  |  |  |  | no | contractual
ER-05.05 | ER-05 Gas turbine | Compressor washing | On-line and off-line compressor washing systems with detergent skid. | mechanical | inspection |  |  |  |  | no | contractual
ER-05.06 | ER-05 Gas turbine | Condition monitoring and remote diagnostics | Vibration, performance and combustion monitoring with secure remote diagnostic access for the OEM (IEC 62443 compliant). | i_and_c | review |  |  |  |  | no | contractual
ER-05.07 | ER-05 Gas turbine | Maintenance intervals | Hot gas path inspection interval shall be not less than 25,000 EOH and major inspection not less than 50,000 EOH at the operating regime of ER-01.03. | mechanical | review |  |  |  |  | no | contractual
ER-06.01 | ER-06 Heat recovery steam generator | HRSG type | Horizontal-gas-flow, triple-pressure, reheat, natural-circulation HRSG, designed for fast cycling (Benson or equivalent HP section acceptable). | mechanical | review |  |  |  |  | no | contractual
ER-06.02 | ER-06 Heat recovery steam generator | Design code | Pressure parts per ASME Section I or EN 12952, PED 2014/68/EU conformity assessment by a notified body. | mechanical | inspection | PED certificates delivered |  |  |  | no | contractual
ER-06.03 | ER-06 Heat recovery steam generator | SCR and CO catalyst | In-duct SCR with aqueous ammonia (< 25 %) injection and an oxidation catalyst sized for the emission guarantees at end of catalyst life (24,000 h). | process | test |  | PG-04 | <= 30 mg/Nm3 |  | no | contractual
ER-06.04 | ER-06 Heat recovery steam generator | Ammonia system | Aqueous ammonia storage (2x7 days at base load), unloading, vaporisation and dosing with leak detection and bunding. | process | inspection |  |  |  |  | no | contractual
ER-06.05 | ER-06 Heat recovery steam generator | Cycling capability | The HRSG shall withstand the start regime of ER-01.03 without drum or header fatigue beyond design life (fatigue analysis per EN 12952-3). | mechanical | analysis |  |  |  |  | no | contractual
ER-06.06 | ER-06 Heat recovery steam generator | Stack | Steel stack 65 m high (EIA decision ALP-OWN-ENV-001), with CEMS platform, sampling ports per EN 15259 and aviation lighting. | structural | inspection |  |  |  | design_parameter/DP-CASE-0043 | yes | contractual
ER-06.07 | ER-06 Heat recovery steam generator | Drains and blowdown | Continuous and intermittent blowdown, HRSG drains recovery to the condenser where water quality permits. | process | review |  |  |  |  | no | contractual
ER-06.08 | ER-06 Heat recovery steam generator | Preservation | Dry and wet lay-up systems (nitrogen capping and dehumidified air) for long shutdowns. | process | inspection |  |  |  |  | no | contractual
ER-07.01 | ER-07 Steam turbine and condenser | Steam turbine | Reheat condensing steam turbine with HP, IP and LP sections, axial or side exhaust, 50 Hz, with HP/IP/LP bypass systems of 100 % capacity. | mechanical | review |  |  |  |  | no | contractual
ER-07.02 | ER-07 Steam turbine and condenser | Main steam conditions | HP live steam about 170 bar(a)/600 degC and hot reheat about 600 degC at base load, as optimised by the OEM. | process | review |  |  |  |  | no | contractual
ER-07.03 | ER-07 Steam turbine and condenser | Condenser | Single-shell or two-shell surface condenser with titanium tubes (Grade 2, welded) and titanium-clad tube sheets, divided water boxes for on-load cleaning of one half, and an automatic ball-type tube cleaning system. | mechanical | inspection |  |  |  |  | no | contractual
ER-07.04 | ER-07 Steam turbine and condenser | Cooling water temperature rise | Temperature rise across the condenser shall not exceed 7 K at base load. | process | test | <= 7 K | PG-13 | <= 7 K | design_parameter/DP-CASE-0015 | yes | contractual
ER-07.05 | ER-07 Steam turbine and condenser | Vacuum system | 2x100 % liquid-ring vacuum pumps (holding) plus hogging capability for fast start-up. | mechanical | inspection |  |  |  |  | no | contractual
ER-07.06 | ER-07 Steam turbine and condenser | Lube and control oil | Fire-resistant control fluid, lube oil system with 2x100 % AC pumps, DC emergency pump and oil purification. | mechanical | inspection |  |  |  |  | no | contractual
ER-07.07 | ER-07 Steam turbine and condenser | Condenser design standard | Thermal design per HEI Standards for Steam Surface Condensers (11th edition or later): cleanliness factor 0.85, 5 % tube plugging margin, tube velocity 1.8 m/s to 2.2 m/s, titanium wall per HEI. Hotwell storage at least 3 minutes of maximum condensate flow; dissolved oxygen at hotwell outlet <= 20 ug/l in normal operation. | process | analysis | Condenser datasheet and HEI calculation approved |  |  | design_parameter/DP-OWNR-0022 design_parameter/DP-OWNR-0023 | yes | contractual
ER-07.08 | ER-07 Steam turbine and condenser | Condenser pressure | Design condenser pressure at base load and Site Reference Conditions (seawater 16.0 degC, 7 K rise): not more than 36 mbar(a). At the maximum seawater temperature (27.0 degC) the plant shall run at base load without load limitation; the back-pressure shall stay within the steam turbine continuous limits with margin to the alarm value. | process | test | Design requirement (condenser datasheet and HEI calculation); contractual compliance through PG-02; ASME PTC 12.2 test for information |  |  | design_parameter/DP-OWNR-0021 | yes | contractual
ER-07.09 | ER-07 Steam turbine and condenser | Steam bypass to the condenser | The condenser shall accept 100 % HP/IP/LP bypass steam at the maximum steam flow (including cold-ambient and LDO cases) with desuperheating, dump-device design per HEI, and protection against shell overheating and tube erosion. | mechanical | analysis |  |  |  |  | no | contractual
ER-07.10 | ER-07 Steam turbine and condenser | Condenser leak detection and protection | Cation conductivity measurement per water box half and in the hotwell with automatic alarm and isolation logic for seawater ingress; water boxes rubber-lined with impressed-current cathodic protection; air in-leakage allowance and vacuum pump sizing per HEI. | i_and_c | test |  |  |  |  | no | contractual
ER-07.11 | ER-07 Steam turbine and condenser | Circulating water flow | Circulating water flow for the design heat duty at 7 K rise (indicatively 43,000 m3/h to 47,000 m3/h, to be confirmed by the Contractor); CW system hydraulic transient analysis including pump trip and valve closure. | process | analysis |  |  |  |  | no | contractual
ER-08.01 | ER-08 Cooling water system | Once-through seawater cooling | Offshore intake head above the pycnocline at about -12 m (at least 3 m above seabed, about 650 m offshore) with velocity cap and intake velocity <= 0.15 m/s; intake pipelines; pump house; outfall diffuser at least 250 m from the intake discharging into the upper layer (ALP-OWN-MAR-001 section 6). | civil | inspection |  |  |  |  | no | contractual
ER-08.02 | ER-08 Cooling water system | Screening | Bar screens, 2x100 % travelling band screens with fish return system, trash rakes. | mechanical | inspection |  |  |  |  | no | contractual
ER-08.03 | ER-08 Cooling water system | Circulating water pumps | 2x50 % vertical CW pumps with a common spare pump assembly stored on Site; materials suitable for seawater (duplex). | mechanical | test |  |  |  |  | no | contractual
ER-08.04 | ER-08 Cooling water system | Biofouling control | Electro-chlorination with intermittent/shock dosing; residual chlorine at outfall <= 0.1 mg/l. | process | test | <= 0.1 mg/l residual chlorine |  |  | design_parameter/DP-CASE-0017 | yes | contractual
ER-08.05 | ER-08 Cooling water system | Thermal plume | The outfall shall limit the temperature excess to <= 3 K at the edge of the 100 m mixing zone. | process | test | <= 3 K | PG-14 | <= 3 K | design_parameter/DP-CASE-0016 | yes | contractual
ER-08.06 | ER-08 Cooling water system | Closed cooling water | Closed cooling water circuit for auxiliaries with 2x100 % plate heat exchangers (titanium plates) and 2x100 % pumps. | mechanical | inspection |  |  |  |  | no | contractual
ER-08.07 | ER-08 Cooling water system | Jellyfish and mucilage | Screens, trash rakes and screen wash shall remain operable at jellyfish loads up to 20 kg/m3 and during mucilage events; the CW system shall allow operation at reduced flow with automatic load reduction rather than trip. | mechanical | demonstration |  |  |  | design_parameter/DP-OWNR-0019 | yes | contractual
ER-09.01 | ER-09 Water treatment and effluents | Raw water | Seawater reverse osmosis (2 x 100 %) with ultrafiltration pre-treatment (raw SDI15 > 5), designed for the upper-layer quality of ALP-OWN-MAR-001 including boron removal for demineralisation feed. | process | test |  |  |  |  | no | contractual
ER-09.02 | ER-09 Water treatment and effluents | Demineralised water | Two-pass RO plus electrodeionisation, 2 x 100 %, conductivity < 0.1 uS/cm, silica < 10 ug/l, with capacity for continuous water injection at 50 % load on LDO; demineralised water storage 2 x 1,250 m3 (3 days of cycle make-up plus about 24 h of water injection); connection point for mobile demin trailers. | process | test |  |  |  |  | no | contractual
ER-09.03 | ER-09 Water treatment and effluents | Cycle chemistry | Water/steam chemistry per VGB-S-010 (all-volatile treatment, oxygenated where applicable) with on-line analysers and sampling panel. | process | review |  |  |  |  | no | contractual
ER-09.04 | ER-09 Water treatment and effluents | Condensate polishing | Full-flow condensate polishing for start-up and seawater ingress events. | process | inspection |  |  |  |  | no | contractual
ER-09.05 | ER-09 Water treatment and effluents | Waste water | Neutralisation, oil separation and treatment of process wastewater, and a packaged biological treatment plant with UV disinfection for sanitary wastewater (no municipal sewer), so that all effluents meet the Turkish Water Pollution Control Regulation sea-discharge limits before the outfall. | hse | test | Effluent within permit limits |  |  |  | no | contractual
ER-09.06 | ER-09 Water treatment and effluents | Stormwater | Separate clean and potentially oily stormwater drainage with oil interceptors. | civil | inspection |  |  |  |  | no | contractual
ER-10.01 | ER-10 Balance of plant mechanical systems | Feed water pumps | 2x100 % variable-speed (VFD or hydraulic coupling) HP/IP boiler feed pumps. | mechanical | test |  |  |  |  | no | contractual
ER-10.02 | ER-10 Balance of plant mechanical systems | Condensate pumps | 2x100 % condensate extraction pumps. | mechanical | test |  |  |  |  | no | contractual
ER-10.03 | ER-10 Balance of plant mechanical systems | Compressed air | 2x100 % oil-free compressors, 2x100 % dryers, instrument air dew point -40 degC, receiver for 15 min of instrument air after loss of compressors. | mechanical | test |  |  |  |  | no | contractual
ER-10.04 | ER-10 Balance of plant mechanical systems | Auxiliary boiler | Gas-fired auxiliary boiler for start-up and sealing steam, sized for a cold start without external steam. | mechanical | test |  |  |  |  | no | contractual
ER-10.05 | ER-10 Balance of plant mechanical systems | Fire protection | Fire detection and protection per NFPA 850 and Turkish Fire Regulation: ring main, 2x100 % electric plus diesel fire pumps, water mist/CO2 for GT enclosure, deluge for transformers, gas detection, fire alarm system. | hse | test | Insurer and fire brigade acceptance |  |  |  | no | contractual
ER-10.06 | ER-10 Balance of plant mechanical systems | HVAC | HVAC for all buildings; electrical and control rooms with N+1 cooling and positive pressure with filtered (coastal) air. | hvac | test |  |  |  |  | no | contractual
ER-10.07 | ER-10 Balance of plant mechanical systems | Cranes | Turbine hall EOT crane sized for the heaviest maintenance lift (excluding generator stator), and maintenance hoists for pumps and valves. | mechanical | test |  |  |  |  | no | contractual
ER-10.08 | ER-10 Balance of plant mechanical systems | Nitrogen and hydrogen | Nitrogen supply for purging and preservation; hydrogen supply for generator cooling if hydrogen-cooled generators are offered. | mechanical | inspection |  |  |  |  | no | contractual
ER-11.01 | ER-11 Electrical systems | Grid connection | Connection to the 380 kV transmission system via an indoor GIS switchyard in a ventilated building (salt atmosphere), double busbar and bus coupler, two line bays and two generator transformer bays, designed for 50 kA short-circuit current; outdoor bushings with creepage per ER-02.10. | electrical | test |  |  |  | design_parameter/DP-CASE-0024 design_parameter/DP-CASE-0025 | yes | contractual
ER-11.02 | ER-11 Electrical systems | Generators | Air- or hydrogen-cooled synchronous generators per IEC 60034, 50 Hz, static excitation with PSS, generator circuit breakers per IEC/IEEE 62271-37-013. | electrical | test |  |  |  |  | no | contractual
ER-11.03 | ER-11 Electrical systems | Generator step-up transformers | One GSU per generator, ONAN/ONAF, rated for the maximum generator output at -8 degC, on-load tap changer, per IEC 60076; fire walls between transformers. | electrical | test |  |  |  |  | no | contractual
ER-11.04 | ER-11 Electrical systems | Auxiliary power supply | Two unit auxiliary transformers, 10.5 kV MV switchboards (2 sections with bus tie), 0.4 kV PMCC with automatic transfer. Start-up power from the grid via back-feed through the GSU. | electrical | test |  |  |  |  | no | contractual
ER-11.05 | ER-11 Electrical systems | Emergency power | Emergency diesel generator for safe shutdown loads (turning gear, lube oil, emergency lighting); the diesel fire pump has its own independent drive; UPS (2x100 %) for DCS and critical loads with 60 min autonomy; 220 V DC and 24 V DC systems. | electrical | test |  |  |  |  | no | contractual
ER-11.06 | ER-11 Electrical systems | Protection | Duplicated main protection (Main 1/Main 2 from different manufacturers where required by the TSO) for generators, transformers, busbars and lines. | electrical | test |  |  |  |  | no | contractual
ER-11.07 | ER-11 Electrical systems | Earthing and lightning | Earthing grid per IEEE 80 with safe touch and step voltages; lightning protection per IEC 62305. | electrical | test |  |  |  |  | no | contractual
ER-11.08 | ER-11 Electrical systems | Cables | Cables per IEC standards, halogen-free flame-retardant inside buildings, fire-rated cables for safety circuits. | electrical | inspection |  |  |  |  | no | contractual
ER-11.09 | ER-11 Electrical systems | Metering and TSO interface | Revenue metering per TSO/market operator rules (main and check meters, class 0.2S), RTU and telecommunication to the national dispatch centre. | electrical | test |  |  |  |  | no | contractual
ER-12.01 | ER-12 Instrumentation, control and cybersecurity | Distributed control system | Single integrated plant DCS for GT, ST, HRSG and BOP with redundant controllers, networks and power supplies; operation of the whole plant from the central control room by two operators. | i_and_c | test |  |  |  |  | no | contractual
ER-12.02 | ER-12 Instrumentation, control and cybersecurity | Automation level | Automatic start-up and shutdown sequences (one-button start to base load) and automatic load control from the dispatch set-point. | i_and_c | demonstration |  |  |  |  | no | contractual
ER-12.03 | ER-12 Instrumentation, control and cybersecurity | Safety instrumented systems | SIS per IEC 61511 with SIL verification, including burner management and HRSG protection. | i_and_c | analysis | SIL verification reports approved |  |  |  | no | contractual
ER-12.04 | ER-12 Instrumentation, control and cybersecurity | CEMS | Certified continuous emission monitoring (NOx, CO, O2, NH3, flow, moisture) per EN 14181 with data transmission to the environmental authority. | i_and_c | test |  |  |  |  | no | contractual
ER-12.05 | ER-12 Instrumentation, control and cybersecurity | Historian and performance monitoring | Plant historian (5 years on-line storage) and on-line performance calculation per ASME PTC 46 principles. | i_and_c | test |  |  |  |  | no | contractual
ER-12.06 | ER-12 Instrumentation, control and cybersecurity | Operator training simulator | High-fidelity operator training simulator of the whole plant, delivered 6 months before first fire. | i_and_c | demonstration |  |  |  |  | no | contractual
ER-12.07 | ER-12 Instrumentation, control and cybersecurity | Cybersecurity | OT cybersecurity per IEC 62443 (target security level SL2), zones and conduits, DMZ, patch and backup management, security acceptance test. | i_and_c | test | Security acceptance test passed |  |  |  | no | contractual
ER-12.08 | ER-12 Instrumentation, control and cybersecurity | Time synchronisation | GPS time synchronisation of DCS, protection relays and recorders (1 ms sequence of events). | i_and_c | test |  |  |  |  | no | contractual
ER-13.01 | ER-13 Civil, structural and architectural works | Foundations | Turbine and generator foundations designed for dynamic loads with separated foundations from buildings; settlement limits per OEM. | civil | analysis |  |  |  |  | no | contractual
ER-13.02 | ER-13 Civil, structural and architectural works | Buildings | Turbine hall, control and electrical building, administration building, workshop/warehouse, water treatment building, gatehouse, fire station. | civil | inspection |  |  |  |  | no | contractual
ER-13.03 | ER-13 Civil, structural and architectural works | Structural steel | Structural steel per EN 1993 with seismic detailing, hot-dip galvanised outdoors (EN ISO 1461). | structural | inspection |  |  |  |  | no | contractual
ER-13.04 | ER-13 Civil, structural and architectural works | Concrete | Concrete per EN 1992 / TS 500 with exposure class XS for marine-exposed elements; minimum 50-year durability. | civil | inspection |  |  |  |  | no | contractual
ER-13.05 | ER-13 Civil, structural and architectural works | Roads and drainage | Internal asphalt roads for 40 t axle loads to the heaviest delivery route, surface water drainage for ER-02.05 rainfall. | civil | inspection |  |  |  |  | no | contractual
ER-13.06 | ER-13 Civil, structural and architectural works | Marine works | Intake and outfall pipelines (HDPE or GRP) with ballast and scour protection, designed for 50-year wave conditions. | civil | analysis |  |  |  |  | no | contractual
ER-14.01 | ER-14 Environment, health and safety | EIA compliance | The Works shall comply with the conditions of the positive EIA decision and the Environmental Law (No. 2872) and its regulations. | hse | review | No outstanding EIA non-conformities at Taking-Over |  |  |  | no | contractual
ER-14.02 | ER-14 Environment, health and safety | Air emissions | Natural gas: NOx <= 30 mg/Nm3, CO <= 30 mg/Nm3, NH3 slip <= 5 mg/Nm3. LDO: NOx <= 50 mg/Nm3, CO <= 50 mg/Nm3, SO2 <= 10 mg/Nm3, dust <= 5 mg/Nm3, NH3 slip <= 5 mg/Nm3. All dry, 15 % O2, 50 % to 100 % GT load (ALP-OWN-ENV-001 section 1). | hse | test | Within guaranteed limits | PG-04 | <= 30 mg/Nm3 | design_parameter/DP-CASE-0040 design_parameter/DP-CASE-0041 design_parameter/DP-CASE-0042 design_parameter/DP-OWNR-0041 design_parameter/DP-OWNR-0042 design_parameter/DP-OWNR-0043 | yes | contractual
ER-14.03 | ER-14 Environment, health and safety | Near-field noise | Maximum 85 dB(A) at 1 m from any equipment in normal operation. | hse | test | <= 85 dB(A) | PG-07 | <= 85 dB(A) | design_parameter/DP-CASE-0044 | yes | contractual
ER-14.04 | ER-14 Environment, health and safety | Environmental noise | Maximum 45 dB(A) LAeq night at the nearest sensitive receptor. | hse | test | <= 45 dB(A) | PG-08 | <= 45 dB(A) | design_parameter/DP-CASE-0045 | yes | contractual
ER-14.05 | ER-14 Environment, health and safety | Occupational health and safety | Construction and design shall comply with the Occupational Health and Safety Law (No. 6331); the Contractor shall implement an ISO 45001-certified HSE management system and a lost-time-injury target of zero. | hse | review |  |  |  |  | no | contractual
ER-14.06 | ER-14 Environment, health and safety | Hazardous areas | Hazardous area classification per IEC 60079-10-1; equipment certified accordingly. | hse | review |  |  |  |  | no | contractual
ER-14.07 | ER-14 Environment, health and safety | Process safety studies | HAZID, HAZOP, SIL determination, fire and explosion risk assessment and a Major Accident Prevention assessment where applicable. | hse | review | All actions closed before first fire |  |  |  | no | contractual
ER-14.08 | ER-14 Environment, health and safety | Carbon capture readiness | Space reservation and tie-in points for a future post-combustion carbon capture plant at the HRSG outlet. | process | review |  |  |  |  | no | contractual
ER-15.01 | ER-15 Quality, inspection and testing during manufacture | Quality management | ISO 9001 quality management for the Contractor and all major subcontractors; project quality plan within 30 days of NTP. | general | review |  |  |  |  | no | contractual
ER-15.02 | ER-15 Quality, inspection and testing during manufacture | Inspection and test plans | ITPs for all major equipment with hold and witness points for the Engineer, 15 days' notice for witnessed tests. | general | review |  |  |  |  | no | contractual
ER-15.03 | ER-15 Quality, inspection and testing during manufacture | Factory acceptance tests | FATs at least for: GT and ST control systems, generators, GSU transformers, GIS, MV switchgear, DCS, CEMS. | general | test |  |  |  |  | no | contractual
ER-15.04 | ER-15 Quality, inspection and testing during manufacture | Material traceability | Material certificates per EN 10204 3.1 (3.2 for pressure parts above 50 bar) and positive material identification of alloy piping. | mechanical | inspection |  |  |  |  | no | contractual
ER-15.05 | ER-15 Quality, inspection and testing during manufacture | Welding | Welding per ASME IX / EN ISO 15614, 100 % NDE of HP/HRH/main steam butt welds. | piping | inspection |  |  |  |  | no | contractual
ER-16.01 | ER-16 Commissioning and Tests on Completion | Commissioning plan | System-based commissioning plan with pre-commissioning, cold and hot commissioning, submitted 9 months before first fire. | commissioning | review |  |  |  |  | no | contractual
ER-16.02 | ER-16 Commissioning and Tests on Completion | Steam blowing and chemical cleaning | Chemical cleaning of the HRSG and steam blowing of steam lines to OEM cleanliness criteria. | commissioning | test |  |  |  |  | no | contractual
ER-16.03 | ER-16 Commissioning and Tests on Completion | Grid Code compliance tests | All tests required by the TSO for connection and commercial operation, including reactive capability and frequency response. | electrical | test | TSO acceptance |  |  |  | no | contractual
ER-16.04 | ER-16 Commissioning and Tests on Completion | Performance test | Performance test per ASME PTC 46 within 30 days after initial operation, test procedure submitted 90 days before, with instrument calibration traceable to national standards. | commissioning | test | PG-01/PG-02/PG-03 demonstrated | PG-01 | >= 600 MW |  | no | contractual
ER-16.05 | ER-16 Commissioning and Tests on Completion | Emission and noise tests | Emission tests by an accredited laboratory and noise surveys per PG-04 to PG-08. | hse | test |  | PG-04 | <= 30 mg/Nm3 |  | no | contractual
ER-16.06 | ER-16 Commissioning and Tests on Completion | Operational demonstration | Demonstration of start times, ramp rates, minimum load, load rejection and trip tests. | commissioning | demonstration |  | PG-09 | <= 45 min |  | no | contractual
ER-16.07 | ER-16 Commissioning and Tests on Completion | Reliability run | 30-day continuous reliability run with availability >= 98 %; restarted after rectification if failed. | commissioning | test | >= 98 % | PG-12 | >= 98 % |  | no | contractual
ER-16.08 | ER-16 Commissioning and Tests on Completion | Tests on LDO | Performance test on LDO (24 h, corrected to SRC), emission tests on LDO, automatic fuel transfer tests and a start on LDO. | commissioning | test | PG-15, PG-16, PG-17, PG-18 demonstrated | PG-15 | >= 560 MW |  | no | contractual
ER-17.01 | ER-17 Documentation, training, O&M and spares | Document management | Documents submitted electronically with the Owner's numbering and a master document register; review period 14 days (21 days for the Basic Design Package). | project_control | review |  |  |  |  | no | contractual
ER-17.02 | ER-17 Documentation, training, O&M and spares | Schedule and reporting | Level 3 CPM schedule (MS Project XML or Primavera P6) with monthly updates, S-curves and progress reports. | project_control | review |  |  |  |  | no | contractual
ER-17.03 | ER-17 Documentation, training, O&M and spares | As-built documentation | As-built drawings, 3D model and engineering database within 3 months of Taking-Over. | general | review |  |  |  |  | no | contractual
ER-17.04 | ER-17 Documentation, training, O&M and spares | O&M manuals | Operation and maintenance manuals (English, operating procedures also in Turkish) 6 months before first fire, final at Taking-Over. | general | review |  |  |  |  | no | contractual
ER-17.05 | ER-17 Documentation, training, O&M and spares | Training | Classroom, simulator and on-the-job training for 60 Owner staff (operators, maintenance, I&C, chemistry), minimum 12 weeks per key trade. | general | demonstration |  |  |  |  | no | contractual
ER-17.06 | ER-17 Documentation, training, O&M and spares | Spare parts | Commissioning spares, special tools, and a recommended two-year operating spares list with prices valid for 18 months. | general | review |  |  |  |  | no | contractual
ER-17.07 | ER-17 Documentation, training, O&M and spares | Long-term service | The power island supplier shall offer a long-term service agreement for GT/ST/generators (separate contract, not part of the Contract Price). | general | review |  |  |  |  | no | contractual
ER-18.01 | ER-18 Interfaces and terminal points | Terminal points | Terminal points and scope limits are defined in Appendix D; the Contractor shall provide all works up to and including the terminal points. | general | review |  |  |  |  | no | contractual
ER-18.02 | ER-18 Interfaces and terminal points | Grid connection interface | The Owner builds and energises the 380 kV line up to TP-E1 (available by 2028-07-15, an Owner-furnished item under Sub-Clause 2.4) and coordinates the line energisation with the TSO. The Contractor coordinates plant-side protection settings, SCADA and the Grid Code compliance tests with the TSO and the Owner's line contractor. | electrical | review |  |  |  |  | no | contractual
ER-18.03 | ER-18 Interfaces and terminal points | Gas network interface | The Contractor shall coordinate the gas receiving station tie-in, pressure protection and metering approval with the gas network operator. | process | review |  |  |  |  | no | contractual
ER-18.04 | ER-18 Interfaces and terminal points | Owner's engineering database | All interface data shall be exchanged through the Owner's engineering database (single source of truth). | general | review |  |  |  |  | no | contractual
ER-18.05 | ER-18 Interfaces and terminal points | Tie-in register | The tie-in points, their location, conditions and the Owner's availability dates are listed in the tie-in register (Appendix D). The Contractor's scope starts at each tie-in; the Contractor shall verify the conditions and coordinate the interface works. | general | review |  |  |  |  | no | contractual

## Guarantees
Alpilla 600 MW Combined Cycle Power Plant - Guarantees
engine requirements_matrix v1.0.0 ¦ generated 2026-09-27T17:46:40Z by SETUP ¦ data b226b6c9cd57c954
ID | Parameter | Category | Value | Unit | Direction | Minimum acceptance | LD rate | LD unit | Remedy | Requirements
PG-01 | Net electrical output at Site Reference Conditions | performance | 600 | MW | min | 582 | 2200 | EUR per kW shortfall | Below 97 % of the guaranteed value the Owner may reject the Works after the rectification period (Sub-Clause 12.5). | ER-04.01, ER-16.04
PG-02 | Net heat rate (LHV) at Site Reference Conditions | performance | 5860 | kJ/kWh | max | 6035.8 | 400000 | EUR per kJ/kWh excess | Above 103 % of the guaranteed value the Owner may reject the Works after the rectification period. | ER-04.02
PG-03 | Net heat rate (LHV) at 60 % plant load | performance | 6250 | kJ/kWh | max |  | 150000 | EUR per kJ/kWh excess |  | ER-04.03
PG-04 | NOx emission (as NO2) | emissions | 30 | mg/Nm3 | max |  |  |  | No LD: the Contractor shall rectify at its cost until compliant; Taking-Over is not issued before compliance. | ER-06.03, ER-14.02, ER-16.05
PG-05 | CO emission | emissions | 30 | mg/Nm3 | max |  |  |  | Must rectify (as PG-04).
PG-06 | Ammonia slip from the SCR | emissions | 5 | mg/Nm3 | max |  |  |  | Must rectify.
PG-07 | Near-field noise | noise | 85 | dB(A) | max |  |  |  | Must rectify. | ER-14.03
PG-08 | Noise at nearest sensitive receptor (night) | noise | 45 | dB(A) | max |  | 250000 | EUR per dB(A) exceedance (after rectification attempts) | Contractor to rectify first; LD only if rectification fails. | ER-14.04
PG-09 | Hot start time to base load | operational | 45 | min | max |  | 20000 | EUR per minute exceedance |  | ER-04.04, ER-16.06
PG-10 | Load ramp rate in combined cycle | operational | 35 | MW/min | min |  | 100000 | EUR per MW/min shortfall |  | ER-04.05
PG-11 | Minimum environmental load | operational | 40 | % of plant net output | max |  | 300000 | EUR per percentage point exceedance |  | ER-04.06
PG-12 | Reliability run availability | reliability | 98 | % | min |  |  |  | Failed run to be repeated from the start after rectification. | ER-16.07
PG-13 | Condenser cooling water temperature rise | environmental | 7 | K | max |  |  |  | Must rectify (EIA permit condition). | ER-07.04
PG-14 | Thermal plume at edge of mixing zone | environmental | 3 | K | max |  |  |  | Must rectify (EIA permit condition). | ER-08.05
PG-15 | Net electrical output on LDO at Site Reference Conditions | performance | 560 | MW | min | 543.2 | 800 | EUR per kW shortfall |  | ER-16.08
PG-16 | Net heat rate (LHV) on LDO at Site Reference Conditions | performance | 6150 | kJ/kWh | max | 6334.5 | 60000 | EUR per kJ/kWh excess
PG-17 | NOx emission on LDO (as NO2) | emissions | 50 | mg/Nm3 | max |  |  |  | No LD: the Contractor shall rectify until compliant (permit condition). | ER-03.11
PG-18 | Automatic fuel transfer gas to LDO without trip | operational | 100 | % successful transfers | min |  |  |  | Must rectify; Taking-Over not issued before successful demonstration. | ER-03.10

## Scope split
Alpilla 600 MW Combined Cycle Power Plant - Scope split and terminal points
engine requirements_matrix v1.0.0 ¦ generated 2026-09-27T17:46:40Z by SETUP ¦ data b226b6c9cd57c954
ID | Area | Item | Design | Supply | Install | Commission | Terminal point
SC-001 | Site | Land, access rights and site handover (levelled to +15.0 m) | OWNER | OWNER | OWNER |  | Site boundary per land-use plan
SC-002 | Site | Environmental Impact Assessment (EIA) positive decision | OWNER | OWNER
SC-003 | Site | Construction, operating and building permits (Contractor supplies all design inputs) | IEPC | OWNER
SC-004 | Site | Geotechnical and topographic surveys (baseline supplied by Owner, confirmatory by Contractor) | IEPC | IEPC | IEPC
SC-005 | Site | Site preparation, fencing, roads, drainage, temporary facilities | IEPC | IEPC | IEPC
SC-006 | Power island | Gas turbine package incl. auxiliaries, enclosure, inlet air filtration, exhaust diffuser | IEC | IEC | IEPC | IEC | GT exhaust flange to HRSG inlet duct
SC-007 | Power island | GT generator incl. excitation, protection, cooling | IEC | IEC | IEPC | IEC | Generator terminals (IPB connection)
SC-008 | Power island | Steam turbine (HP/IP/LP, reheat) incl. lube/control oil, gland steam, turning gear | IEC | IEC | IEPC | IEC
SC-009 | Power island | ST generator incl. excitation, protection | IEC | IEC | IEPC | IEC | Generator terminals
SC-010 | Power island | HRSG triple-pressure reheat, horizontal, natural circulation, with SCR and CO catalyst | IEC | IEC | IEPC | IEC | HRSG outlet to stack
SC-011 | Power island | Stack 60 m with CEMS platform and silencer | IEPC | IEPC | IEPC | IEPC
SC-012 | Power island | Water-cooled condenser (seawater), vacuum system | IEC | IEC | IEPC | IEC | Cooling water flanges at condenser water boxes
SC-013 | Power island | Power island control system (TCS/ST controls) integrated in plant DCS | IEC | IEC | IEPC | IEC | DCS interface (redundant fibre)
SC-014 | Power island | GSU transformers (GT and ST), isolated phase busducts, generator circuit breakers | IEC | IEC | IEPC | IEC | GSU HV bushings
SC-015 | Balance of plant | Condensate and boiler feed water systems (pumps 2x100 %) | IEPC | IEPC | IEPC | IEPC
SC-016 | Balance of plant | Seawater intake, screens, CW pumps (2x50 %), outfall and diffuser | IEPC | IEPC | IEPC | IEPC | Offshore intake head / outfall diffuser
SC-017 | Balance of plant | Electro-chlorination for biofouling control | IEPC | IEPC | IEPC | IEPC
SC-018 | Balance of plant | Seawater reverse osmosis and demineralisation plant | IEPC | IEPC | IEPC | IEPC
SC-019 | Balance of plant | Condensate polishing plant | IEPC | IEPC | IEPC | IEPC
SC-020 | Balance of plant | Waste water treatment and effluent monitoring | IEPC | IEPC | IEPC | IEPC | Discharge point to outfall
SC-021 | Balance of plant | Closed cooling water system with plate heat exchangers | IEPC | IEPC | IEPC | IEPC
SC-022 | Balance of plant | Compressed air (service and instrument) 2x100 % | IEPC | IEPC | IEPC | IEPC
SC-023 | Balance of plant | Auxiliary boiler (gas-fired) for start-up steam | IEPC | IEPC | IEPC | IEPC
SC-024 | Balance of plant | Fire detection and protection per NFPA 850 | IEPC | IEPC | IEPC | IEPC
SC-025 | Balance of plant | HVAC for all buildings and electrical rooms | IEPC | IEPC | IEPC | IEPC
SC-026 | Balance of plant | Cranes and hoists (turbine hall EOT crane) | IEPC | IEPC | IEPC | IEPC
SC-027 | Fuel gas | Gas pipeline from national transmission system to plant boundary | OWNER | OWNER | OWNER | OWNER | Owner valve at plant boundary (inlet flange of gas receiving station)
SC-028 | Fuel gas | Gas receiving and metering station (fiscal metering, filtration, heating, pressure control) | IEPC | IEPC | IEPC | IEPC | Inlet flange at plant boundary
SC-029 | Fuel gas | Performance gas heater and GT fuel skid | IEC | IEC | IEPC | IEC
SC-030 | Electrical | 380 kV GIS switchyard (double busbar) within plant boundary | IEPC | IEPC | IEPC | IEPC | 380 kV line gantry / cable sealing ends
SC-031 | Electrical | 380 kV transmission connection line and remote substation works | OWNER | OWNER | OWNER | OWNER | Line gantry at switchyard
SC-032 | Electrical | Unit auxiliary transformers, MV switchgear 10.5 kV, LV 0.4 kV distribution | IEPC | IEPC | IEPC | IEPC
SC-033 | Electrical | Emergency diesel generator and UPS / DC systems | IEPC | IEPC | IEPC | IEPC
SC-034 | Electrical | Earthing, lightning protection, cabling, cable trays | IEPC | IEPC | IEPC | IEPC
SC-035 | Electrical | Revenue metering and TSO SCADA/telecom interface | IEPC | IEPC | IEPC | IEPC | TSO RTU interface in control building
SC-036 | I&C | Plant DCS, historian, operator training simulator | IEPC | IEPC | IEPC | IEPC
SC-037 | I&C | Safety instrumented systems (burner management, HRSG protection) per IEC 61511 | IEC | IEC | IEPC | IEC
SC-038 | I&C | Continuous emission monitoring system (CEMS) | IEPC | IEPC | IEPC | IEPC | Data link to environmental authority
SC-039 | I&C | Plant security, CCTV, access control, cybersecurity (IEC 62443) | IEPC | IEPC | IEPC | IEPC
SC-040 | Civil | Piling, foundations, structures, turbine hall, HRSG structure | IEPC | IEPC | IEPC
SC-041 | Civil | Buildings: control, administration, workshop/warehouse, water treatment, gatehouse | IEPC | IEPC | IEPC
SC-042 | Civil | Marine works for intake and outfall (dredging, pipes, heads) | IEPC | IEPC | IEPC
SC-043 | Utilities | Potable water connection at site boundary (no sewer available) | OWNER | OWNER | OWNER |  | Site boundary
SC-044 | Utilities | Telecommunication connection (fibre) to site boundary | OWNER | OWNER | OWNER |  | Site boundary
SC-045 | Utilities | Construction power and water | IEPC | IEPC | IEPC
SC-046 | Commissioning | Consumables until Taking-Over (except natural gas) | IEPC | IEPC
SC-047 | Commissioning | Natural gas for commissioning and tests | OWNER | OWNER |  |  | Gas receiving station inlet
SC-048 | Commissioning | Grid access for back-feed and test energy; purchase of test energy | OWNER | OWNER
SC-049 | Commissioning | Operation and maintenance staff for training and commissioning participation | OWNER | OWNER
SC-050 | Spares | Commissioning spares and special tools | IEPC | IEPC
SC-051 | Spares | Two-year operating spares (priced list, Owner option) | IEPC | IEPC |  |  | Owner's warehouse
SC-052 | Fuel oil | LDO truck unloading station (4 bays), storage tanks 2 x 50 %, bund, foam system | IEPC | IEPC | IEPC | IEPC | Tanker coupling at unloading bays
SC-053 | Fuel oil | LDO forwarding pumps, filters, metering, fuel treatment (2 x 100 % centrifugal separators) | IEPC | IEPC | IEPC | IEPC | GT liquid fuel skid inlet flange
SC-054 | Power island | Dual-fuel GT combustion system, liquid fuel skid, water injection skid, purge system | IEC | IEC | IEPC | IEC
SC-055 | Commissioning | LDO first fill of the storage tanks | OWNER | OWNER |  |  | Tanker coupling at unloading bays
SC-056 | Commissioning | LDO for tests beyond the first fill |  | IEPC
SC-057 | Balance of plant | Packaged sanitary wastewater treatment plant (biological + UV), discharge via outfall | IEPC | IEPC | IEPC | IEPC | Discharge into the outfall

## Coverage
Alpilla 600 MW Combined Cycle Power Plant - Coverage by section
engine requirements_matrix v1.0.0 ¦ generated 2026-09-27T17:46:40Z by SETUP ¦ data b226b6c9cd57c954
Section | Requirements | With guarantee | Traced to data | Traced % | test | inspection | analysis | review | demonstration
ER-01 General requirements and plant description | 10 | 0 | 1 | 10 | 0 | 0 | 1 | 9 | 0
ER-02 Site conditions and design data | 14 | 0 | 11 | 78.6 | 0 | 3 | 8 | 3 | 0
ER-03 Fuel | 11 | 2 | 5 | 45.5 | 4 | 2 | 2 | 2 | 1
ER-04 Performance and operational requirements | 12 | 6 | 9 | 75 | 6 | 0 | 1 | 1 | 4
ER-05 Gas turbine | 7 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 1
ER-06 Heat recovery steam generator | 8 | 1 | 1 | 12.5 | 1 | 4 | 1 | 2 | 0
ER-07 Steam turbine and condenser | 11 | 1 | 3 | 27.3 | 3 | 3 | 3 | 2 | 0
ER-08 Cooling water system | 7 | 1 | 3 | 42.9 | 3 | 3 | 0 | 0 | 1
ER-09 Water treatment and effluents | 6 | 0 | 0 | 0 | 3 | 2 | 0 | 1 | 0
ER-10 Balance of plant mechanical systems | 8 | 0 | 0 | 0 | 7 | 1 | 0 | 0 | 0
ER-11 Electrical systems | 9 | 0 | 1 | 11.1 | 8 | 1 | 0 | 0 | 0
ER-12 Instrumentation, control and cybersecurity | 8 | 0 | 0 | 0 | 5 | 0 | 1 | 0 | 2
ER-13 Civil, structural and architectural works | 6 | 0 | 0 | 0 | 0 | 4 | 2 | 0 | 0
ER-14 Environment, health and safety | 8 | 3 | 3 | 37.5 | 3 | 0 | 0 | 5 | 0
ER-15 Quality, inspection and testing during manufacture | 5 | 0 | 0 | 0 | 1 | 2 | 0 | 2 | 0
ER-16 Commissioning and Tests on Completion | 8 | 5 | 0 | 0 | 6 | 0 | 0 | 1 | 1
ER-17 Documentation, training, O&M and spares | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 1
ER-18 Interfaces and terminal points | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0
Total | 150 |  | 37 | 24.7