Alpilla Enerji Üretim A.Ş.

Alpilla 600 MW Combined Cycle Power Plant

Grid Connection Data

| Document number | ALP-OWN-ELE-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-11 |
| Status | Issued for tender / contract |
| Confidentiality | Restricted - Contract ALP-EPC-001 parties only |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | Owner's Engineer (discipline lead) | Owner's Engineer (project engineer) | Owner's Project Director |
| Signature / date | signed 2026-09-11 | signed 2026-09-11 | signed 2026-09-11 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-11 | Issued for tender / contract |

CASE STUDY - all organisations, data and signatures are fictional.

# 1. Connection

Connection to the 380 kV TSO substation "Kıyı" (fictional name) by a 7 km double-circuit overhead line built by the Owner.

Connection agreement signed 2026-06-20; connection capacity 640 MW export, 40 MW import.

Line completion and energisation readiness planned by the Owner: 2028-09-30.

# 2. System data at the plant 380 kV busbar

| Parameter | Value |
| --- | --- |
| Nominal / highest system voltage | 380 kV / 420 kV |
| Normal voltage range | 360–410 kV; 342–420 kV for up to 30 min |
| Frequency | 50 Hz; continuous 49.0–51.0 Hz; 47.5–52.5 Hz time-limited per Grid Code |
| Three-phase short-circuit level (2029) | maximum 40 kA, minimum 12 kA |
| Future maximum (2035 planning) | 50 kA |
| X/R ratio | 14 (maximum case) |
| Earthing | solidly earthed |
| Fault clearing time (main protection) | ≤ 100 ms |
| Auto-reclose | single-phase, 1 s dead time on the connection line |

# 3. TSO requirements (summary)

Fault ride through, reactive capability 0.85 lagging / 0.95 leading at the connection point, primary frequency control (droop 4 %), secondary frequency control (AGC) and fast frequency response.

Main 1 / Main 2 line differential protection from different manufacturers; busbar protection with breaker failure.

Revenue metering class 0.2S main and check; RTU with IEC 60870-5-104 to the national control centre.

Power quality: harmonic emission limits per the TSO's connection conditions.

Compliance tests witnessed by the TSO before commercial operation.