Alpilla Enerji Üretim A.Ş.

Alpilla 600 MW Combined Cycle Power Plant

Positive EIA Decision: Conditions Binding the Project

| Document number | ALP-OWN-ENV-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-09 |
| Status | Issued for tender / contract |
| Confidentiality | Restricted - Contract ALP-EPC-001 parties only |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | Owner's Engineer (discipline lead) | Owner's Engineer (project engineer) | Owner's Project Director |
| Signature / date | signed 2026-09-09 | signed 2026-09-09 | signed 2026-09-09 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-09 | Issued for tender / contract |

CASE STUDY - all organisations, data and signatures are fictional.

# 1. Air emissions (dry, 15 % O2, 70–100 % load unless stated)

| Pollutant | Natural gas | Light diesel oil (≤ 500 h/year) |
| --- | --- | --- |
| NOx (as NO2) | 30 mg/Nm³ | 50 mg/Nm³ |
| CO | 30 mg/Nm³ | 50 mg/Nm³ |
| NH3 slip | 5 mg/Nm³ | 5 mg/Nm³ |
| SO2 | — | 10 mg/Nm³ |
| Dust | — | 5 mg/Nm³ |

Stack height: 65 m (result of the approved dispersion study; the Owner's draft contract states 60 m).

CEMS per EN 14181 with on-line reporting.

# 2. Water

Cooling water temperature rise across the condenser ≤ 7 K; temperature excess ≤ 3 K at 100 m from the diffuser.

Residual oxidant (as Cl2) at the outfall ≤ 0.1 mg/l.

Process and sanitary effluents treated to the Water Pollution Control Regulation sea-discharge limits.

No discharge of brine from the SWRO at more than 5 % above ambient salinity at 50 m from the diffuser.

# 3. Noise

Operation: 45 dB(A) night / 55 dB(A) day at the nearest residential receptor.

Construction: 07:00–19:00 on weekdays and 08:00–17:00 on Saturdays for noisy works (piling, blasting, steam blowing); steam blowing requires 7 days' notice to the village and silencers.

# 4. Marine and ecology

No marine works (dredging, trenching, pipe laying) between 1 May and 30 September (fish spawning).

Fish return system at the screens; intake velocity ≤ 0.15 m/s.

Marine monitoring programme during construction and for 3 years of operation (Owner's obligation; the Contractor provides data).

# 5. Other

Traffic: heavy vehicles avoid the village road between 07:30–09:00 and 16:00–18:00.

Archaeological chance-find procedure applies to all excavations.