Alpilla Enerji Üretim A.Ş.

Alpilla 600 MW Combined Cycle Power Plant

Natural Gas Quality and Supply Conditions

| Document number | ALP-OWN-FUL-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-08 |
| Status | Issued for tender / contract |
| Confidentiality | Restricted - Contract ALP-EPC-001 parties only |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | Owner's Engineer (discipline lead) | Owner's Engineer (project engineer) | Owner's Project Director |
| Signature / date | signed 2026-09-08 | signed 2026-09-08 | signed 2026-09-08 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-08 | Issued for tender / contract |

CASE STUDY - all organisations, data and signatures are fictional.

# 1. Basis

Gas transmission network operator's quality data for the regional high-pressure line (2022–2025, on-line chromatograph at the nearest compressor station, 35 km upstream), the operator's network entry specification, and the Owner's gas transport agreement. Reference state for volumes: 15 °C, 1.01325 bar ("Sm³"); energies on LHV unless stated.

# 2. Composition (mol %)

| Component | Minimum | Typical (design) | Maximum |
| --- | --- | --- | --- |
| Methane CH4 | 85.0 | 93.0 | 98.5 |
| Ethane C2H6 | 0.5 | 3.5 | 7.0 |
| Propane C3H8 | 0.05 | 0.80 | 2.5 |
| i-Butane | 0.00 | 0.15 | 0.50 |
| n-Butane | 0.00 | 0.15 | 0.50 |
| Pentanes and heavier (C5+) | 0.00 | 0.05 | 0.20 |
| Nitrogen N2 | 0.30 | 1.55 | 4.0 |
| Carbon dioxide CO2 | 0.00 | 0.80 | 2.5 |
| Oxygen O2 | 0.000 | 0.001 | 0.02 |
| Hydrogen H2 | 0.0 | < 0.1 | see 5 |
| Helium | 0.00 | 0.01 | 0.05 |

# 3. Physical properties

| Property | Unit | Minimum | Typical | Maximum |
| --- | --- | --- | --- | --- |
| LHV (mass) | MJ/kg | 44.2 | 48.4 | 49.8 |
| LHV (volume) | MJ/Sm³ | 31.4 | 34.4 | 37.9 |
| GCV (volume) | MJ/Sm³ | 35.0 | 38.2 | 42.0 |
| Wobbe index (GCV) | MJ/Sm³ | 47.2 | 50.2 | 51.8 |
| Relative density | - | 0.560 | 0.600 | 0.690 |
| Rate of change of Wobbe index | %/min |  |  | 1.0 |
| Methane number | - | 72 | 88 | 97 |

Note: the lower end of the LHV range (44.2 MJ/kg) occurs with high N2/CO2 gas from one entry point; it has occurred for 3 % of hours.

# 4. Contaminants and trace components

| Parameter | Unit | Network limit | Measured typical | Measured max |
| --- | --- | --- | --- | --- |
| Total sulphur (incl. H2S, COS, mercaptans) | mg S/Sm³ | 30 | 4 | 17 |
| H2S + COS (as S) | mg/Sm³ | 5 | 0.8 | 3.1 |
| Mercaptan sulphur | mg/Sm³ | 6 | 0.5 | 2.2 |
| Mercury | µg/Sm³ | 1 | < 0.01 | 0.03 |
| Water dew point | °C at 70 barg | ≤ −8 | −14 | −9 |
| Hydrocarbon dew point | °C (1–70 barg) | ≤ −2 | −9 | −4 |
| Particulates (> 10 µm) | mg/Sm³ | 1 | n.m. | n.m. |
| Sodium + potassium (alkali metals) | mg/Sm³ | not specified | < 0.005 (d.l.) | < 0.005 |
| Lead | mg/Sm³ | not specified | < 0.005 (d.l.) | < 0.005 |
| Vanadium | mg/Sm³ | not specified | < 0.005 (d.l.) | < 0.005 |
| Calcium | mg/Sm³ | not specified | < 0.01 (d.l.) | < 0.01 |
| Chlorides | mg/Sm³ | not specified | < 0.05 (d.l.) | < 0.05 |
| Compressor oil carry-over | mg/Sm³ | not specified | not measured | not measured |
| Odorant | - | transmission gas is not odorised |  |  |

d.l. = detection limit of the laboratory method; n.m. = not measured. The network operator does not guarantee trace metal, chloride or compressor oil content. The Owner requires the Contractor's fuel gas conditioning to protect the gas turbine against liquid carry-over and particulates under all network conditions.

# 5. Hydrogen blending

The network operator has announced hydrogen blending pilots of up to 5 vol % from 2030 and up to 10 vol % after 2035 (not firm). The plant shall be capable of 10 vol % H2 (contract ER-03.02); the Owner accepts reduced emissions guarantees above 5 vol % if justified by the OEM.

# 6. Supply pressure, temperature and capacity at the plant tie-in (TP-G1)

| Parameter | Value |
| --- | --- |
| Normal pressure | 55–65 barg |
| Minimum guaranteed pressure | 45 barg |
| Exceptional minimum (winter peak, max 72 h/year, notified 24 h in advance) | 40 barg |
| Maximum operating pressure / MAOP | 70 barg / 75 barg |
| Pressure rate of change | ≤ 1.0 bar/min |
| Temperature | 5–25 °C |
| Booked capacity | 115,000 Sm³/h firm; 130,000 Sm³/h interruptible |
| Fiscal metering | by the Contractor per network operator standards; custody transfer at the metering station outlet |

The network operator requires a slam-shut and relief protection at the station inlet and approval of the metering design.