## T1 2. Composition (mol %)
ALP-OWN-FUL-001 Rev 0 - 2. Composition (mol %)
Component | Minimum | Typical (design) | Maximum
Methane CH4 | 85 | 93 | 98.5
Ethane C2H6 | 0.5 | 3.5 | 7
Propane C3H8 | 0.05 | 0.8 | 2.5
i-Butane | 0 | 0.15 | 0.5
n-Butane | 0 | 0.15 | 0.5
Pentanes and heavier (C5+) | 0 | 0.05 | 0.2
Nitrogen N2 | 0.3 | 1.55 | 4
Carbon dioxide CO2 | 0 | 0.8 | 2.5
Oxygen O2 | 0 | 0.001 | 0.02
Hydrogen H2 | 0 | < 0.1 | see 5
Helium | 0 | 0.01 | 0.05

## T2 3. Physical properties
ALP-OWN-FUL-001 Rev 0 - 3. Physical properties
Property | Unit | Minimum | Typical | Maximum
LHV (mass) | MJ/kg | 44.2 | 48.4 | 49.8
LHV (volume) | MJ/Sm³ | 31.4 | 34.4 | 37.9
GCV (volume) | MJ/Sm³ | 35 | 38.2 | 42
Wobbe index (GCV) | MJ/Sm³ | 47.2 | 50.2 | 51.8
Relative density | - | 0.56 | 0.6 | 0.69
Rate of change of Wobbe index | %/min |  |  | 1
Methane number | - | 72 | 88 | 97

## T3 4. Contaminants and trace co
ALP-OWN-FUL-001 Rev 0 - 4. Contaminants and trace components
Parameter | Unit | Network limit | Measured typical | Measured max
Total sulphur (incl. H2S, COS, mercaptans) | mg S/Sm³ | 30 | 4 | 17
H2S + COS (as S) | mg/Sm³ | 5 | 0.8 | 3.1
Mercaptan sulphur | mg/Sm³ | 6 | 0.5 | 2.2
Mercury | µg/Sm³ | 1 | < 0.01 | 0.03
Water dew point | °C at 70 barg | ≤ −8 | −14 | −9
Hydrocarbon dew point | °C (1–70 barg) | ≤ −2 | −9 | −4
Particulates (> 10 µm) | mg/Sm³ | 1 | n.m. | n.m.
Sodium + potassium (alkali metals) | mg/Sm³ | not specified | < 0.005 (d.l.) | < 0.005
Lead | mg/Sm³ | not specified | < 0.005 (d.l.) | < 0.005
Vanadium | mg/Sm³ | not specified | < 0.005 (d.l.) | < 0.005
Calcium | mg/Sm³ | not specified | < 0.01 (d.l.) | < 0.01
Chlorides | mg/Sm³ | not specified | < 0.05 (d.l.) | < 0.05
Compressor oil carry-over | mg/Sm³ | not specified | not measured | not measured
Odorant | - | transmission gas is not odorised

## T4 6. Supply pressure, temperat
ALP-OWN-FUL-001 Rev 0 - 6. Supply pressure, temperature and capacity at the plant tie-in (TP-G1)
Parameter | Value
Normal pressure | 55–65 barg
Minimum guaranteed pressure | 45 barg
Exceptional minimum (winter peak, max 72 h/year, notified 24 h in advance) | 40 barg
Maximum operating pressure / MAOP | 70 barg / 75 barg
Pressure rate of change | ≤ 1.0 bar/min
Temperature | 5–25 °C
Booked capacity | 115,000 Sm³/h firm; 130,000 Sm³/h interruptible
Fiscal metering | by the Contractor per network operator standards; custody transfer at the metering station outlet