Alpilla Enerji Üretim A.Ş.

Alpilla 600 MW Combined Cycle Power Plant

Secondary Fuel: Light Diesel Oil (LDO)

| Document number | ALP-OWN-FUL-002 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-15 |
| Status | Issued for tender / contract |
| Confidentiality | Restricted - Contract ALP-EPC-001 parties only |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | Owner's Engineer (discipline lead) | Owner's Engineer (project engineer) | Owner's Project Director |
| Signature / date | signed 2026-09-15 | signed 2026-09-15 | signed 2026-09-15 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-15 | Issued for tender / contract |

CASE STUDY - all organisations, data and signatures are fictional.

# 1. Purpose and operating philosophy

Light diesel oil is the secondary (back-up) fuel, used when natural gas is curtailed by the network operator or unavailable.

Expected use: up to 500 hours per year (emergency back-up fuel status under the environmental permit), typically in winter.

Autonomy: 72 hours of base-load operation on LDO from full storage.

Automatic transfer from gas to LDO on loss of gas pressure, without unit trip; manual transfer back to gas on load.

Start-up on LDO shall be possible (gas not available).

# 2. Fuel quality as delivered (supplier's specification, based on TS EN 590 automotive diesel, class B/F)

| Property | Unit | Limit / value | Test method |
| --- | --- | --- | --- |
| Density at 15 °C | kg/m³ | 820–845 | EN ISO 12185 |
| Kinematic viscosity at 40 °C | mm²/s | 2.0–4.5 | EN ISO 3104 |
| Flash point | °C | ≥ 55 | EN ISO 2719 |
| Cloud point / CFPP (winter grade) | °C | ≤ −5 / ≤ −15 | EN 23015 / EN 116 |
| Sulphur | mg/kg | ≤ 10 | EN ISO 20846 |
| Water | mg/kg | ≤ 200 | EN ISO 12937 |
| Total contamination (particulates) | mg/kg | ≤ 24 | EN 12662 |
| Ash | % m/m | ≤ 0.01 | EN ISO 6245 |
| Carbon residue (10 % distillation residue) | % m/m | ≤ 0.30 | EN ISO 10370 |
| FAME (biodiesel) content | % v/v | ≤ 7.0 | EN 14078 |
| Net calorific value (LHV) | MJ/kg | 42.6–43.2 (typical 42.9) | ASTM D240 |
| Sodium + potassium | mg/kg | ≤ 1.0 (as delivered, not guaranteed by supplier) | ASTM D3605 / ICP |
| Vanadium | mg/kg | ≤ 0.1 | ASTM D5708 |
| Lead | mg/kg | ≤ 0.5 | ICP |
| Calcium | mg/kg | ≤ 1.0 | ICP |
| Nitrogen (fuel-bound) | mg/kg | ≤ 150 | ASTM D4629 |

The supplier does not guarantee alkali metal content after road transport. Past deliveries to other plants showed Na+K up to 1.8 mg/kg after contamination with water in tanker trucks.

# 3. Supply logistics

Delivery by road tankers of 30–36 m³ from the refinery terminal (95 km).

The supplier can guarantee up to 25 trucks per day in winter emergencies.

The Owner will purchase the first fill of the LDO tanks; the Contractor provides LDO for its own testing beyond the first fill.

# 4. Owner requirements

Truck unloading station with at least 4 bays, metering, filtration and spill containment.

Storage: two tanks, each 50 % of the 72-hour autonomy, in a bunded area with foam fire protection (NFPA 11 / NFPA 30).

Water drain, sampling and fuel quality monitoring. Fuel treatment if needed to meet the gas turbine OEM limits at the burner.

Emissions on LDO: as per the environmental permit (see ALP-OWN-ENV-001).