## T1 2. Fuel quality as delivered
ALP-OWN-FUL-002 Rev 0 - 2. Fuel quality as delivered (supplier's specification, based on TS EN 590 automotive diesel, class B/F)
Property | Unit | Limit / value | Test method
Density at 15 °C | kg/m³ | 820–845 | EN ISO 12185
Kinematic viscosity at 40 °C | mm²/s | 2.0–4.5 | EN ISO 3104
Flash point | °C | ≥ 55 | EN ISO 2719
Cloud point / CFPP (winter grade) | °C | ≤ −5 / ≤ −15 | EN 23015 / EN 116
Sulphur | mg/kg | ≤ 10 | EN ISO 20846
Water | mg/kg | ≤ 200 | EN ISO 12937
Total contamination (particulates) | mg/kg | ≤ 24 | EN 12662
Ash | % m/m | ≤ 0.01 | EN ISO 6245
Carbon residue (10 % distillation residue) | % m/m | ≤ 0.30 | EN ISO 10370
FAME (biodiesel) content | % v/v | ≤ 7.0 | EN 14078
Net calorific value (LHV) | MJ/kg | 42.6–43.2 (typical 42.9) | ASTM D240
Sodium + potassium | mg/kg | ≤ 1.0 (as delivered, not guaranteed by supplier) | ASTM D3605 / ICP
Vanadium | mg/kg | ≤ 0.1 | ASTM D5708
Lead | mg/kg | ≤ 0.5 | ICP
Calcium | mg/kg | ≤ 1.0 | ICP
Nitrogen (fuel-bound) | mg/kg | ≤ 150 | ASTM D4629