Alpilla Enerji Üretim A.Ş.

Alpilla 600 MW Combined Cycle Power Plant

Site, Existing Infrastructure and Tie-in Points

| Document number | ALP-OWN-GEN-001 |
| --- | --- |
| Revision | 1 |
| Date | 2026-09-27 |
| Status | Issued for contract (Rev 1: drawings added, temporary area defined, TQ answers incorporated) |
| Confidentiality | Restricted - Contract ALP-EPC-001 parties only |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | Owner's Engineer (discipline lead) | Owner's Engineer (project engineer) | Owner's Project Director |
| Signature / date | signed 2026-09-27 | signed 2026-09-27 | signed 2026-09-27 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-14 | Issued for tender / contract |
| 1 | 2026-09-27 | Issued for contract (Rev 1: drawings added, temporary area defined, TQ answers incorporated) |

CASE STUDY - all organisations, data and signatures are fictional.

# 1. Site

Plot area 12.0 ha: rectangle 400 m (east–west) × 300 m (north–south), plant grid origin (E 0, N 0) at the south-west corner, plant north = true north. Grid coordinates in metres; geographic coordinates will be given in the land survey (UTM 35N).

Shoreline 60 m south of the southern plot boundary; the 60 m strip is public coastal land (no permanent structures except intake/outfall pipes and a temporary landing structure under separate permit).

Levelled by the Owner to +15.0 m (completed 2025); compaction records available.

A seasonal stream runs in a concrete channel (3 m × 2 m) along the western boundary (E 0–10 m), discharging to the sea. A 10 m maintenance/flood buffer from the channel is required by the water authority.

Usable area after the coastal setback, the channel buffer and a 5 m boundary landscaping strip: about 10.6 ha.

Temporary construction area (TP-A1): 5.04 ha field immediately north of the plot and west of the access road, E 0–180, N 320–600 (180 m × 280 m), leased by the Owner and available free of charge from 2027-03-01 until Taking-Over (TQ-012). The field is at +14.0 to +15.5 m, grassland, no services; the Contractor levels, fences and restores it.

Drawings: ALP-OWN-DWG-001 (external connections) and ALP-OWN-DWG-002 (site and construction area plan) form part of this document.

# 2. Existing features on the Site

| Feature | Location (plant grid) | Status / responsibility |
| --- | --- | --- |
| Buried 11 kV distribution cable of the regional utility | along the east boundary, E 390, N 0–300, depth 1.0 m | Owner to have it relocated outside the plot by 2027-06-30 |
| Abandoned concrete foundations of a former warehouse (about 1,200 m²) | E 300–360, N 20–60 | Contractor to demolish and remove (debris non-hazardous per Owner survey) |
| Owner's meteorological mast | E 20, N 280 | to be kept until Taking-Over; relocate at Contractor's cost if in conflict |
| Groundwater observation wells (3) | per survey | keep or replace |

# 3. Access and heavy transport

Existing asphalt access road (6 m wide) from the state road (1.2 km north) to the north gate at E 200, N 300.

State road has two bridges limited to 120 t gross vehicle weight. Components heavier than about 90 t (GT, generators, GSU transformers, HRSG modules above 90 t) cannot use the road.

Nearest port with heavy-lift quay (400 t crane) and RoRo ramp: 18 km by sea, 26 km by road.

No jetty or barge landing exists at the Site. A temporary barge landing on the coastal strip is permissible under a separate coastal permit, which the Owner can apply for once the Contractor provides the design (permit duration about 6 months).

# 4. Utilities and tie-in points available at the plot boundary

| Tie-in | Description | Location (plant grid) | Owner provides | Available by |
| --- | --- | --- | --- | --- |
| TP-G1 | Natural gas: 16" spur line from the transmission system with tap valve station (4.5 km) | E 380, N 300 (north-east corner), EL +14.0 flange | pipeline, isolation valve, insulating joint | 2028-06-30 |
| TP-E1 | 380 kV double-circuit overhead line from the TSO substation (7 km) | line gantry E 30, N 290 | line up to and including the dead-end tower; conductors to the gantry | 2028-07-15 (TQ-010) |
| TP-E2 | Construction power 34.5 kV, 5 MVA, from distribution network | north gate | connection agreement, meter | 2027-02-28 |
| TP-W1 | Potable water DN150 municipal main, 3 barg, 20 m³/h | north gate | connection and meter | 2027-02-28 |
| TP-S1 | Sanitary wastewater | — | no municipal sewer available; Contractor's packaged treatment plant discharges via the outfall (TQ-008) | — |
| TP-T1 | Telecommunication fibre (2 operators) | north gate | ducts to the plot boundary | 2027-06-30 |
| TP-R1 | Access road | north gate E 200, N 300 | existing road, maintained by Owner | available |
| TP-CW1 | Seawater intake head | about 650 m offshore, −12 m | seabed survey, marine permit | permit by 2027-04-30 |
| TP-CW2 | Outfall diffuser | about 350 m offshore, ≥ 250 m from intake | marine permit | permit by 2027-04-30 |
| TP-D1 | Storm water discharge | to the western stream channel (max 2 m³/s) or to sea | water authority consent | available |
| TP-L1 | LDO supply by road tankers | north gate | supply contract, first fill | first fill by first fire |
| TP-M1 | Temporary barge landing | public coastal strip, around E 120, N −40 | coastal permit (application by 2027-04-30) | 2027-09-30 (target) |
| TP-A1 | Temporary construction area 5.04 ha | E 0–180, N 320–600 | lease, free of charge | 2027-03-01 |

# 5. Routes of the external connections (see ALP-OWN-DWG-001)

| Connection | Route | Length |
| --- | --- | --- |
| Access road | from the state road (junction at about E 200, N 1,500) south to the north gate | 1.2 km |
| Gas spur line 16" | from the tap valve station on the transmission line (about E 900, N 4,800) south, crossing the state road, to TP-G1 | 4.5 km |
| 380 kV OHL | from TSO substation "Kıyı" (about E −4,500, N 5,600) south-east to the line gantry TP-E1 | 7.0 km |
| Potable water DN150, 34.5 kV line, fibre | along the access road from the state road to the north gate | 1.2 km |
| Heavy transport | by sea from the heavy-lift port (18 km) to the barge landing TP-M1 | 18 km |

# 6. Neighbours and constraints

Nearest residential receptor: village houses 900 m north-east of the plot centre.

Industrial neighbour (cement terminal) 700 m west.

Height restriction from the civil aviation authority: 120 m above grade within the plot (no conflict expected with a 60–70 m stack).