Alpilla Enerji Üretim A.Ş.

Alpilla 600 MW Combined Cycle Power Plant

Geotechnical Baseline Summary

| Document number | ALP-OWN-GEO-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-05 |
| Status | Issued for tender / contract (for information; Contractor to verify) |
| Confidentiality | Restricted - Contract ALP-EPC-001 parties only |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | Owner's Engineer (discipline lead) | Owner's Engineer (project engineer) | Owner's Project Director |
| Signature / date | signed 2026-09-05 | signed 2026-09-05 | signed 2026-09-05 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-05 | Issued for tender / contract |

CASE STUDY - all organisations, data and signatures are fictional.

# 1. Investigation

12 boreholes (30–45 m), 20 CPTu, 6 MASW profiles, laboratory testing (2025). Grade +15.0 m after Owner's levelling fill (1.5–3.0 m engineered fill, compacted to 95 % Standard Proctor).

# 2. Stratigraphy (typical)

| Depth below grade | Layer | Key parameters |
| --- | --- | --- |
| 0–2.5 m | engineered fill (sandy gravel) | γ 20 kN/m³ |
| 2.5–9 m | loose to medium dense silty sand (alluvium) | SPT N 6–18; liquefiable under DD-2 |
| 9–18 m | soft to firm clay with sand lenses | cu 30–70 kPa, compressible |
| 18–25 m | dense sand and gravel | SPT N > 40 |
| > 18–25 m | weathered to moderately weathered sandstone/marl | UCS 5–25 MPa |

Groundwater at +13.5 m (1.5 m below grade), tidal influence negligible, chloride 3,000–8,000 mg/l (brackish) — aggressive to concrete (XS/XA2).

Site class per TBDY 2018: ZD (Vs30 = 240 m/s). Site-specific PGA (DD-2): 0.45 g.

# 3. Owner's note

Deep foundations (bored piles to the sandstone) or ground improvement are expected for all heavy and vibrating structures. The baseline is for information; the Contractor is responsible for interpretation and confirmatory investigation (Sub-Clause 4.5).