Alpilla Enerji Üretim A.Ş.

Alpilla 600 MW Combined Cycle Power Plant

Seawater Quality and Marine Conditions

| Document number | ALP-OWN-MAR-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-12 |
| Status | Issued for tender / contract |
| Confidentiality | Restricted - Contract ALP-EPC-001 parties only |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | Owner's Engineer (discipline lead) | Owner's Engineer (project engineer) | Owner's Project Director |
| Signature / date | signed 2026-09-12 | signed 2026-09-12 | signed 2026-09-12 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-12 | Issued for tender / contract |

CASE STUDY - all organisations, data and signatures are fictional.

# 1. Basis

Twelve-month sampling campaign (September 2024 – August 2025) at three stations offshore of the Site (M1 at 300 m, M2 at 650 m, M3 at 1,000 m from the shoreline), monthly profiles at 1 m, 12 m and 30 m depth; continuous temperature logger at M2 (12 m). Bathymetry and current survey by the Owner's marine consultant (2025).

Important: the Sea of Marmara is a two-layer sea. The upper layer (Black Sea origin, brackish) lies above a sharp pycnocline at 20–25 m depth; the lower layer (Mediterranean origin) is saline, colder in summer and low in dissolved oxygen, with occasional H2S.

# 2. Bathymetry and hydrodynamics

Seabed slope about 1:45; −12 m depth at 550 m, −15 m at 650 m (station M2), −30 m at 1,000 m from the shoreline.

Tidal range negligible (< 0.1 m). Sea level variation from storm surge and barometric effects: −0.4 m to +0.6 m (100-year).

Surface currents 0.1–0.4 m/s, predominantly westward; at 12 m 0.05–0.25 m/s.

Waves: Hs 1-year 2.1 m; Hs 50-year 4.4 m (Tp 8.5 s), SW (lodos) direction.

# 3. Seawater temperature at 12 m (station M2)

| Month | Min (°C) | Mean (°C) | Max (°C) |
| --- | --- | --- | --- |
| Jan | 7.8 | 9.0 | 10.4 |
| Feb | 6.9 | 8.1 | 9.3 |
| Mar | 7.4 | 8.6 | 10.1 |
| Apr | 9.6 | 11.2 | 13.5 |
| May | 13.1 | 15.4 | 18.2 |
| Jun | 17.0 | 19.8 | 23.1 |
| Jul | 20.4 | 23.2 | 26.4 |
| Aug | 21.6 | 24.1 | 27.0 |
| Sep | 19.8 | 22.0 | 24.6 |
| Oct | 15.9 | 18.1 | 20.7 |
| Nov | 12.6 | 14.3 | 16.8 |
| Dec | 9.8 | 11.0 | 12.9 |
| Year | 6.9 | 15.4 | 27.0 |

At 30 m (lower layer) the temperature is stable at 14.5–15.5 °C all year. Note: the draft contract uses 16.0 °C as Site Reference seawater temperature; the measured annual mean at 12 m is 15.4 °C.

# 4. Chemical quality (upper layer, 12 m; lower layer, 30 m for information)

| Parameter | Unit | Upper layer min | Upper layer mean | Upper layer max | Lower layer mean |
| --- | --- | --- | --- | --- | --- |
| Salinity | PSU | 21.8 | 23.6 | 26.1 | 38.2 |
| Total dissolved solids | mg/l | 22,100 | 24,000 | 26,600 | 39,000 |
| Chloride | mg/l | 12,000 | 13,100 | 14,500 | 21,200 |
| Sodium | mg/l | 6,700 | 7,300 | 8,100 | 11,800 |
| Magnesium | mg/l | 800 | 870 | 960 | 1,410 |
| Calcium | mg/l | 250 | 275 | 305 | 440 |
| Potassium | mg/l | 245 | 268 | 300 | 430 |
| Sulphate | mg/l | 1,700 | 1,830 | 2,020 | 2,960 |
| Bicarbonate | mg/l | 150 | 165 | 185 | 145 |
| Boron | mg/l | 2.4 | 2.9 | 3.4 | 4.5 |
| Silica (SiO2) | mg/l | 0.2 | 0.7 | 1.6 | 1.1 |
| pH | - | 7.9 | 8.15 | 8.35 | 7.8 |
| Dissolved oxygen | mg/l | 6.1 | 7.8 | 9.4 | 1.2 (occasionally 0) |
| H2S | mg/l | n.d. | n.d. | n.d. | up to 0.4 |
| Ammonium (NH4-N) | mg/l | 0.02 | 0.09 | 0.35 | 0.15 |
| Iron (total) | mg/l | 0.02 | 0.05 | 0.14 | 0.08 |
| Manganese | mg/l | < 0.01 | 0.01 | 0.04 | 0.03 |
| TOC | mg/l | 1.2 | 2.1 | 3.8 | 1.1 |
| Oil and grease | mg/l | < 0.2 | < 0.2 | 0.6 | < 0.2 |
| Total suspended solids | mg/l | 3 | 9 | 48 (storm: 140) | 5 |
| Turbidity | NTU | 0.8 | 3.5 | 22 (storm: 65) | 1.5 |
| SDI15 (raw) | - | 4.8 | > 5 | not measurable | - |
| Chlorophyll-a | µg/l | 0.5 | 2.8 | 14 | 0.3 |

n.d. = not detected (< 0.02 mg/l).

# 5. Biology and fouling

Mussel (Mytilus galloprovincialis) settlement May–October, heavy.

Jellyfish blooms (Aurelia aurita, Mnemiopsis leidyi): up to 20 kg/m³ of seawater locally during blooms (June–September).

Mucilage ("sea snot") events: severe episodes in 2007 and 2021 (May–July) covering the surface and water column down to 25 m; the Owner requires the intake and screens to remain operable during such events.

Fish spawning season (restriction on marine works per EIA): 1 May – 30 September.

# 6. Owner requirements arising

Intake above the pycnocline, recommended depth −12 m, at least 3 m above seabed, velocity cap, intake velocity ≤ 0.15 m/s.

Outfall at least 250 m from the intake, discharge in the upper layer.

Materials: all seawater-wetted parts for chloride up to 14,500 mg/l and occasional H2S.