Alpilla Enerji Üretim A.Ş.

Alpilla 600 MW Combined Cycle Power Plant

Meteorological and Ambient Air Data

| Document number | ALP-OWN-MET-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-10 |
| Status | Issued for tender / contract |
| Confidentiality | Restricted - Contract ALP-EPC-001 parties only |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | Owner's Engineer (discipline lead) | Owner's Engineer (project engineer) | Owner's Project Director |
| Signature / date | signed 2026-09-10 | signed 2026-09-10 | signed 2026-09-10 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-10 | Issued for tender / contract |

CASE STUDY - all organisations, data and signatures are fictional.

# 1. Basis

Ten years (2015–2024) of hourly records from the Owner's on-site meteorological mast (installed 2014, 10 m and 60 m levels), checked against the nearest state meteorological station (22 km) and ERA5 reanalysis. Extremes use the state station's 1960–2024 record.

# 2. Air temperature (dry bulb, 2 m)

| Month | Mean (°C) | Mean daily max (°C) | Mean daily min (°C) | Abs. max (°C) | Abs. min (°C) | Mean RH (%) |
| --- | --- | --- | --- | --- | --- | --- |
| Jan | 6.1 | 9.2 | 3.3 | 20.8 | -11.4 | 80 |
| Feb | 6.6 | 10.1 | 3.5 | 23.1 | -9.6 | 78 |
| Mar | 8.6 | 12.6 | 5.0 | 27.9 | -6.2 | 77 |
| Apr | 12.5 | 16.9 | 8.6 | 30.4 | -1.1 | 75 |
| May | 17.2 | 21.6 | 13.1 | 33.5 | 4.8 | 73 |
| Jun | 22.0 | 26.4 | 17.6 | 37.2 | 9.4 | 69 |
| Jul | 24.6 | 29.0 | 20.3 | 39.6 | 13.1 | 66 |
| Aug | 24.5 | 28.9 | 20.4 | 38.8 | 13.5 | 67 |
| Sep | 20.6 | 25.0 | 16.6 | 35.2 | 7.9 | 70 |
| Oct | 16.0 | 20.1 | 12.4 | 31.0 | 1.2 | 75 |
| Nov | 11.5 | 15.2 | 8.2 | 26.3 | -4.3 | 78 |
| Dec | 8.0 | 11.3 | 5.0 | 21.7 | -8.8 | 80 |
| Year | 14.9 |  |  | 39.6 | -11.4 | 74 |

# 3. Design points (derived by the Owner)

| Design point | Dry bulb (°C) | Coincident RH (%) | Remark |
| --- | --- | --- | --- |
| Summer 0.4 % exceedance | 32.8 | 48 | cooling / HVAC design |
| Summer 1 % exceedance | 31.5 | 52 |  |
| Annual average | 14.9 | 74 | the contract Site Reference Condition uses 15.0 °C / 70 % |
| Winter 99 % | -2.6 | 85 | heating / freeze protection |
| Winter 99.6 % | -4.8 | 88 |  |
| Record maximum | 39.6 | 30 |  |
| Record minimum | -11.4 | 90 |  |

Barometric pressure: annual mean 1011.5 mbar at site grade (+15.0 m); range 985–1038 mbar. Relative humidity range: 18 % (foehn, rare) to 100 % (fog). Fog: 21 days/year, mostly November–February.

# 4. Wind

Prevailing directions: NE (poyraz, 38 % of hours) and SW (lodos, 22 %). Lodos storms bring onshore wind with sea spray. Mean wind speed at 10 m: 4.6 m/s. Basic wind speed (10 min, 10 m, 50-year): 30 m/s. Maximum recorded gust: 38 m/s (SW, 2019).

# 5. Precipitation, snow, lightning

Annual precipitation 680 mm (max 24 h: 142 mm, 2021). Design intensity 110 mm/h (10 min, 25-year). Snow: 6 days/year on average, maximum recorded depth 34 cm; ground snow load 0.75 kN/m². Thunderstorm days: 26/year; ground flash density 2.4 flashes/km²/year.

# 6. Airborne salt and dust (measured by the Owner, 2023–2025)

| Parameter | Annual mean | 95th percentile | Maximum (event) | Remark |
| --- | --- | --- | --- | --- |
| Sea-salt aerosol (as NaCl), at 10 m | 14 µg/m³ | 62 µg/m³ | 165 µg/m³ | lodos storms, 2–4 events/year of 1–3 days |
| Sodium (Na) in PM10 | 4.5 µg/m³ | 20 µg/m³ | 54 µg/m³ |  |
| Chloride deposition (ISO 9225 wet candle) | 180 mg/m²·day |  | 420 mg/m²·day | ISO 9223 category S3 |
| PM10 | 34 µg/m³ | 78 µg/m³ | 260 µg/m³ | Saharan dust episodes in spring |
| PM2.5 | 18 µg/m³ | 41 µg/m³ | 120 µg/m³ |  |

Atmospheric corrosivity per ISO 9223 is C5 (chloride-driven). The Owner considers salt ingestion into the gas turbine a major risk and expects the inlet air filtration to be designed for the event maximum above.

# 7. Performance test correction range

The Owner proposes that performance tests may be carried out at ambient temperatures between 5 °C and 30 °C; outside this range the test shall be postponed unless both Parties agree.