## T1 2. Air temperature (dry bulb
ALP-OWN-MET-001 Rev 0 - 2. Air temperature (dry bulb, 2 m)
Month | Mean (°C) | Mean daily max (°C) | Mean daily min (°C) | Abs. max (°C) | Abs. min (°C) | Mean RH (%)
Jan | 6.1 | 9.2 | 3.3 | 20.8 | -11.4 | 80
Feb | 6.6 | 10.1 | 3.5 | 23.1 | -9.6 | 78
Mar | 8.6 | 12.6 | 5 | 27.9 | -6.2 | 77
Apr | 12.5 | 16.9 | 8.6 | 30.4 | -1.1 | 75
May | 17.2 | 21.6 | 13.1 | 33.5 | 4.8 | 73
Jun | 22 | 26.4 | 17.6 | 37.2 | 9.4 | 69
Jul | 24.6 | 29 | 20.3 | 39.6 | 13.1 | 66
Aug | 24.5 | 28.9 | 20.4 | 38.8 | 13.5 | 67
Sep | 20.6 | 25 | 16.6 | 35.2 | 7.9 | 70
Oct | 16 | 20.1 | 12.4 | 31 | 1.2 | 75
Nov | 11.5 | 15.2 | 8.2 | 26.3 | -4.3 | 78
Dec | 8 | 11.3 | 5 | 21.7 | -8.8 | 80
Year | 14.9 |  |  | 39.6 | -11.4 | 74

## T2 3. Design points (derived by
ALP-OWN-MET-001 Rev 0 - 3. Design points (derived by the Owner)
Design point | Dry bulb (°C) | Coincident RH (%) | Remark
Summer 0.4 % exceedance | 32.8 | 48 | cooling / HVAC design
Summer 1 % exceedance | 31.5 | 52
Annual average | 14.9 | 74 | the contract Site Reference Condition uses 15.0 °C / 70 %
Winter 99 % | -2.6 | 85 | heating / freeze protection
Winter 99.6 % | -4.8 | 88
Record maximum | 39.6 | 30
Record minimum | -11.4 | 90

## T3 6. Airborne salt and dust (m
ALP-OWN-MET-001 Rev 0 - 6. Airborne salt and dust (measured by the Owner, 2023–2025)
Parameter | Annual mean | 95th percentile | Maximum (event) | Remark
Sea-salt aerosol (as NaCl), at 10 m | 14 µg/m³ | 62 µg/m³ | 165 µg/m³ | lodos storms, 2–4 events/year of 1–3 days
Sodium (Na) in PM10 | 4.5 µg/m³ | 20 µg/m³ | 54 µg/m³
Chloride deposition (ISO 9225 wet candle) | 180 mg/m²·day |  | 420 mg/m²·day | ISO 9223 category S3
PM10 | 34 µg/m³ | 78 µg/m³ | 260 µg/m³ | Saharan dust episodes in spring
PM2.5 | 18 µg/m³ | 41 µg/m³ | 120 µg/m³