# Alpilla 600 MW Combined Cycle Power Plant
Plant Heat and Mass Balances

| Document number | ALP-EPC-00000-PR-HMB-0001 |
| --- | --- |
| Description | 9 cases |
| Revision / status | Rev A - IFR, issued 2026-12-14 |
| Originator | Istanbul EPC Mühendislik ve Taahhüt A.Ş. |
| Discipline / type | process / HMB Heat and mass balance |
| Review class | approval (Basic Design Package) |
| Basis | requirement:ER-03.02, requirement:ER-04.06 |

| Rev | Purpose | Date | Description | Prepared | Checked | Approved |
| --- | --- | --- | --- | --- | --- | --- |
| A | IFR | 2026-12-14 | First issue for Owner approval (CW rise open, TQ-IEC-026) | EPCE | EPC process lead | EPC engineering manager |

# 1. Purpose and basis

This document gives the plant heat and mass balances of all design and guarantee cases: the power island performance data of Imaginary Electric, the EPC piping pressure and temperature drops, the balance-of-plant auxiliary loads and the other plant fuel consumers. Every stream enthalpy is recomputed (IAPWS-IF97 for water / steam, ideal-gas mixtures for air, fuel and flue gas), every node is closed for mass and energy, and each case is checked against the guarantees and limits it covers. Power island data:

SRC-IECE-0005 Power island off-design heat balances (case book) - Rev A

SRC-OWNR-0004 Secondary fuel: light diesel oil (LDO)

# 2. Cases

| Case | Description | Fuel | Ambient degC | RH % | Seawater degC | GT load % |
| --- | --- | --- | --- | --- | --- | --- |
| MAX-NG-100 | Maximum ambient (40 degC) with maximum seawater (27 degC), natural gas, base load | gas | 40 | 35 | 27 | 100 |
| MIN-NG-100 | Minimum ambient for full capability (-8 degC), natural gas, base load | gas | -8 | 80 | 6.9 | 100 |
| SRC-LDO-100 | Site Reference Conditions, LDO with water injection, base load (guarantee PG-15/16) | LDO | 15 | 70 | 16 | 100 |
| SRC-NG-060 | Site Reference Conditions, natural gas, 60 % plant net load (guarantee PG-03) | gas | 15 | 70 | 16 | 55.78 |
| SRC-NG-100 | Site Reference Conditions, natural gas, base load (guarantee case) | gas | 15 | 70 | 16 | 100 |
| SRC-NG-GT80 | Site Reference Conditions, natural gas, GT at 80 % load | gas | 15 | 70 | 16 | 80 |
| SRC-NG-MEL | Site Reference Conditions, natural gas, GT at minimum emissions-compliant load (30 %, low-load extension) | gas | 15 | 70 | 16 | 30 |
| SUM-NG-100 | Summer design (32.8 degC, 0.4 %), natural gas, base load | gas | 32.8 | 45 | 24 | 100 |
| WIN-NG-100 | Winter design (-4.8 degC, 99.6 %), natural gas, base load (GT at output limit) | gas | -4.8 | 80 | 8 | 100 |

# 3. Results

| Item | MAX-NG-100 | MIN-NG-100 | SRC-LDO-100 | SRC-NG-060 | SRC-NG-100 | SRC-NG-GT80 | SRC-NG-MEL | SUM-NG-100 | WIN-NG-100 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GT output MW | 348.2 | 470.0 | 400.5 | 237.1 | 425.0 | 340.0 | 127.5 | 372.8 | 470.0 |
| ST output MW | 175.8 | 204.9 | 178.4 | 140.7 | 200.7 | 175.1 | 94.4 | 184.5 | 207.9 |
| Gross output MW | 524.1 | 674.9 | 578.9 | 377.8 | 625.7 | 515.0 | 221.9 | 557.3 | 677.9 |
| Auxiliaries + transformer losses MW | 10.8 | 12.1 | 11.1 | 9.3 | 11.8 | 10.5 | 8.1 | 11.1 | 12.2 |
| Net output MW | 513.3 | 662.8 | 567.8 | 368.5 | 613.9 | 504.5 | 213.8 | 546.2 | 665.7 |
| Heat input LHV MW | 832.2 | 1,058.3 | 961.2 | 635.1 | 983.0 | 827.3 | 412.9 | 881.2 | 1,063.8 |
| of which other plant fuel consumers MW | 0.8 | 2.3 | 0.0 | 1.0 | 1.5 | 1.3 | 0.6 | 0.8 | 2.3 |
| Net heat rate LHV kJ/kWh | 5,836.4 | 5,748.2 | 6,094.4 | 6,204.0 | 5,764.2 | 5,903.5 | 6,952.8 | 5,807.7 | 5,752.8 |
| Net efficiency % | 61.7 | 62.6 | 59.1 | 58.0 | 62.5 | 61.0 | 51.8 | 62.0 | 62.6 |

# 4. Checks against guarantees and limits

| Case | Result | Check |
| --- | --- | --- |
| MIN-NG-100 | WARN | CW temperature rise 7.20 K vs DP-CASE-0015 <= 7.0 K (Condenser cooling water temperature rise) |
| MIN-NG-100 | INFO | net export 662.8 MW vs DP-OWNR-0051 connection capacity 640 MW (this case); capability above the capacity, export limited: 640 MW net at the 380 kV revenue meters (TQ-027, TP-E1) |
| SRC-LDO-100 | OK | guarantee cover: at IG-09/IG-10 limits and this HMB's auxiliaries the net plant is 560.9 MW / 6,139 kJ/kWh vs Owner PG-15 560 MW / PG-16 6,150 kJ/kWh |
| SRC-NG-100 | OK | guarantee cover: at IG-01/IG-02 limits and this HMB's auxiliaries the net plant is 603.2 MW / 5,847 kJ/kWh vs Owner PG-01 600 MW / PG-02 5,860 kJ/kWh |
| WIN-NG-100 | WARN | CW temperature rise 7.28 K vs DP-CASE-0015 <= 7.0 K (Condenser cooling water temperature rise) |
| WIN-NG-100 | INFO | net export 665.7 MW vs DP-OWNR-0051 connection capacity 640 MW (this case); capability above the capacity, export limited: 640 MW net at the 380 kV revenue meters (TQ-027, TP-E1) |

# 5. Auxiliary loads at Site Reference Conditions

| Id | Consumer | Basis | kW |
| --- | --- | --- | --- |
| AL-01 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | fixed | 1,180 |
| AL-02 | GT generator auxiliaries (seal oil, stator water, excitation) | fixed | 420 |
| AL-03 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | fixed | 380 |
| AL-04 | ST generator auxiliaries (excitation, TEWAC) | fixed | 260 |
| AL-05 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | fixed | 210 |
| AL-06 | Condenser vacuum pump (1 running) | fixed | 75 |
| AL-07 | Turbine control system and UPS load | fixed | 60 |
| AL-08 | GT GSU losses at this case load | fixed | 1,107 |
| AL-09 | ST GSU losses at this case load | fixed | 584 |
| AL-10 | Boiler feed pumps 2 x 100 % (1 running) | enthalpy rise 2,981 kW / motor 0.965 | 3,089 |
| AL-11 | Condensate extraction pumps 2 x 100 % (1 running) | enthalpy rise 282 kW / motor 0.95 | 297 |
| AL-12 | Circulating water pumps 2 x 50 % | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | 1,939 |
| AL-13 | Closed cooling water pumps | fixed | 160 |
| AL-14 | Electro-chlorination | fixed | 180 |
| AL-15 | Water treatment (SWRO, demineralisation, condensate polishing) | fixed | 250 |
| AL-16 | Compressed air | fixed | 180 |
| AL-17 | HVAC and lighting | fixed | 750 |
| AL-18 | Ammonia and chemical dosing | fixed | 40 |
| AL-19 | Fuel gas receiving station | fixed | 60 |
| AL-20 | LDO system (standby on gas) | fixed | 30 |
| AL-21 | UAT and MV/LV transformer losses | fixed | 240 |
| AL-22 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | fixed | 300 |

# 6. Notes

Performance cases are at continuous blowdown closed (as during the performance tests); the demineralised water make-up, blowdown and cycle losses in normal operation are given in the Plant Water Balance ALP-EPC-00000-PR-STU-0001.

The station gas preheaters (indirect water-bath heaters, DEC-EPCE-0014) burn plant fuel downstream of the fiscal metering: their fuel (stream 31) is part of the plant heat input and of the net heat rate, not of the power island (gross) heat rate.

Auxiliary loads of the balance of plant follow the preliminary equipment sizing (DEC-EPCE-0014 / 0015 / 0016) and are updated with the electrical load list.

The diagrams of all cases follow this report (A1 sheets, stream data in the boxes, node balances in the case workbooks ALP-HMB-<case>.xlsx).