## Codes and standards
Alpilla 600 MW Combined Cycle Power Plant - Codes, standards and regulations register (Appendix A.19)
engine standards_register v1.0.0 ¦ generated 2026-09-28T03:56:06Z by SETUP ¦ data b66cf958da23f2cb
ID | Precedence | Kind | Jurisdiction | Code | Title | Edition | Issuer | Disciplines | Applies to | Responsible | Authority | Requirements | Deviation / clarification | Status | Agreed by | Agreed in
REF-CONS-0028 | 1 | law | TR | Law 167 | Groundwater Law (Yeralti Sulari Hakkinda Kanun) | 1960, as amended | TBMM | civil | construction dewatering and groundwater wells | Istanbul EPC | DSI |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0026 | 1 | law | TR | Law 2863 | Law on the Protection of Cultural and Natural Assets | 1983, as amended | TBMM | civil | archaeological chance-find procedure during excavation | Istanbul EPC | Museum Dir. |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0001 | 1 | law | TR | Law 2872 | Environmental Law (Cevre Kanunu) | 1983, as amended | TBMM | hse | all environmental obligations; EIA conditions | Istanbul EPC, Imaginary Electric | Ministry Env. | ER-14.01 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0029 | 1 | law | TR | Law 2918 | Highway Traffic Law (Karayollari Trafik Kanunu) | 1983, as amended | TBMM | general | abnormal load transport permits | Istanbul EPC | KGM | ER-02.14 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0015 | 1 | law | TR | Law 3194 | Zoning Law (Imar Kanunu) | 1985, as amended | TBMM | civil | building permit and occupancy permit | Istanbul EPC, Imaginary Electric | Municipality |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0018 | 1 | law | TR | Law 3621 | Coastal Law (Kiyi Kanunu) | 1990, as amended | TBMM | civil hse | intake and outfall pipelines and the temporary barge landing on the coastal strip | Istanbul EPC | Ministry Env. |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0027 | 1 | law | TR | Law 4646 | Natural Gas Market Law (Dogal Gaz Piyasasi Kanunu) | 2001, as amended | TBMM | process | gas connection, metering and station approval by the network operator | Istanbul EPC | Gas network operator | ER-18.03 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0011 | 1 | law | TR | Law 6331 | Occupational Health and Safety Law (Is Sagligi ve Guvenligi Kanunu) | 2012 | TBMM | hse | design and construction safety, risk assessment | Istanbul EPC, Imaginary Electric | MoLSS | ER-14.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0019 | 1 | law | TR | Law 6446 | Electricity Market Law (Elektrik Piyasasi Kanunu) | 2013 | TBMM | electrical | generation licence, connection and system use | Owner | EMRA |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0030 | 1 | law | TR | Law 7381 | Nuclear Regulatory Law (Nukleer Duzenleme Kanunu) | 2022 | TBMM | hse | licensing of radiation sources for radiographic testing | Istanbul EPC, Imaginary Electric | NDK | ER-15.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0012 | 1 | regulation | TR | Construction OHS Regulation | Regulation on OHS in Construction Works (Yapi Islerinde ISG Yonetmeligi) | 2013 | MOLSS | hse | site safety plan, coordination between contractors | Istanbul EPC, Imaginary Electric | MoLSS | ER-14.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0002 | 1 | regulation | TR | EIA Regulation | Environmental Impact Assessment Regulation (CED Yonetmeligi) | 2022 | MOEUCC | hse | conditions of the positive EIA decision (ALP-OWN-ENV-001); changes to the project need an EIA review | Istanbul EPC, Imaginary Electric | Ministry Env. | ER-14.01 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0022 | 1 | regulation | TR | Earthing Regulation | Regulation on Earthing in Electrical Installations (Elektrik Tesislerinde Topraklamalar Yonetmeligi) | 2001 | MENR | electrical | earthing system design and verification | Istanbul EPC, Imaginary Electric | MENR | ER-11.07 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0003 | 1 | regulation | TR | Env. Permit Regulation | Environmental Permit and Licence Regulation (Cevre Izin ve Lisans Yonetmeligi) | 2014 | MOEUCC | hse | temporary activity certificate and environmental permit (air emissions, discharges) | Istanbul EPC, Imaginary Electric | Ministry Env. |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0014 | 1 | regulation | TR | Explosive Atmospheres Regulation | Regulation on Protection of Workers from Explosive Atmospheres | 2013 | MOLSS | hse electrical | explosion protection document for the gas station, GT package, LDO, H2 | Istanbul EPC, Imaginary Electric | MoLSS | ER-14.06 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0016 | 1 | regulation | TR | Fire Regulation | Regulation on Fire Protection of Buildings (Binalarin Yangindan Korunmasi Hakkinda Yonetmelik) | 2007, as amended | Presidency | hse | fire protection design approval of buildings | Istanbul EPC, Imaginary Electric | Municipality | ER-10.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0021 | 1 | regulation | TR | Heavy Current Regulation | Regulation on Electrical Heavy Current Installations (Elektrik Kuvvetli Akim Tesisleri Yonetmeligi) | 2000 | MENR | electrical | HV/MV installations, clearances | Istanbul EPC, Imaginary Electric | MENR |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0005 | 1 | regulation | TR | LCP Regulation | Large Combustion Plants Regulation (Buyuk Yakma Tesisleri Yonetmeligi) | 2010 | MOEUCC | hse process | emission limit values of gas turbines > 50 MWth; the stricter EIA limits (ER-14.02) govern | Istanbul EPC, Imaginary Electric | Ministry Env. | ER-14.02 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0010 | 1 | regulation | TR | Major Accident Regulation | Regulation on Prevention and Mitigation of Major Industrial Accidents (Seveso III) | 2019 | MOEUCC | hse process | LDO storage about 5,850 t (2 x 3,500 m3) exceeds the 2,500 t lower-tier threshold for petroleum products: notification and Major Accident Prevention Policy; aqueous ammonia and hydrogen inventories added by the aggregation rule | Istanbul EPC, Imaginary Electric | Ministry Env. | ER-03.08 ER-06.04 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0007 | 1 | regulation | TR | Noise Regulation | Environmental Noise Control Regulation (Cevresel Gurultunun Kontrolu Yonetmeligi) | edition at Base Date | MOEUCC | hse | noise at the receptors (45/55 dB(A)), construction noise assessment | Istanbul EPC, Imaginary Electric | Ministry Env. | ER-14.03 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0004 | 1 | regulation | TR | SKHKKY | Industrial Air Pollution Control Regulation (Sanayi Kaynakli Hava Kirliliginin Kontrolu Yonetmeligi) | 2009 | MOEUCC | hse process | stack height and dispersion, emission measurement | Istanbul EPC, Imaginary Electric | Ministry Env. | ER-06.06 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0009 | 1 | regulation | TR | Soil Regulation | Soil Pollution Control and Point-Source Contaminated Sites Regulation | 2010 | MOEUCC | hse civil | baseline and closure soil condition, spill prevention | Istanbul EPC | Ministry Env. |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0017 | 1 | regulation | TR | TBDY 2018 | Turkish Building Earthquake Code (Turkiye Bina Deprem Yonetmeligi) | 2018 | AFAD | civil structural | seismic design of buildings and structures; equipment anchorage | Istanbul EPC, Imaginary Electric | Municipality | ER-02.06 | Governs seismic design; EN 1998 not used. | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0006 | 1 | regulation | TR | WPCR | Water Pollution Control Regulation (Su Kirliligi Kontrolu Yonetmeligi) | 2004 | MOEUCC | hse process | sea discharge limits of process, sanitary and cooling water effluents | Istanbul EPC | Ministry Env. | ER-08.04 ER-08.05 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0008 | 1 | regulation | TR | Waste Regulation | Waste Management Regulation (Atik Yonetimi Yonetmeligi) | 2015 | MOEUCC | hse | construction and operation waste, hazardous waste | Istanbul EPC | Ministry Env. |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0013 | 1 | regulation | TR | Work Equipment Regulation | Regulation on Health and Safety in the Use of Work Equipment | 2013 | MOLSS | hse mechanical | first and periodic inspection of lifting and pressure equipment before use | Istanbul EPC, Imaginary Electric | MoLSS |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0025 | 1 | regulation | EU | ATEX 2014/34/EU | ATEX Equipment Directive, transposed as the regulation on equipment for potentially explosive atmospheres | 2014/34/EU | EU / MoIT | electrical mechanical | equipment in hazardous areas | Istanbul EPC, Imaginary Electric | MoIT | ER-14.06 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0024 | 1 | regulation | EU | Machinery Directive 2006/42/EC | Machinery Directive, transposed as the Machinery Safety Regulation (Makine Emniyeti Yonetmeligi) | 2006/42/EC | EU / MoIT | mechanical | CE marking and declarations of conformity of machinery packages (GT, ST, pumps, cranes) | Istanbul EPC, Imaginary Electric | MoIT |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0023 | 1 | regulation | EU | PED 2014/68/EU | Pressure Equipment Directive, transposed as the Pressure Equipment Regulation (Basincli Ekipmanlar Yonetmeligi) | 2014/68/EU | EU / MoIT | mechanical piping | conformity assessment of pressure equipment by a notified body (HRSG, vessels, piping) | Istanbul EPC, Imaginary Electric | MoIT | ER-06.02 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0020 | 2 | grid_code | TR | Grid Code | Electricity Grid Regulation (Elektrik Sebeke Yonetmeligi) - TSO Grid Code | edition at Base Date | EMRA | electrical i_and_c | generator performance, protection, frequency and voltage control, compliance tests | Istanbul EPC, Imaginary Electric | TSO | ER-01.07 ER-04.07 ER-16.03 ER-18.02 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0089 | 4 | standard | TR | TS 500 | Requirements for design and construction of reinforced concrete structures | edition at Base Date | TSE | civil structural | reinforced concrete (with EN 1992) | Istanbul EPC |  | ER-13.04 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0096 | 4 | standard | TR | TS EN 590 | Automotive fuels - Diesel - Requirements and test methods (basis of the LDO specification) | edition at Base Date | TSE | process | LDO delivered by the Owner's supplier (TP-L1) | Owner |  | ER-03.07 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0093 | 4 | guideline | US | ACI 351.3R | Report on Foundations for Dynamic Equipment | edition at Base Date | ACI | civil | turbine-generator foundations (IEC load data, IF-43) | Istanbul EPC |  | ER-13.01 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0066 | 4 | standard | US | API 650 | Welded Tanks for Oil Storage | edition at Base Date | API | mechanical | LDO and water storage tanks | Istanbul EPC |  | ER-03.08 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0060 | 4 | standard | US | ASME B16.25 | Buttwelding Ends | edition at Base Date | ASME | piping | weld-end terminal points | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0061 | 4 | standard | US | ASME B16.34 | Valves - Flanged, Threaded, and Welding End | edition at Base Date | ASME | piping | valves | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0059 | 4 | standard | US | ASME B16.5 | Pipe Flanges and Flanged Fittings NPS 1/2 through NPS 24 | edition at Base Date | ASME | piping | flanged terminal points | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0055 | 4 | standard | US | ASME B31.1 | Power Piping | edition at Base Date | ASME | piping | steam, feedwater, condensate and utility piping | Istanbul EPC |  |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0056 | 4 | standard | US | ASME B31.3 | Process Piping | edition at Base Date | ASME | piping | chemical, ammonia and LDO piping | Istanbul EPC |  |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0057 | 4 | standard | US | ASME B31.8 | Gas Transmission and Distribution Piping Systems | edition at Base Date | ASME | piping | gas receiving station and plant gas piping | Istanbul EPC |  | ER-18.03 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-SETUP-0002 | 4 | standard | US | ASME B36.10M | Welded and Seamless Wrought Steel Pipe |  | ASME | piping | pipe dimensions and wall thicknesses (pipe_size records) | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0046 | 4 | standard | US | ASME PTC 12.2 | Performance Test Code on Steam Surface Condensers | edition at Base Date | ASME | process | condenser performance test | Imaginary Electric |  | ER-07.08 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0034 | 4 | standard | US | ASME PTC 22 | Performance Test Code on Gas Turbines | edition at Base Date | ASME | process | GT performance tests | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0044 | 4 | standard | US | ASME PTC 4.4 | Performance Test Code on Gas Turbine Heat Recovery Steam Generators | edition at Base Date | ASME | process | HRSG performance tests | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0050 | 4 | standard | US | ASME PTC 46 | Performance Test Code on Overall Plant Performance | edition at Base Date | ASME | process | plant performance tests and correction curves | Istanbul EPC, Imaginary Electric |  | ER-16.04 ER-12.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0036 | 4 | standard | US | ASME PTC 6 | Performance Test Code on Steam Turbines | edition at Base Date | ASME | process | ST performance tests (flow section in the main steam line) | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0042 | 4 | standard | US | ASME Section I | ASME BPVC Section I - Rules for Construction of Power Boilers | edition at Base Date | ASME | mechanical | HRSG pressure parts, boiler external piping | Istanbul EPC, Imaginary Electric |  | ER-06.02 | Selected for the HRSG (IEC); PED module G by a notified body; boiler external piping by the EPC to ASME Section I / B31.1. | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0063 | 4 | standard | US | ASME Section IX | ASME BPVC Section IX - Welding, Brazing and Fusing Qualifications | edition at Base Date | ASME | mechanical piping | welding procedure and welder qualification (alternative EN ISO 15614) | Istanbul EPC, Imaginary Electric |  | ER-15.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0062 | 4 | standard | US | ASME Section VIII Div. 1 | ASME BPVC Section VIII Division 1 - Pressure Vessels | edition at Base Date | ASME | mechanical | BOP pressure vessels (flash tanks, air receivers, deaeration) | Istanbul EPC |  |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0065 | 4 | standard | EU | EN 10204 | Metallic products - Types of inspection documents | 2004 | CEN | mechanical | material certificates 3.1 / 3.2 | Istanbul EPC, Imaginary Electric |  | ER-15.04 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0058 | 4 | standard | EU | EN 12186 | Gas infrastructure - Gas pressure regulating stations for transmission and distribution | edition at Base Date | CEN | process piping | gas pressure regulation and safety devices (slam-shut, relief) | Istanbul EPC |  | ER-03.04 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0043 | 4 | standard | EU | EN 12952 | Water-tube boilers and auxiliary installations (all parts) | edition at Base Date | CEN | mechanical | HRSG - alternative to ASME Section I (ER-06.02); EN 12952-3 fatigue assessment for cyclic operation (ER-06.05) | Imaginary Electric |  | ER-06.02 ER-06.05 | HRSG designed to ASME Section I with PED conformity by a notified body (module G); EN 12952-3 applied only for the low-cycle fatigue assessment of the thick-walled parts (HP drum, SH/RH outlet headers) per ER-06.05. | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0072 | 4 | standard | EU | EN 13001 | Cranes - General design (all parts) | edition at Base Date | CEN | mechanical | turbine hall EOT crane and hoists | Istanbul EPC |  | ER-10.07 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0084 | 4 | standard | EU | EN 14181 | Stationary source emissions - Quality assurance of automated measuring systems | edition at Base Date | CEN | i_and_c hse | CEMS QAL1/QAL2/QAL3/AST | Istanbul EPC |  | ER-12.04 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0086 | 4 | standard | EU | EN 15259 | Air quality - Measurement of stationary source emissions - Measurement sections and sites | edition at Base Date | CEN | mechanical hse | stack measurement ports and platforms | Istanbul EPC |  | ER-06.06 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0085 | 4 | standard | EU | EN 15267-3 | Air quality - Certification of automated measuring systems - Part 3 | edition at Base Date | CEN | i_and_c | certified CEMS analysers | Istanbul EPC |  | ER-12.04 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0047 | 4 | standard | EU | EN 1822 | High efficiency air filters (EPA, HEPA and ULPA) | edition at Base Date | CEN | mechanical | GT inlet air final filter class | Imaginary Electric |  | ER-05.02 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0087 | 4 | standard | EU | EN 1990 | Eurocode - Basis of structural design (with EN 1991 actions) | edition at Base Date | CEN | civil structural | structural design basis and actions (wind, snow, thermal) | Istanbul EPC |  |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0088 | 4 | standard | EU | EN 1992 | Eurocode 2 - Design of concrete structures | edition at Base Date | CEN | civil structural | concrete structures and foundations | Istanbul EPC |  | ER-13.04 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0090 | 4 | standard | EU | EN 1993 | Eurocode 3 - Design of steel structures | edition at Base Date | CEN | structural | steel structures | Istanbul EPC |  | ER-13.03 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0091 | 4 | standard | EU | EN ISO 1461 | Hot dip galvanized coatings on fabricated iron and steel articles | edition at Base Date | CEN/ISO | structural | galvanizing of structural steel | Istanbul EPC |  | ER-13.03 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0064 | 4 | standard | EU | EN ISO 15614 | Specification and qualification of welding procedures for metallic materials - Welding procedure test | edition at Base Date | CEN/ISO | mechanical piping | welding procedure qualification (alternative ASME IX) | Istanbul EPC, Imaginary Electric |  | ER-15.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0045 | 4 | standard | US | HEI 2629 | HEI Standards for Steam Surface Condensers | 12th edition | HEI | mechanical | condenser thermal and mechanical design | Imaginary Electric |  | ER-07.07 ER-07.08 ER-07.09 ER-07.10 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0053 | 4 | guideline | international | IAPWS TGD | IAPWS Technical Guidance Documents on cycle chemistry (HRSG, AVT, instrumentation) | edition at Base Date | IAPWS | process | water/steam chemistry of the HRSG plant | Istanbul EPC, Imaginary Electric |  | ER-09.03 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0052 | 4 | guideline | international | IAPWS-IF97 | Industrial Formulation 1997 for the Thermodynamic Properties of Water and Steam | 1997 | IAPWS | process | water/steam properties in heat balances and tests | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0037 | 4 | standard | international | IEC 60034-1 | Rotating electrical machines - Part 1: Rating and performance | edition at Base Date | IEC | electrical | generators; also -3 for turbine-type generators | Imaginary Electric |  | ER-11.02 ER-04.08 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0035 | 4 | standard | international | IEC 60045-1 | Steam turbines - Part 1: Specifications | edition at Base Date | IEC | mechanical | steam turbine; rated and design conditions | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0040 | 4 | standard | international | IEC 60076 | Power transformers (all parts) | edition at Base Date | IEC | electrical | GSU, UAT and auxiliary transformers | Istanbul EPC, Imaginary Electric |  | ER-11.03 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0083 | 4 | standard | international | IEC 60079-10-1 | Explosive atmospheres - Classification of areas - Explosive gas atmospheres | edition at Base Date | IEC | electrical hse | hazardous area classification | Istanbul EPC, Imaginary Electric |  | ER-14.06 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0077 | 4 | standard | international | IEC 60364 | Low-voltage electrical installations (all parts) | edition at Base Date | IEC | electrical | LV installations | Istanbul EPC |  |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0080 | 4 | standard | international | IEC 60815 | Selection and dimensioning of high-voltage insulators for polluted conditions | edition at Base Date | IEC | electrical | creepage distances of outdoor insulation (salt air) | Istanbul EPC, Imaginary Electric |  | ER-02.10 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0075 | 4 | standard | international | IEC 60909 | Short-circuit currents in three-phase AC systems | edition at Base Date | IEC | electrical | short-circuit studies (TP-E1, IF-34..IF-38) | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0081 | 4 | standard | international | IEC 61511 | Functional safety - Safety instrumented systems for the process industry sector | edition at Base Date | IEC | i_and_c | SIS incl. burner management and HRSG protection | Istanbul EPC, Imaginary Electric |  | ER-12.03 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0076 | 4 | standard | international | IEC 61850 | Communication networks and systems for power utility automation | edition at Base Date | IEC | electrical i_and_c | substation automation and protection interface (IF-41) | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0073 | 4 | standard | international | IEC 61936-1 | Power installations exceeding 1 kV AC - Part 1: Common rules | edition at Base Date | IEC | electrical | HV/MV installations, transformer fire separation | Istanbul EPC |  |  |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0074 | 4 | standard | international | IEC 62271-203 | High-voltage switchgear - Gas-insulated metal-enclosed switchgear for rated voltages above 52 kV | edition at Base Date | IEC | electrical | 380 kV GIS | Istanbul EPC |  | ER-11.01 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0079 | 4 | standard | international | IEC 62305 | Protection against lightning (all parts) | edition at Base Date | IEC | electrical | lightning protection and risk assessment | Istanbul EPC |  | ER-02.12 ER-11.07 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0082 | 4 | standard | international | IEC 62443 | Security for industrial automation and control systems (all parts) | edition at Base Date | IEC | i_and_c | OT cybersecurity SL2 (DCS, TCS, zone/conduit at IF-40) | Istanbul EPC, Imaginary Electric |  | ER-05.06 ER-12.07 | IEC TCS certified to IEC 62443-4-1 / -4-2 components, system SL2 per IEC 62443-3-3; zone/conduit boundary and firewall at IF-40 by the EPC. | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0041 | 4 | standard | international | IEC 62770 | Fluids for electrotechnical applications - Unused natural esters for transformers | edition at Base Date | IEC | electrical | GSU insulating liquid (natural ester) | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0038 | 4 | standard | international | IEC/IEEE 62271-37-013 | High-voltage switchgear - Alternating-current generator circuit-breakers | edition at Base Date | IEC/IEEE | electrical | generator circuit breakers | Imaginary Electric |  | ER-11.02 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0078 | 4 | guideline | US | IEEE 80 | Guide for Safety in AC Substation Grounding | edition at Base Date | IEEE | electrical | earthing grid | Istanbul EPC |  | ER-11.07 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0039 | 4 | guideline | US | IEEE C37.102 | Guide for AC generator protection | edition at Base Date | IEEE | electrical | generator protection functions | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0033 | 4 | standard | international | ISO 10494 | Gas turbines and gas turbine sets - Measurement of emitted airborne noise | edition at Base Date | ISO | mechanical hse | GT noise data and tests | Imaginary Electric |  | ER-14.03 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0092 | 4 | standard | international | ISO 12944-2 | Paints and varnishes - Corrosion protection of steel structures by protective paint systems - Part 2: Classification of environments | edition at Base Date | ISO | mechanical structural | corrosivity category of outdoor equipment (coastal) | Istanbul EPC, Imaginary Electric |  | ER-02.08 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-OWNR-0001 | 4 | standard | international | ISO 14001 | Environmental management systems - Requirements | 2015 | ISO | hse | environmental management during construction and commissioning (ESMP) | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0097 | 4 | standard | international | ISO 20816-2 | Mechanical vibration - Measurement and evaluation of machine vibration - Part 2: Land-based gas turbines, steam turbines and generators above 40 MW with fluid-film bearings | edition at Base Date | ISO | mechanical | vibration limits of the GT, ST and generators (IEC) | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0031 | 4 | standard | international | ISO 21789 | Gas turbine applications - Safety | edition at Base Date | ISO | mechanical hse | GT package | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0032 | 4 | standard | international | ISO 3977-3 | Gas turbines - Procurement - Part 3: Design requirements | edition at Base Date | ISO | mechanical | GT package | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0095 | 4 | standard | international | ISO 45001 | Occupational health and safety management systems | 2018 | ISO | hse | HSE management system | Istanbul EPC, Imaginary Electric |  | ER-14.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0051 | 4 | standard | international | ISO 6976 | Natural gas - Calculation of calorific values, density, relative density and Wobbe indices | 2016 | ISO | process | fuel LHV in heat balances and performance tests | Istanbul EPC, Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0094 | 4 | standard | international | ISO 9001 | Quality management systems - Requirements | 2015 | ISO | general | quality management of the Contractor and major suppliers | Istanbul EPC, Imaginary Electric |  | ER-15.01 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0068 | 4 | standard | US | NFPA 11 | Standard for Low-, Medium-, and High-Expansion Foam | edition at Base Date | NFPA | hse | LDO tank foam protection | Istanbul EPC |  | ER-03.08 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0048 | 4 | standard | US | NFPA 12 | Standard on Carbon Dioxide Extinguishing Systems | edition at Base Date | NFPA | hse | GT enclosure CO2 system | Imaginary Electric |  | ER-10.05 | CO2 total flooding for the GT enclosure (ER-10.05 allows water mist or CO2); no water mist. | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0070 | 4 | standard | US | NFPA 20 | Standard for the Installation of Stationary Pumps for Fire Protection | edition at Base Date | NFPA | hse | fire pumps | Istanbul EPC |  | ER-10.05 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0067 | 4 | standard | US | NFPA 30 | Flammable and Combustible Liquids Code | edition at Base Date | NFPA | hse mechanical | LDO unloading, storage and bunds | Istanbul EPC |  | ER-03.08 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0071 | 4 | standard | US | NFPA 72 | National Fire Alarm and Signaling Code | edition at Base Date | NFPA | hse i_and_c | fire detection and alarm (IF-33) | Istanbul EPC |  | ER-10.05 |  | agreed | Istanbul EPC, Owner | TQ-033
REF-CONS-0049 | 4 | standard | US | NFPA 85 | Boiler and Combustion Systems Hazards Code | edition at Base Date | NFPA | i_and_c hse | HRSG purge and combustion turbine exhaust systems | Imaginary Electric |  |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0069 | 4 | guideline | US | NFPA 850 | Recommended Practice for Fire Protection for Electric Generating Plants and HVDC Converter Stations | edition at Base Date | NFPA | hse | plant fire protection concept | Istanbul EPC, Imaginary Electric |  | ER-10.05 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-CONS-0054 | 4 | guideline | international | VGB-S-010 | Feed water, boiler water and steam quality for power plants | edition at Base Date | VGB | process | cycle chemistry limits | Istanbul EPC, Imaginary Electric |  | ER-09.03 |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
REF-SETUP-0001 | 5 | library | international | AVEVA class library 1.0.1 | AVEVA engineering class library (classes, attributes, units, value lists) - project tag classification standard | modelUpdatedAtVersion 4.0.0.0 | AVEVA | general | engineering classes and attributes of the project database | Istanbul EPC |  |  |  | agreed | Istanbul EPC, Owner | TQ-033

## Permits
Alpilla 600 MW Combined Cycle Power Plant - Permits, licences and approvals register
engine standards_register v1.0.0 ¦ generated 2026-09-28T03:56:06Z by SETUP ¦ data b66cf958da23f2cb
ID | Permit | Authority | Legal basis | Phase | Applicant | Support by | Scope | Deliverables (who provides) | Lead time d | Apply by | Needed by | Gates | Permit status | Obtained | Tie-ins | Status | Agreed by | Agreed in
PMT-001 | Positive EIA decision | Ministry Env. | Law 2872 EIA Regulation | development | Owner |  | Power plant, intake/outfall and connections as described in the EIA file; binding conditions ALP-OWN-ENV-001 |  |  |  | 2026-11-02 | all works | granted | 2026-03-12 |  | agreed | Istanbul EPC, Owner | TQ-033
PMT-002 | Generation licence | EMRA | Law 6446 | development | Owner |  | 600 MW class CCGT generation licence |  |  |  | 2026-11-02 | Contract effectiveness | granted | 2026-05-28 |  | agreed | Istanbul EPC, Owner | TQ-033
PMT-003 | Grid connection agreement | TSO | Law 6446 Grid Code | development | Owner |  | Connection capacity 640 MW export / 40 MW import at Kiyi 380 kV |  |  |  | 2026-11-02 | grid design | granted | 2026-06-20 | TP-E1 | agreed | Istanbul EPC, Owner | TQ-033
PMT-010 | Workplace registration and construction site notification | SGK | Law 6331 Construction OHS Regulation | construction | Istanbul EPC |  | Construction workplace, hazard class very hazardous | EPC: site safety plan, OHS professionals | 10 | 2026-11-02 | 2026-11-16 | mobilisation | in_preparation |  |  | agreed | Istanbul EPC, Owner | TQ-033
PMT-025 | Archaeological chance-find notifications | Museum Dir. | Law 2863 | construction | Istanbul EPC |  | Stop-work and notification procedure for chance finds | EPC: chance-find procedure in the construction ESMP |  |  | 2026-11-16 | excavations | planned |  |  | agreed | Istanbul EPC, Owner | TQ-033
PMT-011 | Construction noise assessment report | Ministry Env. | Noise Regulation EIA Regulation | construction | Istanbul EPC |  | Noise of piling, steam blowing and night works | EPC: acoustic report, working hours plan | 30 | 2026-12-01 | 2027-01-15 | piling | planned |  |  | agreed | Istanbul EPC, Owner | TQ-033
PMT-022 | Storm water discharge consent | DSI | WPCR | construction | Owner | Istanbul EPC | Storm water to the western stream channel (max 2 m3/s) | EPC: drainage design, oil interceptors |  |  | 2027-01-15 | site drainage | granted | 2026-10-20 | TP-D1 | agreed | Istanbul EPC, Owner | TQ-033
PMT-005 | Building permit (yapi ruhsati) | Municipality | Law 3194 TBDY 2018 Fire Regulation | pre_construction | Owner | Istanbul EPC, Imaginary Electric | Permanent buildings and structures of the plant | EPC: architectural, structural (TBDY 2018), mechanical and electrical projects signed by licensed Turkish engineers, geotechnical report, fire approval; IEC: equipment loads and foundation drawings | 60 | 2026-11-16 | 2027-02-15 | start of permanent foundations (piling) | in_preparation |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-012 | Construction dewatering permit | DSI | Law 167 | construction | Istanbul EPC |  | Temporary groundwater lowering for deep excavations (CW pump house) | EPC: dewatering design and discharge plan | 60 | 2026-11-16 | 2027-02-15 | deep excavations | planned |  | TP-D1 | agreed | Istanbul EPC, Owner | TQ-033
PMT-023 | Construction power connection | DISCO | Law 6446 | construction | Owner | Istanbul EPC | 34.5 kV / 5 MVA construction supply | EPC: load list, RMU design | 60 | 2026-12-15 | 2027-03-15 | construction power | applied |  | TP-E2 | agreed | Istanbul EPC, Owner | TQ-033
PMT-006 | Coastal permit for intake and outfall pipelines | Ministry Env. | Law 3621 EIA Regulation | pre_construction | Owner | Istanbul EPC | Offshore intake head, outfall diffuser and pipelines across the coastal strip | EPC: marine design, route survey, construction method statement | 180 | 2026-11-02 | 2027-10-01 | marine works (window 1 October - 30 April) | applied |  | TP-CW1 TP-CW2 | agreed | Istanbul EPC, Owner | TQ-033
PMT-007 | Coastal permit for the temporary barge landing | Ministry Env. | Law 3621 | pre_construction | Owner | Istanbul EPC | Temporary ro-ro barge landing on the public coastal strip for the construction period | EPC: landing design and removal plan by 2027-03-31 | 180 | 2027-04-01 | 2027-11-01 | first heavy delivery by barge | planned |  | TP-M1 | agreed | Istanbul EPC, Owner | TQ-033
PMT-008 | Harbour master approval for barge operations | MoTI / Harbour Master | Law 3621 | construction | Istanbul EPC | Imaginary Electric | Barge berthing and ro-ro operations | EPC: marine operations plan; IEC: heavy piece list (weights, dimensions) | 30 | 2027-09-15 | 2027-11-01 | first heavy delivery by barge | planned |  | TP-M1 | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-009 | Abnormal load road transport permits | KGM | Law 2918 | construction | Istanbul EPC | Imaginary Electric | Road moves of indivisible loads from the barge landing to site | EPC: route survey; IEC: transport drawings | 30 | 2027-09-01 | 2027-11-01 | heavy haul to site | planned |  | TP-M1 TP-R1 | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-013 | Radiation source licence for radiographic testing | NDK | Law 7381 | construction | Istanbul EPC | Imaginary Electric | Gamma / X-ray sources of the NDT subcontractors on site | NDT subcontractor licence, radiation protection plan | 60 | 2027-09-15 | 2027-12-01 | first site radiography | planned |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-004 | System use agreement and energisation approval | TSO | Law 6446 Grid Code | commissioning | Owner | Istanbul EPC, Imaginary Electric | Back-feed energisation of the plant substation and test energy | EPC: protection settings, SCADA test report, single-line diagram; IEC: generator and GSU data, excitation and governor models | 90 | 2028-03-15 | 2028-07-15 | KD-010 back-feed | planned |  | TP-E1 TP-T3 | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-016 | First inspection of lifting and pressure equipment | MoLSS | Work Equipment Regulation PED 2014/68/EU | commissioning | Istanbul EPC | Imaginary Electric | Cranes, hoists, pressure vessels and the HRSG before first use | EPC and IEC: declarations of conformity, notified body certificates, load tests | 14 | 2028-06-15 | 2028-08-01 | use of equipment in commissioning | planned |  |  | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-014 | Gas connection and receiving station approval | Gas network operator | Law 4646 | commissioning | Owner | Istanbul EPC, Imaginary Electric | Connection of the plant gas station to the spur line, fiscal metering approval, gas-in permission | EPC: station design (EN 12186 / ASME B31.8), metering, pressure protection, test records; IEC: GT gas demand and pressure requirements | 120 | 2028-03-15 | 2028-08-15 | gas-in (TP-G1) | planned |  | TP-G1 IF-01 | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-017 | Emission data link registration (continuous emission monitoring centre) | Ministry Env. | Env. Permit Regulation SKHKKY | commissioning | Owner | Istanbul EPC | CEMS on-line data transmission | EPC: CEMS certificates (EN 15267), QAL1, data link test | 45 | 2028-07-15 | 2028-10-02 | first fire (KD-020) | planned |  | TP-T2 | agreed | Istanbul EPC, Owner | TQ-033
PMT-018 | Temporary activity certificate (environmental) | Ministry Env. | Env. Permit Regulation LCP Regulation WPCR | commissioning | Owner | Istanbul EPC, Imaginary Electric | Operation of the combustion plant and the discharges before the environmental permit | EPC: emission and discharge measurement plan, CEMS; IEC: GT emission data | 30 | 2028-08-15 | 2028-10-02 | first fire (KD-020) | planned |  | IF-26 TP-CW2 | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-015 | Major accident notification and Major Accident Prevention Policy | Ministry Env. | Major Accident Regulation | commissioning | Owner | Istanbul EPC, Imaginary Electric | Lower-tier establishment (LDO > 2,500 t); inventory incl. aqueous ammonia and H2 | EPC: hazardous substance inventory, QRA inputs, MAPP draft; IEC: inventories in the power island (lube oil, H2, ammonia skid) | 60 | 2028-08-15 | 2028-11-01 | LDO first fill (TP-L1) | planned |  | TP-L1 IF-25 IF-31 | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022
PMT-019 | Environmental permit (air emissions and discharges) | Ministry Env. | Env. Permit Regulation LCP Regulation WPCR | operation | Owner | Istanbul EPC | Permanent environmental permit within the validity of the temporary certificate | EPC: QAL2 report, accredited emission and discharge test reports (ER-16.05) | 90 | 2029-03-01 | 2029-07-04 | Taking-Over (KD-040) | planned |  | IF-26 TP-CW2 | agreed | Istanbul EPC, Owner | TQ-033
PMT-020 | Occupancy permit (yapi kullanma izin belgesi) | Municipality | Law 3194 Fire Regulation | operation | Owner | Istanbul EPC | Use of the permanent buildings | EPC: as-built drawings, fire system test certificates | 30 | 2029-05-15 | 2029-07-04 | Taking-Over (KD-040) | planned |  |  | agreed | Istanbul EPC, Owner | TQ-033
PMT-021 | Grid Code compliance approval (provisional and final) | TSO | Grid Code | commissioning | Owner | Istanbul EPC, Imaginary Electric | Compliance tests of the generating units (frequency and voltage control, FRT models) | EPC and IEC: test programme, validated models, test reports (ER-16.03) | 60 | 2029-01-02 | 2029-07-04 | commercial operation | planned |  | TP-E1 | agreed | Imaginary Electric, Istanbul EPC, Owner | TQ-033 TQ-IEC-022

## Authorities
Alpilla 600 MW Combined Cycle Power Plant - Authorities
engine standards_register v1.0.0 ¦ generated 2026-09-28T03:56:06Z by SETUP ¦ data b66cf958da23f2cb
ID | Authority | Short name | Regulations | Permits
DISCO | Regional electricity distribution company (construction power) | DISCO |  | PMT-023 Construction power connection
DSI | General Directorate of State Hydraulic Works (surface and groundwater) | DSI | Law 167 | PMT-012 Construction dewatering permit PMT-022 Storm water discharge consent
EMRA | Energy Market Regulatory Authority (EPDK) | EMRA | Law 6446 | PMT-002 Generation licence
GASNO | Natural gas transmission network operator (connection and station approval) | Gas network operator | Law 4646 | PMT-014 Gas connection and receiving station approval
KGM | General Directorate of Highways (abnormal load permits) | KGM | Law 2918 | PMT-009 Abnormal load road transport permits
MENR | Ministry of Energy and Natural Resources | MENR | Heavy Current Regulation Earthing Regulation
MOCT | Ministry of Culture and Tourism (regional museum directorate) | Museum Dir. | Law 2863 | PMT-025 Archaeological chance-find notifications
MOEUCC | Ministry of Environment, Urbanisation and Climate Change (and its Provincial Directorate) | Ministry Env. | Law 2872 EIA Regulation Env. Permit Regulation SKHKKY LCP Regulation WPCR Noise Regulation Waste Regulation Soil Regulation Major Accident Regulation Law 3621 | PMT-001 Positive EIA decision PMT-006 Coastal permit for intake and outfall pipelines PMT-007 Coastal permit for the temporary barge landing PMT-011 Construction noise assessment report PMT-015 Major accident notification and Major Accident Prevention Policy PMT-017 Emission data link registration (continuous emission monitoring centre) PMT-018 Temporary activity certificate (environmental) PMT-019 Environmental permit (air emissions and discharges)
MOIT | Ministry of Industry and Technology (market surveillance of products) | MoIT | PED 2014/68/EU Machinery Directive 2006/42/EC ATEX 2014/34/EU
MOLSS | Ministry of Labour and Social Security (OHS inspection) | MoLSS | Law 6331 Construction OHS Regulation Work Equipment Regulation Explosive Atmospheres Regulation | PMT-016 First inspection of lifting and pressure equipment
MOTI | Ministry of Transport and Infrastructure (Harbour Master, coastal structures) | MoTI / Harbour Master |  | PMT-008 Harbour master approval for barge operations
MUNI | District municipality / provincial special administration (building, occupancy, fire approval, water) | Municipality | Law 3194 Fire Regulation TBDY 2018 | PMT-005 Building permit (yapi ruhsati) PMT-020 Occupancy permit (yapi kullanma izin belgesi)
NDK | Nuclear Regulatory Authority (radiation sources for NDT) | NDK | Law 7381 | PMT-013 Radiation source licence for radiographic testing
SGK | Social Security Institution (workplace registration) | SGK |  | PMT-010 Workplace registration and construction site notification
TSO | National Transmission System Operator | TSO | Grid Code | PMT-003 Grid connection agreement PMT-004 System use agreement and energisation approval PMT-021 Grid Code compliance approval (provisional and final)

## Checks
Alpilla 600 MW Combined Cycle Power Plant - Register checks
engine standards_register v1.0.0 ¦ generated 2026-09-28T03:56:06Z by SETUP ¦ data b66cf958da23f2cb
Item | Check | Result | Detail
ER-01.07 | ER coverage | OK | cites Grid Code: in the register
ER-02.06 | ER coverage | OK | cites TBDY 2018: in the register
ER-02.08 | ER coverage | OK | cites ISO 12944-2: in the register
ER-02.10 | ER coverage | OK | cites IEC 60815: in the register
ER-02.12 | ER coverage | OK | cites IEC 62305: in the register
ER-03.07 | ER coverage | OK | cites TS EN 590: in the register
ER-03.08 | ER coverage | OK | cites NFPA 11: in the register
ER-03.08 | ER coverage | OK | cites NFPA 30: in the register
ER-04.07 | ER coverage | OK | cites Grid Code: in the register
ER-05.02 | ER coverage | OK | cites EN 1822: in the register
ER-05.06 | ER coverage | OK | cites IEC 62443: in the register
ER-06.02 | ER coverage | OK | cites ASME I: in the register
ER-06.02 | ER coverage | OK | cites EN 12952: in the register
ER-06.02 | ER coverage | OK | cites PED 2014/68/EU: in the register
ER-06.05 | ER coverage | OK | cites EN 12952-3: in the register
ER-06.06 | ER coverage | OK | cites EN 15259: in the register
ER-07.07 | ER coverage | OK | cites HEI: in the register
ER-07.08 | ER coverage | OK | cites ASME PTC 12.2: in the register
ER-07.08 | ER coverage | OK | cites HEI: in the register
ER-07.09 | ER coverage | OK | cites HEI: in the register
ER-07.10 | ER coverage | OK | cites HEI: in the register
ER-09.03 | ER coverage | OK | cites VGB-S-010: in the register
ER-10.05 | ER coverage | OK | cites NFPA 850: in the register
ER-11.02 | ER coverage | OK | cites IEC 60034: in the register
ER-11.02 | ER coverage | OK | cites IEC/IEEE 62271-37-013: in the register
ER-11.03 | ER coverage | OK | cites IEC 60076: in the register
ER-11.07 | ER coverage | OK | cites IEC 62305: in the register
ER-11.07 | ER coverage | OK | cites IEEE 80: in the register
ER-12.03 | ER coverage | OK | cites IEC 61511: in the register
ER-12.04 | ER coverage | OK | cites EN 14181: in the register
ER-12.05 | ER coverage | OK | cites ASME PTC 46: in the register
ER-12.07 | ER coverage | OK | cites IEC 62443: in the register
ER-13.03 | ER coverage | OK | cites EN 1993: in the register
ER-13.03 | ER coverage | OK | cites EN ISO 1461: in the register
ER-13.04 | ER coverage | OK | cites EN 1992: in the register
ER-13.04 | ER coverage | OK | cites TS 500: in the register
ER-14.01 | ER coverage | OK | cites Law 2872: in the register
ER-14.05 | ER coverage | OK | cites ISO 45001: in the register
ER-14.05 | ER coverage | OK | cites Law 6331: in the register
ER-14.06 | ER coverage | OK | cites IEC 60079-10-1: in the register
ER-15.01 | ER coverage | OK | cites ISO 9001: in the register
ER-15.04 | ER coverage | OK | cites EN 10204: in the register
ER-15.05 | ER coverage | OK | cites ASME IX: in the register
ER-15.05 | ER coverage | OK | cites EN ISO 15614: in the register
ER-16.04 | ER coverage | OK | cites ASME PTC 46: in the register
ER-18.02 | ER coverage | OK | cites Grid Code: in the register
REF-CONS-0025 | agreement | OK | ATEX 2014/34/EU: agreed by IEC, IEPC, OWNER
REF-CONS-0012 | agreement | OK | Construction OHS Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0002 | agreement | OK | EIA Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0022 | agreement | OK | Earthing Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0003 | agreement | OK | Env. Permit Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0014 | agreement | OK | Explosive Atmospheres Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0016 | agreement | OK | Fire Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0021 | agreement | OK | Heavy Current Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0005 | agreement | OK | LCP Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0028 | agreement | OK | Law 167: agreed by IEPC, OWNER
REF-CONS-0026 | agreement | OK | Law 2863: agreed by IEPC, OWNER
REF-CONS-0001 | agreement | OK | Law 2872: agreed by IEC, IEPC, OWNER
REF-CONS-0029 | agreement | OK | Law 2918: agreed by IEPC, OWNER
REF-CONS-0015 | agreement | OK | Law 3194: agreed by IEC, IEPC, OWNER
REF-CONS-0018 | agreement | OK | Law 3621: agreed by IEPC, OWNER
REF-CONS-0027 | agreement | OK | Law 4646: agreed by IEPC, OWNER
REF-CONS-0011 | agreement | OK | Law 6331: agreed by IEC, IEPC, OWNER
REF-CONS-0019 | agreement | OK | Law 6446: agreed by IEPC, OWNER
REF-CONS-0030 | agreement | OK | Law 7381: agreed by IEC, IEPC, OWNER
REF-CONS-0024 | agreement | OK | Machinery Directive 2006/42/EC: agreed by IEC, IEPC, OWNER
REF-CONS-0010 | agreement | OK | Major Accident Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0007 | agreement | OK | Noise Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0023 | agreement | OK | PED 2014/68/EU: agreed by IEC, IEPC, OWNER
REF-CONS-0004 | agreement | OK | SKHKKY: agreed by IEC, IEPC, OWNER
REF-CONS-0009 | agreement | OK | Soil Regulation: agreed by IEPC, OWNER
REF-CONS-0017 | agreement | OK | TBDY 2018: agreed by IEC, IEPC, OWNER
REF-CONS-0006 | agreement | OK | WPCR: agreed by IEPC, OWNER
REF-CONS-0008 | agreement | OK | Waste Regulation: agreed by IEPC, OWNER
REF-CONS-0013 | agreement | OK | Work Equipment Regulation: agreed by IEC, IEPC, OWNER
REF-CONS-0020 | agreement | OK | Grid Code: agreed by IEC, IEPC, OWNER
REF-CONS-0093 | agreement | OK | ACI 351.3R: agreed by IEPC, OWNER
REF-CONS-0066 | agreement | OK | API 650: agreed by IEPC, OWNER
REF-CONS-0060 | agreement | OK | ASME B16.25: agreed by IEC, IEPC, OWNER
REF-CONS-0061 | agreement | OK | ASME B16.34: agreed by IEC, IEPC, OWNER
REF-CONS-0059 | agreement | OK | ASME B16.5: agreed by IEC, IEPC, OWNER
REF-CONS-0055 | agreement | OK | ASME B31.1: agreed by IEPC, OWNER
REF-CONS-0056 | agreement | OK | ASME B31.3: agreed by IEPC, OWNER
REF-CONS-0057 | agreement | OK | ASME B31.8: agreed by IEPC, OWNER
REF-SETUP-0002 | agreement | OK | ASME B36.10M: agreed by IEC, IEPC, OWNER
REF-CONS-0046 | agreement | OK | ASME PTC 12.2: agreed by IEC, IEPC, OWNER
REF-CONS-0034 | agreement | OK | ASME PTC 22: agreed by IEC, IEPC, OWNER
REF-CONS-0044 | agreement | OK | ASME PTC 4.4: agreed by IEC, IEPC, OWNER
REF-CONS-0050 | agreement | OK | ASME PTC 46: agreed by IEC, IEPC, OWNER
REF-CONS-0036 | agreement | OK | ASME PTC 6: agreed by IEC, IEPC, OWNER
REF-CONS-0042 | agreement | OK | ASME Section I: agreed by IEC, IEPC, OWNER
REF-CONS-0063 | agreement | OK | ASME Section IX: agreed by IEC, IEPC, OWNER
REF-CONS-0062 | agreement | OK | ASME Section VIII Div. 1: agreed by IEPC, OWNER
REF-CONS-0065 | agreement | OK | EN 10204: agreed by IEC, IEPC, OWNER
REF-CONS-0058 | agreement | OK | EN 12186: agreed by IEPC, OWNER
REF-CONS-0043 | agreement | OK | EN 12952: agreed by IEC, IEPC, OWNER
REF-CONS-0072 | agreement | OK | EN 13001: agreed by IEPC, OWNER
REF-CONS-0084 | agreement | OK | EN 14181: agreed by IEPC, OWNER
REF-CONS-0086 | agreement | OK | EN 15259: agreed by IEPC, OWNER
REF-CONS-0085 | agreement | OK | EN 15267-3: agreed by IEPC, OWNER
REF-CONS-0047 | agreement | OK | EN 1822: agreed by IEC, IEPC, OWNER
REF-CONS-0087 | agreement | OK | EN 1990: agreed by IEPC, OWNER
REF-CONS-0088 | agreement | OK | EN 1992: agreed by IEPC, OWNER
REF-CONS-0090 | agreement | OK | EN 1993: agreed by IEPC, OWNER
REF-CONS-0091 | agreement | OK | EN ISO 1461: agreed by IEPC, OWNER
REF-CONS-0064 | agreement | OK | EN ISO 15614: agreed by IEC, IEPC, OWNER
REF-CONS-0045 | agreement | OK | HEI 2629: agreed by IEC, IEPC, OWNER
REF-CONS-0053 | agreement | OK | IAPWS TGD: agreed by IEC, IEPC, OWNER
REF-CONS-0052 | agreement | OK | IAPWS-IF97: agreed by IEC, IEPC, OWNER
REF-CONS-0037 | agreement | OK | IEC 60034-1: agreed by IEC, IEPC, OWNER
REF-CONS-0035 | agreement | OK | IEC 60045-1: agreed by IEC, IEPC, OWNER
REF-CONS-0040 | agreement | OK | IEC 60076: agreed by IEC, IEPC, OWNER
REF-CONS-0083 | agreement | OK | IEC 60079-10-1: agreed by IEC, IEPC, OWNER
REF-CONS-0077 | agreement | OK | IEC 60364: agreed by IEPC, OWNER
REF-CONS-0080 | agreement | OK | IEC 60815: agreed by IEC, IEPC, OWNER
REF-CONS-0075 | agreement | OK | IEC 60909: agreed by IEC, IEPC, OWNER
REF-CONS-0081 | agreement | OK | IEC 61511: agreed by IEC, IEPC, OWNER
REF-CONS-0076 | agreement | OK | IEC 61850: agreed by IEC, IEPC, OWNER
REF-CONS-0073 | agreement | OK | IEC 61936-1: agreed by IEPC, OWNER
REF-CONS-0074 | agreement | OK | IEC 62271-203: agreed by IEPC, OWNER
REF-CONS-0079 | agreement | OK | IEC 62305: agreed by IEPC, OWNER
REF-CONS-0082 | agreement | OK | IEC 62443: agreed by IEC, IEPC, OWNER
REF-CONS-0041 | agreement | OK | IEC 62770: agreed by IEC, IEPC, OWNER
REF-CONS-0038 | agreement | OK | IEC/IEEE 62271-37-013: agreed by IEC, IEPC, OWNER
REF-CONS-0078 | agreement | OK | IEEE 80: agreed by IEPC, OWNER
REF-CONS-0039 | agreement | OK | IEEE C37.102: agreed by IEC, IEPC, OWNER
REF-CONS-0033 | agreement | OK | ISO 10494: agreed by IEC, IEPC, OWNER
REF-CONS-0092 | agreement | OK | ISO 12944-2: agreed by IEC, IEPC, OWNER
REF-OWNR-0001 | agreement | OK | ISO 14001: agreed by IEC, IEPC, OWNER
REF-CONS-0097 | agreement | OK | ISO 20816-2: agreed by IEC, IEPC, OWNER
REF-CONS-0031 | agreement | OK | ISO 21789: agreed by IEC, IEPC, OWNER
REF-CONS-0032 | agreement | OK | ISO 3977-3: agreed by IEC, IEPC, OWNER
REF-CONS-0095 | agreement | OK | ISO 45001: agreed by IEC, IEPC, OWNER
REF-CONS-0051 | agreement | OK | ISO 6976: agreed by IEC, IEPC, OWNER
REF-CONS-0094 | agreement | OK | ISO 9001: agreed by IEC, IEPC, OWNER
REF-CONS-0068 | agreement | OK | NFPA 11: agreed by IEPC, OWNER
REF-CONS-0048 | agreement | OK | NFPA 12: agreed by IEC, IEPC, OWNER
REF-CONS-0070 | agreement | OK | NFPA 20: agreed by IEPC, OWNER
REF-CONS-0067 | agreement | OK | NFPA 30: agreed by IEPC, OWNER
REF-CONS-0071 | agreement | OK | NFPA 72: agreed by IEPC, OWNER
REF-CONS-0049 | agreement | OK | NFPA 85: agreed by IEC, IEPC, OWNER
REF-CONS-0069 | agreement | OK | NFPA 850: agreed by IEC, IEPC, OWNER
REF-CONS-0089 | agreement | OK | TS 500: agreed by IEPC, OWNER
REF-CONS-0096 | agreement | OK | TS EN 590: agreed by IEPC, OWNER
REF-CONS-0054 | agreement | OK | VGB-S-010: agreed by IEC, IEPC, OWNER
REF-SETUP-0001 | agreement | OK | AVEVA class library 1.0.1: agreed by IEPC, OWNER
PMT-001 | legal basis | OK | Law 2872, EIA Regulation
PMT-001 | agreement | OK | agreed by IEPC, OWNER
PMT-002 | legal basis | OK | Law 6446
PMT-002 | agreement | OK | agreed by IEPC, OWNER
PMT-003 | legal basis | OK | Law 6446, Grid Code
PMT-003 | agreement | OK | agreed by IEPC, OWNER
PMT-004 | legal basis | OK | Law 6446, Grid Code
PMT-004 | timing | OK | apply 2028-03-15 + 90 d = 2028-06-13; needed 2028-07-15: float 32 d
PMT-004 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-005 | legal basis | OK | Law 3194, TBDY 2018, Fire Regulation
PMT-005 | timing | OK | apply 2026-11-16 + 60 d = 2027-01-15; needed 2027-02-15: float 31 d
PMT-005 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-006 | legal basis | OK | Law 3621, EIA Regulation
PMT-006 | timing | OK | apply 2026-11-02 + 180 d = 2027-05-01; needed 2027-10-01: float 153 d
PMT-006 | agreement | OK | agreed by IEPC, OWNER
PMT-007 | legal basis | OK | Law 3621
PMT-007 | timing | OK | apply 2027-04-01 + 180 d = 2027-09-28; needed 2027-11-01: float 34 d
PMT-007 | agreement | OK | agreed by IEPC, OWNER
PMT-008 | legal basis | OK | Law 3621
PMT-008 | timing | OK | apply 2027-09-15 + 30 d = 2027-10-15; needed 2027-11-01: float 17 d
PMT-008 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-009 | legal basis | OK | Law 2918
PMT-009 | timing | OK | apply 2027-09-01 + 30 d = 2027-10-01; needed 2027-11-01: float 31 d
PMT-009 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-010 | legal basis | OK | Law 6331, Construction OHS Regulation
PMT-010 | timing | INFO | apply 2026-11-02 + 10 d = 2026-11-12; needed 2026-11-16: float 4 d
PMT-010 | agreement | OK | agreed by IEPC, OWNER
PMT-011 | legal basis | OK | Noise Regulation, EIA Regulation
PMT-011 | timing | OK | apply 2026-12-01 + 30 d = 2026-12-31; needed 2027-01-15: float 15 d
PMT-011 | agreement | OK | agreed by IEPC, OWNER
PMT-012 | legal basis | OK | Law 167
PMT-012 | timing | OK | apply 2026-11-16 + 60 d = 2027-01-15; needed 2027-02-15: float 31 d
PMT-012 | agreement | OK | agreed by IEPC, OWNER
PMT-013 | legal basis | OK | Law 7381
PMT-013 | timing | OK | apply 2027-09-15 + 60 d = 2027-11-14; needed 2027-12-01: float 17 d
PMT-013 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-014 | legal basis | OK | Law 4646
PMT-014 | timing | OK | apply 2028-03-15 + 120 d = 2028-07-13; needed 2028-08-15: float 33 d
PMT-014 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-015 | legal basis | OK | Major Accident Regulation
PMT-015 | timing | OK | apply 2028-08-15 + 60 d = 2028-10-14; needed 2028-11-01: float 18 d
PMT-015 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-016 | legal basis | OK | Work Equipment Regulation, PED 2014/68/EU
PMT-016 | timing | OK | apply 2028-06-15 + 14 d = 2028-06-29; needed 2028-08-01: float 33 d
PMT-016 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-017 | legal basis | OK | Env. Permit Regulation, SKHKKY
PMT-017 | timing | OK | apply 2028-07-15 + 45 d = 2028-08-29; needed 2028-10-02: float 34 d
PMT-017 | agreement | OK | agreed by IEPC, OWNER
PMT-018 | legal basis | OK | Env. Permit Regulation, LCP Regulation, WPCR
PMT-018 | timing | OK | apply 2028-08-15 + 30 d = 2028-09-14; needed 2028-10-02: float 18 d
PMT-018 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-019 | legal basis | OK | Env. Permit Regulation, LCP Regulation, WPCR
PMT-019 | timing | OK | apply 2029-03-01 + 90 d = 2029-05-30; needed 2029-07-04: float 35 d
PMT-019 | agreement | OK | agreed by IEPC, OWNER
PMT-020 | legal basis | OK | Law 3194, Fire Regulation
PMT-020 | timing | OK | apply 2029-05-15 + 30 d = 2029-06-14; needed 2029-07-04: float 20 d
PMT-020 | agreement | OK | agreed by IEPC, OWNER
PMT-021 | legal basis | OK | Grid Code
PMT-021 | timing | OK | apply 2029-01-02 + 60 d = 2029-03-03; needed 2029-07-04: float 123 d
PMT-021 | agreement | OK | agreed by IEC, IEPC, OWNER
PMT-022 | legal basis | OK | WPCR
PMT-022 | agreement | OK | agreed by IEPC, OWNER
PMT-023 | legal basis | OK | Law 6446
PMT-023 | timing | OK | apply 2026-12-15 + 60 d = 2027-02-13; needed 2027-03-15: float 30 d
PMT-023 | agreement | OK | agreed by IEPC, OWNER
PMT-025 | legal basis | OK | Law 2863
PMT-025 | timing | INFO | no lead time: procedural, needed from 2026-11-16
PMT-025 | agreement | OK | agreed by IEPC, OWNER