## Cases
Alpilla 600 MW Combined Cycle Power Plant - heat and mass balance case summary
engine hmb v1.1.1 ¦ data b6f4b950c7f3b7e0 ¦ 2026-09-29T03:02:22Z
Item | Unit | MAX-NG-100 | MIN-NG-100 | SRC-LDO-100 | SRC-NG-060 | SRC-NG-100 | SRC-NG-GT80 | SRC-NG-MEL | SUM-NG-100 | WIN-NG-100
Title |  | Maximum ambient (40 degC) with maximum seawater (27 degC), natural gas, base load | Minimum ambient for full capability (-8 degC), natural gas, base load | Site Reference Conditions, LDO with water injection, base load (guarantee PG-15/16) | Site Reference Conditions, natural gas, 60 % plant net load (guarantee PG-03) | Site Reference Conditions, natural gas, base load (guarantee case) | Site Reference Conditions, natural gas, GT at 80 % load | Site Reference Conditions, natural gas, GT at minimum emissions-compliant load (30 %, low-load extension) | Summer design (32.8 degC, 0.4 %), natural gas, base load | Winter design (-4.8 degC, 99.6 %), natural gas, base load (GT at output limit)
Fuel |  | natural_gas | natural_gas | ldo | natural_gas | natural_gas | natural_gas | natural_gas | natural_gas | natural_gas
Ambient temperature | degC | 40 | -8 | 15 | 15 | 15 | 15 | 15 | 32.8 | -4.8
Relative humidity | % | 35 | 80 | 70 | 70 | 70 | 70 | 70 | 45 | 80
Seawater temperature | degC | 27 | 6.9 | 16 | 16 | 16 | 16 | 16 | 24 | 8
GT load | % | 100 | 100 | 100 | 55.78 | 100 | 80 | 30 | 100 | 100
GT output | MW | 348.23 | 470 | 400.5 | 237.07 | 425 | 340 | 127.5 | 372.79 | 470
ST output | MW | 175.84 | 204.92 | 178.37 | 140.73 | 200.73 | 175.05 | 94.37 | 184.53 | 207.94
Gross output | MW | 524.07 | 674.92 | 578.87 | 377.8 | 625.73 | 515.05 | 221.87 | 557.33 | 677.95
Auxiliary loads + transformer losses | MW | 10.78 | 12.12 | 11.07 | 9.26 | 11.79 | 10.54 | 8.1 | 11.12 | 12.24
Net output | MW | 513.29 | 662.8 | 567.8 | 368.54 | 613.94 | 504.51 | 213.77 | 546.21 | 665.7
Plant load (net, % of reference) | % | 83.61 | 107.96 | 92.48 | 60.03 |  | 82.18 | 34.82 | 88.97 | 108.43
Heat input (LHV) | MW | 832.17 | 1058.31 | 961.22 | 635.13 | 983.02 | 827.33 | 412.86 | 881.16 | 1063.78
Net heat rate (LHV) | kJ/kWh | 5836.42 | 5748.24 | 6094.42 | 6204.01 | 5764.23 | 5903.5 | 6952.83 | 5807.66 | 5752.77
Net efficiency | % | 61.68 | 62.63 | 59.07 | 58.03 | 62.45 | 60.98 | 51.78 | 61.99 | 62.58
Fuel flow | kg/s | 17.53 | 22.29 | 22.41 | 13.38 | 20.7 | 17.42 | 8.7 | 18.56 | 22.4
Fuel gas flow | Sm3/h | 86136.46 | 109544.14 |  | 65740.93 | 101751.57 | 85636.15 | 42734.28 | 91207.82 | 110110.79
Water injection | kg/s | 0 | 0 | 13.44 | 0 | 0 | 0 | 0 | 0 | 0
Condenser pressure | mbar(a) | 61.13 | 20.13 | 33.4 | 29.25 | 34.44 | 32.04 | 25.95 | 52.71 | 21.74
CW temperature rise | K | 6.4 | 7.2 | 6.65 | 5.16 | 7 | 6.18 | 3.83 | 6.61 | 7.28
Checks WARN |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Warnings
Case | Check