## Streams
ALP-HMB-SRC-NG-100 - streams
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 776.006 | 1.012 | 15 |  | -10.09 | -7.831 | preliminary | source:SRC-IECE-0005
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | fuel_gas | FGS | FGH | 20.672 | 38 | 25 |  | 0 | 0 | preliminary | source:SRC-IECE-0005
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 20.672 | 35.5 | 215 |  | 457.77 | 9.463 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 796.678 | 1.048 | 640 |  | 689.9 | 549.629 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 796.678 | 1.014 | 80.16 |  | 58.38 | 46.514 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 100.155 | 187 | 600 |  | 3550.83 | 355.634 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 100.155 | 181.5 | 598.5 |  | 3551.63 | 355.714 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 100.155 | 40.2 | 366.21 |  | 3132.89 | 313.775 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 100.155 | 39.5 | 365.21 |  | 3131.93 | 313.679 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 17.338 | 40.3 | 330 |  | 3041.69 | 52.737 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 117.493 | 37.6 | 600 |  | 3676.76 | 431.994 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 117.493 | 36.2 | 598.5 |  | 3674.45 | 431.722 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 11.901 | 5.4 | 250 |  | 2959.75 | 35.224 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 11.901 | 5.05 | 249 |  | 2958.88 | 35.214 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 117.493 | 4.95 | 309.2 |  | 3083.72 | 362.316 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 129.394 | 0.03444 | 26.4 | 0.92061 | 2355.5 | 304.788 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 129.394 | 0.03444 | 26.35 |  | 110.48 | 14.296 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 129.394 | 16 | 26.52 |  | 112.67 | 14.578 | preliminary | source:SRC-IECE-0005
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 12.481 | 43 | 75 |  | 317.41 | 3.962 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 141.874 | 15.5 | 30.85 |  | 130.7 | 18.544 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 129.973 | 5.9 | 158.13 |  | 667.45 | 86.751 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 100.155 | 209 | 161.83 |  | 695.52 | 69.66 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 29.819 | 46 | 158.89 |  | 673.11 | 20.071 | preliminary | source:SRC-IECE-0005
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 12.481 | 43.3 | 247.98 |  | 1075.88 | 13.428 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 16 |  | 65.11 | 663.918 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 23 |  | 93.6 | 954.382 | preliminary | source:SRC-IECE-0005

## Node balances
ALP-HMB-SRC-NG-100 - node balances
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 776.006 | 0 | -7.831 | 0 | 7.831 | 0
BFP | FALSE | 129.973 | 129.974 | 86.751 | 89.732 | 0 | -2.981 | 0
CEP | FALSE | 129.394 | 129.394 | 14.296 | 14.578 | 0 | -0.282 | 0
CMIX | FALSE | 141.875 | 141.874 | 18.54 | 18.544 | 0 | -0.004 | 0
COND | FALSE | 10326.198 | 10326.198 | 968.706 | 968.678 | 0 | 0.027 | 0
FGH | FALSE | 33.153 | 33.153 | 13.428 | 13.425 | 0 | 0.003 | 0
FGS | TRUE | 0 | 20.672 | 0 | 0 | 0 | 0 | 0
GT | FALSE | 796.678 | 796.678 | 983.138 | 549.629 | 433.527 | -0.018 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 1168.681 | 1168.681 | 971.583 | 969.544 | 0 | 2.039 | 2.012 | HRSG: gas-side duty 503.12 MW; residual = casing loss
OUT | TRUE | 10196.804 | 0 | 954.382 | 0 | 0 | 954.382 | 0
PIPE | FALSE | 329.704 | 329.704 | 1136.626 | 1136.328 | 0 | 0.298 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 663.918 | 0 | -663.918 | 0
ST | FALSE | 229.549 | 229.549 | 822.649 | 618.563 | 204.086 | 0 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 796.678 | 0 | 46.514 | 0 | 0 | 46.514 | 0

## Auxiliary loads
ALP-HMB-SRC-NG-100 - auxiliary loads
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-01 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-02 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-03 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-04 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-05 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-06 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-07 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-08 | GT GSU losses at this case load | IEC | fixed | 1107 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-09 | ST GSU losses at this case load | IEC | fixed | 584 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-10 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 3089 | auxiliary | enthalpy rise 2,981 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-11 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 297.2 | auxiliary | enthalpy rise 282 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-12 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-13 | Closed cooling water pumps | IEPC | fixed | 320 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-14 | Electro-chlorination | IEPC | fixed | 260 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-15 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 450 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-16 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-17 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-18 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-19 | Fuel gas receiving station | IEPC | fixed | 60 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-20 | LDO system (standby on gas) | IEPC | fixed | 30 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-21 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-22 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-SRC-NG-100 - summary
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
Item | Value | Unit
GT output | 425 | MW
ST output | 200.73 | MW
Gross output | 625.73 | MW
Auxiliary loads | 10.2997 | MW
Transformer losses | 1.931 | MW
Net output | 613.4993 | MW
Heat input (LHV) | 981.5055 | MW
Gross heat rate | 5646.8761 | kJ/kWh
Net heat rate | 5759.4524 | kJ/kWh
Net efficiency | 62.5059 | %
Auxiliary + transformer losses | 1.9546 | % of gross
Fuel LHV (ISO 6976) | 47.4799 | MJ/kg
Fuel LHV volumetric | 34.7797 | MJ/Sm3
Fuel flow | 20.672 | kg/s
Fuel flow | 101594.3026 | Sm3/h
HRSG gas-side duty | 503.1151 | MW
CW flow | 36111.9254 | m3/h
CW temperature rise | 7 | K
Condenser pressure | 34.44 | mbar(a)
Flue gas Ar (wet) | 0.883 | mol %
Flue gas CO2 (wet) | 4.472 | mol %
Flue gas H2O (wet) | 9.674 | mol %
Flue gas N2 (wet) | 73.854 | mol %
Flue gas O2 (wet) | 11.117 | mol %

## Checks
ALP-HMB-SRC-NG-100 - checks
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
Status | Check
OK | energy balance CMIX: residual -0.004 MW (tolerance 0.25 MW)
OK | energy balance COND: residual +0.027 MW (tolerance 0.97 MW)
OK | energy balance FGH: residual +0.003 MW (tolerance 0.25 MW)
OK | energy balance GT: residual -0.018 MW (tolerance 0.98 MW)
OK | energy balance HRSG: residual +2.039 MW vs stated casing loss 2.012 MW (tolerance 0.97 MW)
OK | energy balance PIPE: residual +0.298 MW (tolerance 1.14 MW)
OK | energy balance ST: residual +0.000 MW (tolerance 0.82 MW)
WARN | fuel LHV from the composition (ISO 6976) 47.48 MJ/kg vs DP-CASE-0018 48.4 MJ/kg (-1.90 %)
OK | auxiliary + transformer losses 1.95 % of gross vs DP-CASE-0031 <= 2.2 %
OK | condenser pressure 34.44 mbar(a) vs DP-OWNR-0021 <= 36.0 mbar(a)
OK | gas flow 101,594 Sm3/h = 88.3 % of DP-OWNR-0033 (115,000 Sm3/h)
OK | net export 613.5 MW vs DP-OWNR-0051 connection capacity 640 MW (this case)
OK | gross output 625.73 MW vs IG-01 >= 615.00 (margin +1.74 %)
OK | gross heat rate 5,646.88 kJ/kWh vs IG-02 <= 5,735.00 (margin +1.54 %)
OK | GT output 425.00 MW vs IG-03 >= 418.00 (margin +1.67 %)
OK | condenser pressure 34.44 mbar(a) vs IG-04 <= 35.50 (margin +2.99 %)
OK | net output 613.50 MW vs PG-01 >= 600.00 (margin +2.25 %)
OK | net heat rate 5,759.45 kJ/kWh vs PG-02 <= 5,860.00 (margin +1.72 %)
OK | CW temperature rise 7.00 K vs PG-13 <= 7.00 (margin +0.00 %)
OK | guarantee cover: at IG-01/IG-02 limits and this HMB's auxiliaries the net plant is 602.8 MW / 5,851 kJ/kWh vs Owner PG-01 600 MW / PG-02 5,860 kJ/kWh