## Streams
ALP-HMB-SRC-NG-MEL - streams
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 433.268 | 1.012 | 15 |  | -10.09 | -4.372 | preliminary | source:SRC-IECE-0005
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | fuel_gas | FGS | FGH | 8.682 | 38 | 25 |  | 0 | 0 | preliminary | source:SRC-IECE-0005
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 8.682 | 35.5 | 215 |  | 457.77 | 3.974 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 441.951 | 1.023 | 598 |  | 631.57 | 279.124 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 441.951 | 1.014 | 68.15 |  | 45.15 | 19.955 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 50.31 | 93.719 | 595.75 |  | 3620.69 | 182.157 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 50.31 | 90.949 | 594.25 |  | 3619.37 | 182.091 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 50.31 | 20.646 | 387.59 |  | 3219.78 | 161.987 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 50.31 | 20.302 | 386.59 |  | 3218.17 | 161.906 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 10.61 | 20.885 | 291.34 |  | 3001.34 | 31.844 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 60.92 | 19.307 | 581.92 |  | 3650.71 | 222.401 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 60.92 | 18.574 | 580.42 |  | 3647.97 | 222.234 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 6.357 | 2.796 | 218.65 |  | 2904.99 | 18.467 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 6.357 | 2.602 | 217.65 |  | 2903.77 | 18.459 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 60.92 | 2.574 | 318.81 |  | 3108.96 | 189.398 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 67.277 | 0.02595 | 21.68 | 0.96316 | 2450.3 | 164.849 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 67.277 | 0.02595 | 21.63 |  | 90.74 | 6.105 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 67.277 | 16 | 21.79 |  | 92.9 | 6.25 | preliminary | source:SRC-IECE-0005
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 6.618 | 20.371 | 75 |  | 315.59 | 2.089 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 73.895 | 15.5 | 26.58 |  | 112.87 | 8.341 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 67.538 | 3.072 | 134.28 |  | 564.68 | 38.138 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 50.31 | 101.279 | 135.88 |  | 578.05 | 29.082 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 17.228 | 23.371 | 134.64 |  | 567.57 | 9.778 | preliminary | source:SRC-IECE-0005
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 6.618 | 23.469 | 214.06 |  | 916.38 | 6.065 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 16 |  | 65.11 | 663.918 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 19.83 |  | 80.7 | 822.843 | preliminary | source:SRC-IECE-0005

## Node balances
ALP-HMB-SRC-NG-MEL - node balances
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 433.268 | 0 | -4.372 | 0 | 4.372 | 0
BFP | FALSE | 67.538 | 67.538 | 38.138 | 38.86 | 0 | -0.722 | 0
CEP | FALSE | 67.277 | 67.277 | 6.105 | 6.25 | 0 | -0.146 | 0
CMIX | FALSE | 73.895 | 73.895 | 8.339 | 8.341 | 0 | -0.002 | 0
COND | FALSE | 10264.081 | 10264.081 | 828.767 | 828.948 | 0 | -0.181 | 0
FGH | FALSE | 15.3 | 15.3 | 6.065 | 6.063 | 0 | 0.002 | 0
FGS | TRUE | 0 | 8.682 | 0 | 0 | 0 | 0 | 0
GT | FALSE | 441.95 | 441.951 | 411.823 | 279.124 | 132.718 | -0.019 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 633.694 | 633.694 | 488.231 | 487.182 | 0 | 1.048 | 1.037 | HRSG: gas-side duty 259.17 MW; residual = casing loss
OUT | TRUE | 10196.804 | 0 | 822.843 | 0 | 0 | 822.843 | 0
PIPE | FALSE | 167.897 | 167.897 | 585.013 | 584.69 | 0 | 0.322 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 663.918 | 0 | -663.918 | 0
ST | FALSE | 117.587 | 117.587 | 422.784 | 326.836 | 95.948 | 0 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 441.951 | 0 | 19.955 | 0 | 0 | 19.955 | 0

## Auxiliary loads
ALP-HMB-SRC-NG-MEL - auxiliary loads
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-167 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-168 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-169 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-170 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-171 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-172 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-173 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-174 | GT GSU losses at this case load | IEC | fixed | 273 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-175 | ST GSU losses at this case load | IEC | fixed | 215 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-176 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 748.3 | auxiliary | enthalpy rise 722 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-177 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 153.2 | auxiliary | enthalpy rise 146 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-178 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-179 | Closed cooling water pumps | IEPC | fixed | 320 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-180 | Electro-chlorination | IEPC | fixed | 260 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-181 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 450 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-182 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-183 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-184 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-185 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-186 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-187 | Fuel gas receiving station | IEPC | fixed | 60 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-188 | LDO system (standby on gas) | IEPC | fixed | 30 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-SRC-NG-MEL - summary
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
Item | Value | Unit
GT output | 127.5 | MW
ST output | 94.37 | MW
Gross output | 221.87 | MW
Auxiliary loads | 7.815 | MW
Transformer losses | 0.728 | MW
Net output | 213.327 | MW
Heat input (LHV) | 412.2209 | MW
Gross heat rate | 6688.5802 | kJ/kWh
Net heat rate | 6956.4352 | kJ/kWh
Net efficiency | 51.7506 | %
Auxiliary + transformer losses | 3.8505 | % of gross
Fuel LHV (ISO 6976) | 47.4799 | MJ/kg
Fuel LHV volumetric | 34.7797 | MJ/Sm3
Fuel flow | 8.682 | kg/s
Fuel flow | 42668.4276 | Sm3/h
HRSG gas-side duty | 259.1696 | MW
CW flow | 36111.9254 | m3/h
CW temperature rise | 3.83 | K
Condenser pressure | 25.95 | mbar(a)
Flue gas Ar (wet) | 0.892 | mol %
Flue gas CO2 (wet) | 3.409 | mol %
Flue gas H2O (wet) | 7.639 | mol %
Flue gas N2 (wet) | 74.647 | mol %
Flue gas O2 (wet) | 13.412 | mol %

## Checks
ALP-HMB-SRC-NG-MEL - checks
engine hmb v1.1.0 ¦ data a363d729afc29597 ¦ 2026-09-28T03:15:47Z
Status | Check
OK | energy balance CMIX: residual -0.002 MW (tolerance 0.25 MW)
OK | energy balance COND: residual -0.181 MW (tolerance 0.83 MW)
OK | energy balance FGH: residual +0.002 MW (tolerance 0.25 MW)
OK | energy balance GT: residual -0.019 MW (tolerance 0.41 MW)
OK | energy balance HRSG: residual +1.048 MW vs stated casing loss 1.037 MW (tolerance 0.49 MW)
OK | energy balance PIPE: residual +0.322 MW (tolerance 0.59 MW)
OK | energy balance ST: residual +0.000 MW (tolerance 0.42 MW)
OK | plant load (net, % of the reference case) 34.77 % of plant net output vs PG-11 <= 40.00 (margin +13.07 %)