IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Power Island Off-design Heat Balances (Case Book)

| Document number | IEC-ALP-PER-003 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-28 |
| Status | Issued for EPC engineering (reference data) |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-09-28 | signed 2026-09-28 | signed 2026-09-28 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. Purpose and method

Rated off-design heat balances of the IEC power island for the EPC plant heat and mass balance (all operating and guarantee cases agreed in TQ-IEC-017). Expected values, new and clean.

Design point and surfaces: IEC-ALP-PER-001 Rev B (corrected HRSG arrangement, EPC piping values). The model reproduces the Rev B design point exactly.

HRSG: fixed surface per section (UA from the design point, gas-side scaling with flow^0.6), HP superheater and reheater, HP economiser 1 and IP economiser as parallel banks with the design gas split; economisers limited to 2 K below saturation; HRSG casing loss 0.4 % of gas-side duty.

Steam turbine: sliding pressure (Stodola cone law) above 60 bar(a) HP; section efficiencies reduced off design (1 - 0.3 (1 - m/m_design)^2); LP exhaust loss proportional to the square of the exhaust volume flow (minimum 30 %).

Attemperation to 600 degC main and reheat steam with spray water from the BFP discharge / interstage (streams 29 and 30 where in service).

Condenser: fixed surface (HEI cleanliness 0.85), constant CW flow as at SRC; seawater cp 4.07 kJ/kg K.

GT: IE-9H.02 correction curves; output limit 470 MW (generator/shaft) below about -1 degC; part load by IGV (exhaust temperature held at 640 degC down to 60 % load); minimum emissions-compliant load 40 % GT load.

LDO: C12H23 pseudo-formula, LHV 42.9 MJ/kg, 30 degC at IF-02; water injection 1.02 kg water per kg fuel at 60 bar(a), 30 degC (IF-03); performance gas heater out of service.

Case SRC-NG-060: GT load found by IEC so that the plant net output is 60 % of case SRC-NG-100 using the EPC auxiliary-load model (DEC-EPCE-0001); the EPC HMB confirms the achieved load.

# 2. Case summary

| Case | Ambient degC | RH % | Seawater degC | Fuel | GT load % | GT MW | GT HR kJ/kWh | Exhaust kg/s | Exhaust degC | ST MW | Gross MW | Stack degC | Condenser mbar | Spray HP/RH kg/s | Water inj. kg/s |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SRC-NG-100 | 15.0 | 70 | 16.0 | GAS | 100.0 | 425.0 | 8,314 | 796.7 | 640.0 | 200.73 | 625.73 | 80.2 | 34.4 | 0.00 / 0.00 | - |
| SRC-NG-GT80 | 15.0 | 70 | 16.0 | GAS | 80.0 | 340.0 | 8,746 | 696.5 | 640.0 | 175.05 | 515.05 | 76.1 | 32.0 | 1.39 / 0.31 | - |
| SRC-NG-060 | 15.0 | 70 | 16.0 | GAS | 55.8 | 237.1 | 9,629 | 573.3 | 636.6 | 140.73 | 377.80 | 71.0 | 29.2 | 1.59 / 0.40 | - |
| SRC-NG-MEL | 15.0 | 70 | 16.0 | GAS | 40.0 | 170.0 | 10,600 | 496.9 | 615.0 | 113.23 | 283.23 | 69.1 | 27.3 | 0.50 / 0.00 | - |
| SRC-LDO-100 | 15.0 | 70 | 16.0 | LDO | 100.0 | 395.0 | 8,650 | 715.8 | 622.0 | 175.45 | 570.45 | 82.8 | 32.5 | 0.15 / 0.00 | 22.57 |
| WIN-NG-100 | -4.8 | 80 | 8.0 | GAS | 100.0 | 470.0 | 8,131 | 832.5 | 635.7 | 207.94 | 677.95 | 77.0 | 21.7 | 0.00 / 0.00 | - |
| MIN-NG-100 | -8.0 | 80 | 6.9 | GAS | 100.0 | 470.0 | 8,089 | 823.5 | 634.0 | 204.92 | 674.92 | 76.1 | 20.1 | 0.00 / 0.00 | - |
| SUM-NG-100 | 32.8 | 45 | 24.0 | GAS | 100.0 | 372.8 | 8,501 | 729.5 | 649.3 | 184.53 | 557.33 | 81.7 | 52.7 | 1.52 / 0.68 | - |
| MAX-NG-100 | 40.0 | 35 | 27.0 | GAS | 100.0 | 348.2 | 8,595 | 695.9 | 653.0 | 175.84 | 524.07 | 81.9 | 61.1 | 2.06 / 0.95 | - |

GT output at the limit in cases WIN-NG-100 and MIN-NG-100. Gross output before auxiliaries and transformer losses; net values are the EPC's. IEC notes: SRC-NG-MEL (GT 40 %) gives about 45 % plant net load; SRC-LDO-100 about 559 MW net with the EPC auxiliaries - see the consortium clarifications.

# 3.1 Case SRC-NG-100 - Site Reference Conditions, natural gas, base load (guarantee case)

Ambient 15.0 degC, 70.0 % RH, seawater 16.0 degC; GT 425.0 MW (100.0 % load), HR 8,314 kJ/kWh; ST 200.73 MW; GSU losses GT 1107 kW, ST 584 kW; HRSG gas temperatures 640.0, 450.6, 371.6, 366.9, 295.1, 261.0, 198.7, 258.2, 166.2, 80.2 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 776.006 | 1.012 | 15.00 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 20.672 | 38.000 | 25.00 | - |
| 3 | Heated fuel gas to GT combustion system | FGH | GT | 20.672 | 35.500 | 215.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 796.678 | 1.048 | 640.00 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 796.678 | 1.014 | 80.16 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 100.155 | 187.000 | 600.00 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 100.155 | 181.500 | 598.50 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 100.155 | 40.200 | 366.21 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 100.155 | 39.500 | 365.21 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 17.338 | 40.300 | 330.00 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 117.493 | 37.600 | 600.00 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 117.493 | 36.200 | 598.50 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 11.901 | 5.400 | 250.00 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 11.901 | 5.050 | 249.00 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 117.493 | 4.950 | 309.20 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 129.394 | 0.03444 | 26.40 | 2,355.50 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 129.394 | 0.03444 | 26.35 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 129.394 | 16.000 | 26.52 | - |
| 19 | Fuel gas heater water return to condensate | FGH | CMIX | 12.481 | 43.000 | 75.00 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 141.874 | 15.500 | 30.85 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 129.973 | 5.900 | 158.13 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 100.155 | 209.000 | 161.83 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 29.819 | 46.000 | 158.89 | - |
| 24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 12.481 | 43.300 | 247.98 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 16.00 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 23.00 | - |

# 3.2 Case SRC-NG-GT80 - Site Reference Conditions, natural gas, GT at 80 % load

Ambient 15.0 degC, 70.0 % RH, seawater 16.0 degC; GT 340.0 MW (80.0 % load), HR 8,746 kJ/kWh; ST 175.05 MW; GSU losses GT 777 kW, ST 471 kW; HRSG gas temperatures 640.0, 457.0, 360.6, 355.9, 288.5, 252.8, 191.9, 250.1, 159.9, 76.1 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 679.101 | 1.012 | 15.00 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 17.398 | 38.000 | 25.00 | - |
| 3 | Heated fuel gas to GT combustion system | FGH | GT | 17.398 | 35.500 | 215.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 696.499 | 1.039 | 640.00 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 696.499 | 1.014 | 76.14 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 87.346 | 163.084 | 600.00 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 87.346 | 158.287 | 598.50 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 87.346 | 35.276 | 369.63 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 87.346 | 34.670 | 368.63 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 15.475 | 35.396 | 323.12 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 103.126 | 33.002 | 600.00 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 103.126 | 31.773 | 598.50 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 10.253 | 4.709 | 243.95 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 10.253 | 4.412 | 242.95 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 103.126 | 4.337 | 310.68 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 113.378 | 0.03204 | 25.18 | 2,366.47 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 113.378 | 0.03204 | 25.13 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 113.378 | 16.000 | 25.29 | - |
| 19 | Fuel gas heater water return to condensate | FGH | CMIX | 11.002 | 37.068 | 75.00 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 124.381 | 15.500 | 29.74 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 114.128 | 5.134 | 152.79 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 85.959 | 180.153 | 155.90 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 26.477 | 40.068 | 153.44 | - |
| 24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 11.002 | 38.256 | 240.73 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 16.00 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 22.18 | - |
| 29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 1.386 | 180.153 | 155.90 | - |
| 30 | Reheat attemperation spray water (BFP interstage) | BFP | HRSG | 0.305 | 40.068 | 153.44 | - |

# 3.3 Case SRC-NG-060 - Site Reference Conditions, natural gas, 60 % plant net load (guarantee PG-03)

Ambient 15.0 degC, 70.0 % RH, seawater 16.0 degC; GT 237.1 MW (55.8 % load), HR 9,629 kJ/kWh; ST 140.73 MW; GSU losses GT 475 kW, ST 343 kW; HRSG gas temperatures 636.6, 461.6, 343.7, 339.0, 280.4, 241.4, 182.2, 238.8, 151.0, 71.0 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 559.914 | 1.012 | 15.00 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 13.356 | 38.000 | 25.00 | - |
| 3 | Heated fuel gas to GT combustion system | FGH | GT | 13.356 | 35.500 | 215.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 573.270 | 1.030 | 636.63 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 573.270 | 1.014 | 71.02 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 71.022 | 132.605 | 600.00 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 71.022 | 128.705 | 598.50 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 71.022 | 29.015 | 377.29 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 71.022 | 28.528 | 376.29 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 13.430 | 29.192 | 310.90 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 84.855 | 27.155 | 600.00 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 84.855 | 26.144 | 598.50 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 8.244 | 3.845 | 235.08 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 8.244 | 3.610 | 234.08 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 84.855 | 3.562 | 316.36 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 93.100 | 0.02925 | 23.66 | 2,396.87 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 93.100 | 0.02925 | 23.61 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 93.100 | 16.000 | 23.77 | - |
| 19 | Fuel gas heater water return to condensate | FGH | CMIX | 9.062 | 29.824 | 75.00 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 102.161 | 15.500 | 28.36 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 93.917 | 4.182 | 145.17 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 69.435 | 144.757 | 147.58 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 22.491 | 32.824 | 145.69 | - |
| 24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 9.062 | 31.935 | 230.21 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 16.00 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 21.16 | - |
| 29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 1.587 | 144.757 | 147.58 | - |
| 30 | Reheat attemperation spray water (BFP interstage) | BFP | HRSG | 0.404 | 32.824 | 145.69 | - |

# 3.4 Case SRC-NG-MEL - Site Reference Conditions, natural gas, GT at minimum emissions-compliant load (40 %)

Ambient 15.0 degC, 70.0 % RH, seawater 16.0 degC; GT 170.0 MW (40.0 % load), HR 10,600 kJ/kWh; ST 113.23 MW; GSU losses GT 337 kW, ST 261 kW; HRSG gas temperatures 615.0, 458.2, 328.1, 323.5, 272.2, 231.1, 175.1, 228.6, 144.2, 69.1 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 486.356 | 1.012 | 15.00 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 10.543 | 38.000 | 25.00 | - |
| 3 | Heated fuel gas to GT combustion system | FGH | GT | 10.543 | 35.500 | 215.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 496.899 | 1.026 | 615.00 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 496.899 | 1.014 | 69.10 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 58.533 | 109.287 | 600.00 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 58.533 | 106.072 | 598.50 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 58.533 | 24.023 | 384.98 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 58.533 | 23.623 | 383.98 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 11.950 | 24.258 | 299.56 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 70.482 | 22.479 | 593.62 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 70.482 | 21.636 | 592.12 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 7.255 | 3.229 | 225.83 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 7.255 | 3.011 | 224.83 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 70.482 | 2.974 | 320.25 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 77.737 | 0.02726 | 22.50 | 2,428.23 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 77.737 | 0.02726 | 22.45 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 77.737 | 16.000 | 22.61 | - |
| 19 | Fuel gas heater water return to condensate | FGH | CMIX | 7.629 | 24.253 | 75.00 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 85.367 | 15.500 | 27.32 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 78.112 | 3.540 | 139.21 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 58.028 | 118.581 | 141.12 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 19.579 | 27.253 | 139.64 | - |
| 24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 7.629 | 26.942 | 221.08 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 16.00 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 20.37 | - |
| 29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 0.505 | 118.581 | 141.12 | - |

# 3.5 Case SRC-LDO-100 - Site Reference Conditions, LDO with water injection, base load (guarantee PG-15/16)

Ambient 15.0 degC, 70.0 % RH, seawater 16.0 degC; GT 395.0 MW (100.0 % load), HR 8,650 kJ/kWh; ST 175.45 MW; GSU losses GT 982 kW, ST 472 kW; HRSG gas temperatures 622.0, 453.9, 360.3, 355.5, 292.2, 254.5, 200.9, 251.5, 164.9, 82.8 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 671.131 | 1.012 | 15.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 715.820 | 1.041 | 622.00 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 715.820 | 1.014 | 82.80 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 86.464 | 161.438 | 600.00 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 86.464 | 156.690 | 598.50 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 86.464 | 35.290 | 371.24 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 86.464 | 34.697 | 370.24 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 17.220 | 35.595 | 318.67 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 103.685 | 33.011 | 590.38 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 103.685 | 31.769 | 588.88 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 12.935 | 5.035 | 240.19 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 12.935 | 4.579 | 239.19 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 103.685 | 4.461 | 306.81 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 116.619 | 0.03246 | 25.40 | 2,357.33 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 116.619 | 0.03246 | 25.35 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 116.619 | 16.000 | 25.51 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 116.619 | 15.500 | 25.53 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 103.685 | 5.669 | 156.58 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 86.312 | 178.718 | 159.71 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 17.220 | 38.671 | 157.21 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 16.00 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 22.33 | - |
| 27 | LDO at liquid fuel skid inlet (IEC terminal point IF-02) | LDS | GT | 22.123 | 5.000 | 30.00 | - |
| 28 | Demineralised water for NOx water injection (IF-03) | DMW | GT | 22.566 | 60.000 | 30.00 | - |
| 29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 0.152 | 178.718 | 159.71 | - |

# 3.6 Case WIN-NG-100 - Winter design (-4.8 degC, 99.6 %), natural gas, base load (GT at output limit)

Ambient -4.8 degC, 80.0 % RH, seawater 8.0 degC; GT 470.0 MW (100.0 % load), HR 8,131 kJ/kWh; ST 207.94 MW; GSU losses GT 1311 kW, ST 619 kW; HRSG gas temperatures 635.7, 447.0, 373.6, 368.9, 297.5, 263.3, 200.8, 260.5, 168.0, 77.0 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 810.099 | 1.012 | -4.80 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 22.357 | 38.000 | 25.00 | - |
| 3 | Heated fuel gas to GT combustion system | FGH | GT | 22.357 | 35.500 | 215.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 832.455 | 1.051 | 635.70 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 832.455 | 1.014 | 76.96 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 103.345 | 192.084 | 591.64 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 103.345 | 186.382 | 590.14 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 103.345 | 41.489 | 359.67 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 103.345 | 40.767 | 358.67 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 18.210 | 41.622 | 330.41 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 121.556 | 38.796 | 594.97 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 121.556 | 37.344 | 593.47 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 12.389 | 5.599 | 251.78 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 12.389 | 5.232 | 250.78 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 121.556 | 5.124 | 305.90 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 133.945 | 0.02174 | 18.82 | 2,335.41 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 133.945 | 0.02174 | 18.77 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 133.945 | 16.000 | 18.93 | - |
| 19 | Fuel gas heater water return to condensate | FGH | CMIX | 13.385 | 44.940 | 75.00 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 147.330 | 15.500 | 24.09 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 134.941 | 6.121 | 159.57 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 103.345 | 215.283 | 163.41 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 31.595 | 47.940 | 160.37 | - |
| 24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 13.385 | 44.724 | 249.33 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 8.00 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 15.28 | - |

# 3.7 Case MIN-NG-100 - Minimum ambient for full capability (-8 degC), natural gas, base load

Ambient -8.0 degC, 80.0 % RH, seawater 6.9 degC; GT 470.0 MW (100.0 % load), HR 8,089 kJ/kWh; ST 204.92 MW; GSU losses GT 1311 kW, ST 604 kW; HRSG gas temperatures 634.0, 448.0, 372.5, 367.8, 297.0, 262.5, 200.2, 259.7, 167.4, 76.1 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 801.288 | 1.012 | -8.00 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 22.242 | 38.000 | 25.00 | - |
| 3 | Heated fuel gas to GT combustion system | FGH | GT | 22.242 | 35.500 | 215.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 823.529 | 1.050 | 634.04 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 823.529 | 1.014 | 76.13 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 101.645 | 189.110 | 593.44 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 101.645 | 183.507 | 591.94 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 101.645 | 40.872 | 361.39 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 101.645 | 40.163 | 360.39 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 18.132 | 41.023 | 329.42 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 119.777 | 38.220 | 594.57 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 119.777 | 36.789 | 593.07 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 12.266 | 5.522 | 251.11 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 12.266 | 5.158 | 250.11 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 119.777 | 5.051 | 305.66 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 132.044 | 0.02013 | 17.59 | 2,335.98 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 132.044 | 0.02013 | 17.54 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 132.044 | 16.000 | 17.70 | - |
| 19 | Fuel gas heater water return to condensate | FGH | CMIX | 13.398 | 44.331 | 75.00 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 145.442 | 15.500 | 23.04 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 133.176 | 6.041 | 159.05 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 101.645 | 211.677 | 162.82 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 31.530 | 47.331 | 159.84 | - |
| 24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 13.398 | 44.135 | 248.35 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 6.90 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 14.10 | - |

# 3.8 Case SUM-NG-100 - Summer design (32.8 degC, 0.4 %), natural gas, base load

Ambient 32.8 degC, 45.0 % RH, seawater 24.0 degC; GT 372.8 MW (100.0 % load), HR 8,501 kJ/kWh; ST 184.53 MW; GSU losses GT 895 kW, ST 511 kW; HRSG gas temperatures 649.3, 455.9, 366.9, 362.3, 291.0, 256.8, 194.7, 254.1, 162.7, 81.7 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 710.980 | 1.012 | 32.80 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 18.541 | 38.000 | 25.00 | - |
| 3 | Heated fuel gas to GT combustion system | FGH | GT | 18.541 | 35.500 | 215.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 729.521 | 1.042 | 649.26 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 729.521 | 1.014 | 81.70 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 94.410 | 176.274 | 600.00 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 94.410 | 171.089 | 598.50 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 94.410 | 37.942 | 367.31 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 94.410 | 37.283 | 366.31 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 15.807 | 37.988 | 328.31 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 110.898 | 35.490 | 600.00 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 110.898 | 34.168 | 598.50 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 10.742 | 5.039 | 247.30 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 10.742 | 4.735 | 246.30 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 110.898 | 4.653 | 309.17 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 121.641 | 0.05271 | 33.82 | 2,396.36 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 121.641 | 0.05271 | 33.77 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 121.641 | 16.000 | 33.95 | - |
| 19 | Fuel gas heater water return to condensate | FGH | CMIX | 11.418 | 39.812 | 75.00 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 133.059 | 15.500 | 37.53 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 122.317 | 5.476 | 155.24 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 92.894 | 195.618 | 158.66 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 27.226 | 42.812 | 155.95 | - |
| 24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 11.418 | 40.810 | 244.84 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 24.00 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 30.61 | - |
| 29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 1.516 | 195.618 | 158.66 | - |
| 30 | Reheat attemperation spray water (BFP interstage) | BFP | HRSG | 0.681 | 42.812 | 155.95 | - |

# 3.9 Case MAX-NG-100 - Maximum ambient (40 degC) with maximum seawater (27 degC), natural gas, base load

Ambient 40.0 degC, 35.0 % RH, seawater 27.0 degC; GT 348.2 MW (100.0 % load), HR 8,595 kJ/kWh; ST 175.84 MW; GSU losses GT 805 kW, ST 474 kW; HRSG gas temperatures 653.0, 458.3, 364.0, 359.4, 288.7, 254.4, 192.5, 251.7, 160.7, 81.9 degC.

| No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | AMB | GT | 678.416 | 1.012 | 40.00 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 17.510 | 38.000 | 25.00 | - |
| 3 | Heated fuel gas to GT combustion system | FGH | GT | 17.510 | 35.500 | 215.00 | - |
| 4 | GT exhaust gas to HRSG inlet | GT | HRSG | 695.926 | 1.039 | 653.00 | - |
| 5 | Flue gas at HRSG outlet to stack | HRSG | STK | 695.926 | 1.014 | 81.92 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 91.085 | 170.065 | 600.00 | - |
| 7 | HP steam at ST main stop valve inlet | PIPE | ST | 91.085 | 165.063 | 598.50 | - |
| 8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 91.085 | 36.635 | 368.13 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 91.085 | 36.000 | 367.13 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 15.050 | 36.661 | 327.03 | - |
| 11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 107.082 | 34.268 | 600.00 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 107.082 | 32.992 | 598.50 | - |
| 13 | LP steam at HRSG outlet | HRSG | PIPE | 10.156 | 4.840 | 245.65 | - |
| 14 | LP steam at ST LP admission | PIPE | ST | 10.156 | 4.558 | 244.65 | - |
| 15 | IP turbine exhaust (crossover, internal) | ST | ST | 107.082 | 4.485 | 309.46 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 117.238 | 0.06113 | 36.50 | 2,416.50 |
| 17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 117.238 | 0.06113 | 36.45 | - |
| 18 | Condensate at CEP discharge | CEP | CMIX | 117.238 | 16.000 | 36.63 | - |
| 19 | Fuel gas heater water return to condensate | FGH | CMIX | 10.917 | 38.089 | 75.00 | - |
| 20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 128.155 | 15.500 | 39.95 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 118.000 | 5.246 | 153.61 | - |
| 22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 89.026 | 188.077 | 156.87 | - |
| 23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 25.967 | 41.089 | 154.28 | - |
| 24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 10.917 | 39.404 | 242.91 | - |
| 25 | Circulating seawater to condenser inlet | SEA | COND | 10,196.804 | 2.500 | 27.00 | - |
| 26 | Circulating seawater from condenser outlet | COND | OUT | 10,196.804 | 1.700 | 33.40 | - |
| 29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 2.058 | 188.077 | 156.87 | - |
| 30 | Reheat attemperation spray water (BFP interstage) | BFP | HRSG | 0.948 | 41.089 | 154.28 | - |