## Case summary
IEC-ALP-PER-003 Rev A - Case summary
Case | Ambient degC | RH % | Seawater degC | Fuel | GT load % | GT MW | GT HR kJ/kWh | Exhaust kg/s | Exhaust degC | ST MW | Gross MW | Stack degC | Condenser mbar | Spray HP/RH kg/s | Water inj. kg/s
SRC-NG-100 | 15 | 70 | 16 | GAS | 100 | 425 | 8314 | 796.7 | 640 | 200.73 | 625.73 | 80.2 | 34.4 | 0.00 / 0.00 | -
SRC-NG-GT80 | 15 | 70 | 16 | GAS | 80 | 340 | 8746 | 696.5 | 640 | 175.05 | 515.05 | 76.1 | 32 | 1.39 / 0.31 | -
SRC-NG-060 | 15 | 70 | 16 | GAS | 55.8 | 237.1 | 9629 | 573.3 | 636.6 | 140.73 | 377.8 | 71 | 29.2 | 1.59 / 0.40 | -
SRC-NG-MEL | 15 | 70 | 16 | GAS | 30 | 127.5 | 11640 | 442 | 598 | 94.37 | 221.87 | 68.1 | 25.9 | 0.00 / 0.00 | -
SRC-LDO-100 | 15 | 70 | 16 | LDO | 100 | 400.5 | 8640 | 811.9 | 592.7 | 178.37 | 578.87 | 89.7 | 33.4 | 0.00 / 0.00 | 13.44
WIN-NG-100 | -4.8 | 80 | 8 | GAS | 100 | 470 | 8131 | 832.5 | 635.7 | 207.94 | 677.95 | 77 | 21.7 | 0.00 / 0.00 | -
MIN-NG-100 | -8 | 80 | 6.9 | GAS | 100 | 470 | 8089 | 823.5 | 634 | 204.92 | 674.92 | 76.1 | 20.1 | 0.00 / 0.00 | -
SUM-NG-100 | 32.8 | 45 | 24 | GAS | 100 | 372.8 | 8501 | 729.5 | 649.3 | 184.53 | 557.33 | 81.7 | 52.7 | 1.52 / 0.68 | -
MAX-NG-100 | 40 | 35 | 27 | GAS | 100 | 348.2 | 8595 | 695.9 | 653 | 175.84 | 524.07 | 81.9 | 61.1 | 2.06 / 0.95 | -

## SRC-NG-100
IEC-ALP-PER-003 Rev A - SRC-NG-100
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 776.006 | 1.012 | 15 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 20.672 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | FGH | GT | 20.672 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 796.678 | 1.048 | 640 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 796.678 | 1.014 | 80.16 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 100.155 | 187 | 600 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 100.155 | 181.5 | 598.5 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 100.155 | 40.2 | 366.21 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 100.155 | 39.5 | 365.21 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 17.338 | 40.3 | 330 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 117.493 | 37.6 | 600 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 117.493 | 36.2 | 598.5 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 11.901 | 5.4 | 250 | -
14 | LP steam at ST LP admission | PIPE | ST | 11.901 | 5.05 | 249 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 117.493 | 4.95 | 309.2 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 129.394 | 0.03444 | 26.4 | 2355.5
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 129.394 | 0.03444 | 26.35 | -
18 | Condensate at CEP discharge | CEP | CMIX | 129.394 | 16 | 26.52 | -
19 | Fuel gas heater water return to condensate | FGH | CMIX | 12.481 | 43 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 141.874 | 15.5 | 30.85 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 129.973 | 5.9 | 158.13 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 100.155 | 209 | 161.83 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 29.819 | 46 | 158.89 | -
24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 12.481 | 43.3 | 247.98 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 16 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 23 | -

## SRC-NG-GT80
IEC-ALP-PER-003 Rev A - SRC-NG-GT80
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 679.101 | 1.012 | 15 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 17.398 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | FGH | GT | 17.398 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 696.499 | 1.039 | 640 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 696.499 | 1.014 | 76.14 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 87.346 | 163.084 | 600 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 87.346 | 158.287 | 598.5 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 87.346 | 35.276 | 369.63 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 87.346 | 34.67 | 368.63 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 15.475 | 35.396 | 323.12 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 103.126 | 33.002 | 600 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 103.126 | 31.773 | 598.5 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 10.253 | 4.709 | 243.95 | -
14 | LP steam at ST LP admission | PIPE | ST | 10.253 | 4.412 | 242.95 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 103.126 | 4.337 | 310.68 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 113.378 | 0.03204 | 25.18 | 2366.47
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 113.378 | 0.03204 | 25.13 | -
18 | Condensate at CEP discharge | CEP | CMIX | 113.378 | 16 | 25.29 | -
19 | Fuel gas heater water return to condensate | FGH | CMIX | 11.002 | 37.068 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 124.381 | 15.5 | 29.74 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 114.128 | 5.134 | 152.79 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 85.959 | 180.153 | 155.9 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 26.477 | 40.068 | 153.44 | -
24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 11.002 | 38.256 | 240.73 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 16 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 22.18 | -
29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 1.386 | 180.153 | 155.9 | -
30 | Reheat attemperation spray water (BFP interstage) | BFP | HRSG | 0.305 | 40.068 | 153.44 | -

## SRC-NG-060
IEC-ALP-PER-003 Rev A - SRC-NG-060
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 559.914 | 1.012 | 15 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 13.356 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | FGH | GT | 13.356 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 573.27 | 1.03 | 636.63 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 573.27 | 1.014 | 71.02 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 71.022 | 132.605 | 600 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 71.022 | 128.705 | 598.5 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 71.022 | 29.015 | 377.29 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 71.022 | 28.528 | 376.29 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 13.43 | 29.192 | 310.9 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 84.855 | 27.155 | 600 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 84.855 | 26.144 | 598.5 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 8.244 | 3.845 | 235.08 | -
14 | LP steam at ST LP admission | PIPE | ST | 8.244 | 3.61 | 234.08 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 84.855 | 3.562 | 316.36 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 93.1 | 0.02925 | 23.66 | 2396.87
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 93.1 | 0.02925 | 23.61 | -
18 | Condensate at CEP discharge | CEP | CMIX | 93.1 | 16 | 23.77 | -
19 | Fuel gas heater water return to condensate | FGH | CMIX | 9.062 | 29.824 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 102.161 | 15.5 | 28.36 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 93.917 | 4.182 | 145.17 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 69.435 | 144.757 | 147.58 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 22.491 | 32.824 | 145.69 | -
24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 9.062 | 31.935 | 230.21 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 16 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 21.16 | -
29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 1.587 | 144.757 | 147.58 | -
30 | Reheat attemperation spray water (BFP interstage) | BFP | HRSG | 0.404 | 32.824 | 145.69 | -

## SRC-NG-MEL
IEC-ALP-PER-003 Rev A - SRC-NG-MEL
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 433.268 | 1.012 | 15 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 8.682 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | FGH | GT | 8.682 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 441.951 | 1.023 | 598 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 441.951 | 1.014 | 68.15 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 50.31 | 93.719 | 595.75 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 50.31 | 90.949 | 594.25 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 50.31 | 20.646 | 387.59 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 50.31 | 20.302 | 386.59 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 10.61 | 20.885 | 291.34 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 60.92 | 19.307 | 581.92 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 60.92 | 18.574 | 580.42 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 6.357 | 2.796 | 218.65 | -
14 | LP steam at ST LP admission | PIPE | ST | 6.357 | 2.602 | 217.65 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 60.92 | 2.574 | 318.81 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 67.277 | 0.02595 | 21.68 | 2450.3
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 67.277 | 0.02595 | 21.63 | -
18 | Condensate at CEP discharge | CEP | CMIX | 67.277 | 16 | 21.79 | -
19 | Fuel gas heater water return to condensate | FGH | CMIX | 6.618 | 20.371 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 73.895 | 15.5 | 26.58 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 67.538 | 3.072 | 134.28 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 50.31 | 101.279 | 135.88 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 17.228 | 23.371 | 134.64 | -
24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 6.618 | 23.469 | 214.06 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 16 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 19.83 | -

## SRC-LDO-100
IEC-ALP-PER-003 Rev A - SRC-LDO-100
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 776.006 | 1.012 | 15 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 811.855 | 1.049 | 592.73 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 811.855 | 1.014 | 89.73 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 87.438 | 161.253 | 577.4 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 87.438 | 156.388 | 575.9 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 87.438 | 36.527 | 357.09 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 87.438 | 35.941 | 356.09 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 21.253 | 37.262 | 312.59 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 108.692 | 34.15 | 566.02 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 108.692 | 32.829 | 564.52 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 15.266 | 5.499 | 242.25 | -
14 | LP steam at ST LP admission | PIPE | ST | 15.266 | 4.907 | 241.25 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 108.692 | 4.742 | 291.27 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 123.958 | 0.0334 | 25.88 | 2334.77
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 123.958 | 0.0334 | 25.83 | -
18 | Condensate at CEP discharge | CEP | CMIX | 123.958 | 16 | 26 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 123.958 | 15.5 | 26.01 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 108.692 | 6.307 | 160.74 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 87.438 | 178.995 | 163.95 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 21.253 | 41.833 | 161.44 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 16 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 22.65 | -
27 | LDO at liquid fuel skid inlet (IEC terminal point IF-02) | LDS | GT | 22.406 | 5 | 30 | -
28 | Demineralised water for NOx water injection (IF-03) | DMW | GT | 13.443 | 60 | 30 | -

## WIN-NG-100
IEC-ALP-PER-003 Rev A - WIN-NG-100
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 810.099 | 1.012 | -4.8 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 22.357 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | FGH | GT | 22.357 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 832.455 | 1.051 | 635.7 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 832.455 | 1.014 | 76.96 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 103.345 | 192.084 | 591.64 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 103.345 | 186.382 | 590.14 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 103.345 | 41.489 | 359.67 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 103.345 | 40.767 | 358.67 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 18.21 | 41.622 | 330.41 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 121.556 | 38.796 | 594.97 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 121.556 | 37.344 | 593.47 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 12.389 | 5.599 | 251.78 | -
14 | LP steam at ST LP admission | PIPE | ST | 12.389 | 5.232 | 250.78 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 121.556 | 5.124 | 305.9 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 133.945 | 0.02174 | 18.82 | 2335.41
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 133.945 | 0.02174 | 18.77 | -
18 | Condensate at CEP discharge | CEP | CMIX | 133.945 | 16 | 18.93 | -
19 | Fuel gas heater water return to condensate | FGH | CMIX | 13.385 | 44.94 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 147.33 | 15.5 | 24.09 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 134.941 | 6.121 | 159.57 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 103.345 | 215.283 | 163.41 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 31.595 | 47.94 | 160.37 | -
24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 13.385 | 44.724 | 249.33 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 8 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 15.28 | -

## MIN-NG-100
IEC-ALP-PER-003 Rev A - MIN-NG-100
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 801.288 | 1.012 | -8 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 22.242 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | FGH | GT | 22.242 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 823.529 | 1.05 | 634.04 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 823.529 | 1.014 | 76.13 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 101.645 | 189.11 | 593.44 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 101.645 | 183.507 | 591.94 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 101.645 | 40.872 | 361.39 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 101.645 | 40.163 | 360.39 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 18.132 | 41.023 | 329.42 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 119.777 | 38.22 | 594.57 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 119.777 | 36.789 | 593.07 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 12.266 | 5.522 | 251.11 | -
14 | LP steam at ST LP admission | PIPE | ST | 12.266 | 5.158 | 250.11 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 119.777 | 5.051 | 305.66 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 132.044 | 0.02013 | 17.59 | 2335.98
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 132.044 | 0.02013 | 17.54 | -
18 | Condensate at CEP discharge | CEP | CMIX | 132.044 | 16 | 17.7 | -
19 | Fuel gas heater water return to condensate | FGH | CMIX | 13.398 | 44.331 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 145.442 | 15.5 | 23.04 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 133.176 | 6.041 | 159.05 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 101.645 | 211.677 | 162.82 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 31.53 | 47.331 | 159.84 | -
24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 13.398 | 44.135 | 248.35 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 6.9 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 14.1 | -

## SUM-NG-100
IEC-ALP-PER-003 Rev A - SUM-NG-100
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 710.98 | 1.012 | 32.8 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 18.541 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | FGH | GT | 18.541 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 729.521 | 1.042 | 649.26 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 729.521 | 1.014 | 81.7 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 94.41 | 176.274 | 600 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 94.41 | 171.089 | 598.5 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 94.41 | 37.942 | 367.31 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 94.41 | 37.283 | 366.31 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 15.807 | 37.988 | 328.31 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 110.898 | 35.49 | 600 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 110.898 | 34.168 | 598.5 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 10.742 | 5.039 | 247.3 | -
14 | LP steam at ST LP admission | PIPE | ST | 10.742 | 4.735 | 246.3 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 110.898 | 4.653 | 309.17 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 121.641 | 0.05271 | 33.82 | 2396.36
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 121.641 | 0.05271 | 33.77 | -
18 | Condensate at CEP discharge | CEP | CMIX | 121.641 | 16 | 33.95 | -
19 | Fuel gas heater water return to condensate | FGH | CMIX | 11.418 | 39.812 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 133.059 | 15.5 | 37.53 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 122.317 | 5.476 | 155.24 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 92.894 | 195.618 | 158.66 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 27.226 | 42.812 | 155.95 | -
24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 11.418 | 40.81 | 244.84 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 24 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 30.61 | -
29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 1.516 | 195.618 | 158.66 | -
30 | Reheat attemperation spray water (BFP interstage) | BFP | HRSG | 0.681 | 42.812 | 155.95 | -

## MAX-NG-100
IEC-ALP-PER-003 Rev A - MAX-NG-100
No | Description | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | AMB | GT | 678.416 | 1.012 | 40 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | FGS | FGH | 17.51 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | FGH | GT | 17.51 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | GT | HRSG | 695.926 | 1.039 | 653 | -
5 | Flue gas at HRSG outlet to stack | HRSG | STK | 695.926 | 1.014 | 81.92 | -
6 | HP steam at HRSG outlet (HP SH outlet) | HRSG | PIPE | 91.085 | 170.065 | 600 | -
7 | HP steam at ST main stop valve inlet | PIPE | ST | 91.085 | 165.063 | 598.5 | -
8 | Cold reheat steam at HP turbine exhaust | ST | PIPE | 91.085 | 36.635 | 368.13 | -
9 | Cold reheat steam at HRSG reheater inlet | PIPE | HRSG | 91.085 | 36 | 367.13 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | HRSG | HRSG | 15.05 | 36.661 | 327.03 | -
11 | Hot reheat steam at HRSG outlet | HRSG | PIPE | 107.082 | 34.268 | 600 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | PIPE | ST | 107.082 | 32.992 | 598.5 | -
13 | LP steam at HRSG outlet | HRSG | PIPE | 10.156 | 4.84 | 245.65 | -
14 | LP steam at ST LP admission | PIPE | ST | 10.156 | 4.558 | 244.65 | -
15 | IP turbine exhaust (crossover, internal) | ST | ST | 107.082 | 4.485 | 309.46 | -
16 | LP turbine exhaust to condenser (UEEP) | ST | COND | 117.238 | 0.06113 | 36.5 | 2416.5
17 | Condensate at hotwell outlet / CEP suction | COND | CEP | 117.238 | 0.06113 | 36.45 | -
18 | Condensate at CEP discharge | CEP | CMIX | 117.238 | 16 | 36.63 | -
19 | Fuel gas heater water return to condensate | FGH | CMIX | 10.917 | 38.089 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | CMIX | HRSG | 128.155 | 15.5 | 39.95 | -
21 | Feedwater from LP drum to boiler feed pumps | HRSG | BFP | 118 | 5.246 | 153.61 | -
22 | HP feedwater at BFP discharge to HP economiser | BFP | HRSG | 89.026 | 188.077 | 156.87 | -
23 | IP feedwater at BFP interstage to IP economiser | BFP | HRSG | 25.967 | 41.089 | 154.28 | -
24 | IP economiser water to performance fuel gas heater | HRSG | FGH | 10.917 | 39.404 | 242.91 | -
25 | Circulating seawater to condenser inlet | SEA | COND | 10196.804 | 2.5 | 27 | -
26 | Circulating seawater from condenser outlet | COND | OUT | 10196.804 | 1.7 | 33.4 | -
29 | HP attemperation spray water (BFP discharge) | BFP | HRSG | 2.058 | 188.077 | 156.87 | -
30 | Reheat attemperation spray water (BFP interstage) | BFP | HRSG | 0.948 | 41.089 | 154.28 | -