## Register
Alpilla 600 MW Combined Cycle Power Plant - Technical Query Register
engine clarification_register v1.0.0 ¦ generated 2026-09-27T17:19:53Z by SETUP ¦ data b3484cc0109a087a
TQ | Round | Follows | Raised by | Raised | Discipline | Subject | Question | Contractor proposal | References | Owner's answer | Answered | Status | Outcome | Impact | Price effect (EUR) | Records changed
TQ-001 | 1 |  | Imaginary Electric | 2026-09-18 | process | Site Reference seawater temperature 16.0 degC vs measured 15.4 degC | ER-02.03 and ER-07.08 fix the Site Reference seawater temperature at 16.0 degC. ALP-OWN-MAR-001 section 3 gives a measured annual mean of 15.4 degC at the intake depth. Which value is the contractual reference for PG-01/PG-02 and the condenser design? | Keep 16.0 degC as the contractual reference (our guarantees are priced on it); the measured data is used for the condenser/CW design range only. | requirement:ER-02.03 requirement:ER-07.08 source:SRC-OWNR-0002 design_parameter:DP-CASE-0014 | Confirmed: 16.0 degC remains the contractual Site Reference seawater temperature for all guarantees. The measured data in ALP-OWN-MAR-001 (annual mean 15.4 degC, range 6.9-27.0 degC) is the design range for the condenser and CW system. ER-02.03 is annotated accordingly. | 2026-09-22 | closed | confirmed as is | none |  | requirement/ER-02.03
TQ-002 | 1 |  | Imaginary Electric | 2026-09-18 | process | Gas LHV range: 45.0 MJ/kg (contract) vs 44.2 MJ/kg (network data) | ER-03.02 requires operation for LHV 45.0-50.0 MJ/kg; ALP-OWN-FUL-001 shows 44.2 MJ/kg for 3 % of hours (high N2/CO2 gas). Must the plant operate, and meet guarantees and emissions, below 45.0 MJ/kg? | Plant to operate and meet emission limits over 44.2-50.0 MJ/kg (the Wobbe range 47.2-51.8 is within the combustion system capability); performance guarantees remain at the reference gas. | requirement:ER-03.02 source:SRC-OWNR-0003 design_parameter:DP-CASE-0019 | Accepted. The plant shall operate and meet the emission limits for LHV 44.2-50.0 MJ/kg; performance guarantees apply at the reference gas with corrections per the agreed curves. | 2026-09-22 | closed | requirement changed | technical_only |  | requirement/ER-03.02 design_parameter/DP-CASE-0019
TQ-003 | 1 |  | Imaginary Electric | 2026-09-18 | process | Exceptional minimum gas pressure 40 barg is below the gas turbine requirement | The GT requires at least 43.5 barg at the fuel skid inlet at base load; with about 1.5 bar loss in the gas receiving station we need 45 barg at TP-G1. ALP-OWN-FUL-001 allows 40 barg for up to 72 h/year. Is a gas booster compressor expected, or may the plant transfer to LDO / reduce load during these periods? | No compressor. Below 45 barg the control system transfers automatically to LDO (ER-03.10); availability loss is limited to the transfer. Option price for a booster compressor on request. | requirement:ER-03.03 source:SRC-OWNR-0003 tie_in:TP-G1 | Superseded by TQ-017: load limitation between 40 and 45 barg, no compressor. | 2026-09-22 | closed | contractor proposal accepted | cost
TQ-004 | 1 |  | Imaginary Electric | 2026-09-18 | mechanical | Hydrogen admixture up to 10 vol % | The offered DLN combustion system is released for 5 vol % hydrogen. 10 vol % requires an upgraded combustor set that will be available as a retrofit. ALP-OWN-FUL-001 says 10 % is not firm before 2035. Please confirm the requirement. | 5 vol % without modification and with full guarantees; 10 vol % by future OEM retrofit, with provisions now (fuel system materials, gas detection, control system capacity). | requirement:ER-03.02 source:SRC-OWNR-0003 design_parameter:DP-CASE-0021 | Accepted: 5 vol % hydrogen without modification and with all guarantees; 10 vol % by future OEM retrofit (not in the Contract Price) with provisions now as proposed. | 2026-09-22 | closed | contractor proposal accepted | technical_only |  | requirement/ER-03.02 design_parameter/DP-CASE-0021
TQ-005 | 1 |  | Istanbul EPC | 2026-09-18 | mechanical | LDO alkali metals: delivered 1.0 mg/kg (history 1.8) vs 0.5 mg/kg at GT inlet | ER-03.07 requires Na+K <= 0.5 mg/kg at the GT inlet; ALP-OWN-FUL-002 says delivered LDO may contain up to 1.0 mg/kg and has reached 1.8 mg/kg. ER-03.09 asks for treatment 'if needed'. Is the Owner's intent that treatment is always included? | Treatment is needed: 2 x 100 % centrifugal separators with water washing. Not in our price (the tender was based on on-spec fuel): EUR 1,900,000. | requirement:ER-03.07 requirement:ER-03.09 source:SRC-OWNR-0004 scope_item:SC-053 | Rejected in round 1; resolved by the compromise in TQ-018. | 2026-09-22 | closed | price adjustment | none
TQ-006 | 1 |  | Istanbul EPC | 2026-09-18 | mechanical | LDO storage volume and resupply rate | 72 h at base load on LDO is about 6,900 m3 (two tanks of about 3,500 m3 net). The supplier's maximum of 25 trucks/day (about 825 m3/day) covers only about 36 % of base-load consumption. Please confirm that the plant is not required to run beyond the storage autonomy, and that 'net working volume' excludes heel and fire-fighting reserves. | Two tanks of 3,500 m3 net working volume each (about 4,000 m3 gross); no requirement to sustain operation beyond 72 h. | requirement:ER-03.08 source:SRC-OWNR-0004 tie_in:TP-L1 | Confirmed: two tanks of 3,500 m3 net working volume each (heel and fire-fighting reserves in addition); the plant is not required to operate beyond the storage autonomy. | 2026-09-22 | closed | requirement changed | technical_only |  | requirement/ER-03.08
TQ-007 | 1 |  | Istanbul EPC | 2026-09-18 | structural | Stack height 60 m (contract) vs 65 m (EIA decision) | ER-06.06 and Appendix E state 60 m; ALP-OWN-ENV-001 requires 65 m based on the approved dispersion study. Please confirm 65 m. | 65 m stack; additional cost EUR 180,000 (steel, foundation, platforms). | requirement:ER-06.06 design_parameter:DP-CASE-0043 source:SRC-OWNR-0007 | Accepted: stack height 65 m as required by the EIA decision; price adjustment EUR 180,000 accepted. | 2026-09-22 | closed | price adjustment | cost | 180000 | requirement/ER-06.06 design_parameter/DP-CASE-0043
TQ-008 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Sanitary wastewater: no municipal sewer at the Site | SC-043 assigns 'potable water and sewage connections at site boundary' to the Owner, but ALP-OWN-GEN-001 states that no sewer is available (TP-S1). Who provides sanitary wastewater treatment and discharge? | Contractor provides a packaged sanitary treatment plant (biological + UV), discharge through the outfall within EIA limits; EUR 350,000. | scope_item:SC-043 tie_in:TP-S1 source:SRC-OWNR-0005 source:SRC-OWNR-0007 | Accepted: the Owner provides potable water only. The Contractor provides a packaged sanitary wastewater treatment plant with discharge through the outfall within the EIA limits; EUR 350,000 accepted. | 2026-09-22 | closed | price adjustment | cost | 350000 | scope_item/SC-043 scope_item/SC-057 tie_in/TP-S1 requirement/ER-09.05
TQ-009 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Heavy transport: no jetty, 120 t bridges | The GT (about 460 t), generators (about 330 t) and GSU transformers (about 280 t) cannot use the state road. We plan a temporary barge landing on the 60 m public coastal strip. ALP-OWN-GEN-001 says the Owner can apply for the coastal permit (about 6 months). Please confirm the Owner obtains the permit and the dates. | Contractor designs, builds and removes the landing at its cost (within ER-02.14); Owner applies for the coastal permit within 30 days of receiving the design and obtains it by 2027-09-30, so the landing is built in the Oct 2027 - Apr 2028 window. | requirement:ER-02.14 source:SRC-OWNR-0005 source:SRC-OWNR-0007 | Confirmed: the Contractor designs, builds, operates and removes the temporary barge landing at its cost (ER-02.14). The Owner applies for the coastal permit within 30 days of receiving the Contractor's permit design and will use reasonable endeavours to obtain it by 2027-09-30. Please state when the permit design will be submitted. | 2026-09-22 | closed | owner to provide | time |  | requirement/ER-02.14 tie_in/TP-M1
TQ-010 | 1 |  | Istanbul EPC | 2026-09-18 | electrical | 380 kV line readiness 2028-09-30 is after the back-feed key date 2028-08-02 | Key date KD-010 (back-feed, 2028-08-02) and first fire KD-020 (2028-10-02) need the 380 kV line, which ALP-OWN-ELE-001 and TP-E1 give as ready on 2028-09-30. Please advance the line or move the key dates. | Owner to make TP-E1 available by 2028-07-15, or the key dates KD-010 to KD-040 move by about 2.5 months. | tie_in:TP-E1 source:SRC-OWNR-0006 contract_clause:ALP-EPC-001_9.4 | The Owner will accelerate its 380 kV line contract: TP-E1 will be available by 2028-07-15. The key dates remain unchanged. | 2026-09-22 | closed | owner to provide | none |  | tie_in/TP-E1
TQ-011 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Marine works window and marine permit date | Marine works are prohibited 1 May - 30 September (ALP-OWN-ENV-001). With the marine permit by 2027-04-30 (TP-CW1/CW2) the first usable window is October 2027 - April 2028, which must also carry the barge landing. Can the permit be obtained by 2027-02-28 to use part of the spring 2027 window? | Owner targets 2027-02-28; our programme will not depend on it. | tie_in:TP-CW1 tie_in:TP-CW2 source:SRC-OWNR-0007 | The contractual marine permit date remains 2027-04-30. The Owner will target 2027-02-28 without commitment. | 2026-09-22 | closed | confirmed as is | none
TQ-012 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Construction laydown area | The usable plot area is about 10.6 ha after setbacks, which is not enough for the power block, laydown, pre-assembly and contractor facilities. Will the Owner exercise its option on the 5 ha field north of the plot? | Owner exercises the option and makes the 5 ha available free of charge from 2027-03-01 until Taking-Over; the Contractor restores it. | requirement:ER-02.01 source:SRC-OWNR-0005 | Accepted: the Owner will exercise the option; the 5 ha field north of the plot is available free of charge from 2027-03-01 until Taking-Over; the Contractor restores it to its original condition. | 2026-09-22 | closed | owner to provide | none |  | tie_in/TP-A1 requirement/ER-02.01
TQ-013 | 1 |  | Imaginary Electric | 2026-09-18 | mechanical | Verification of salt removal at the GT air inlet | ER-02.10 requires Na+K at the compressor inlet within the OEM limit at the storm maximum (165 ug/m3). This cannot be tested on demand. Please accept verification by analysis plus monitoring. | Filter design report with OEM confirmation, plus an Na+K air sampler downstream of the filters with 12 months of data reported during the Defects Notification Period. | requirement:ER-02.10 source:SRC-OWNR-0001 | Accepted as proposed: verification by filter design report with OEM confirmation plus 12 months of Na+K air sampling downstream of the filters, reported during the Defects Notification Period. | 2026-09-22 | closed | contractor proposal accepted | technical_only |  | requirement/ER-02.10
TQ-014 | 1 |  | Imaginary Electric | 2026-09-18 | process | Status of the 36 mbar(a) condenser pressure | ER-07.08 sets 36 mbar(a) at SRC and names an ASME PTC 12.2 test, but there is no guarantee or LD for it. Is the condenser pressure a separate guarantee, or is compliance demonstrated through the plant heat rate guarantee? | Design requirement only; compliance through PG-02; PTC 12.2 test for information. | requirement:ER-07.08 guarantee:PG-02 | Accepted: the condenser pressure is a design requirement; contractual compliance is through PG-02. The ASME PTC 12.2 test is carried out for information. | 2026-09-22 | closed | contractor proposal accepted | technical_only |  | requirement/ER-07.08
TQ-015 | 1 |  | Istanbul EPC | 2026-09-18 | electrical | 380 kV switchgear in a C5 salt atmosphere | ER-11.01 asks for a GIS switchyard and ER-02.10 for very-heavy-pollution creepage outdoors. Is an indoor GIS in a building acceptable to the Owner? | Indoor GIS in a ventilated building; only line gantry bushings outdoors. No change to the price. | requirement:ER-11.01 requirement:ER-02.10 | Accepted: indoor GIS in a ventilated building, only the line gantry bushings outdoors; no price change. | 2026-09-22 | closed | contractor proposal accepted | technical_only |  | requirement/ER-11.01
TQ-016 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Relocation of the buried 11 kV cable | The 11 kV cable along the east boundary is relocated only by 2027-06-30 (ALP-OWN-GEN-001). Our layout places the LDO tank farm and warehouse in the east. Can the relocation be completed by 2027-02-28? | Owner to relocate by 2027-02-28; otherwise we re-sequence the east area works. | requirement:ER-02.13 source:SRC-OWNR-0005 | Not possible: the relocation is carried out by the regional utility and 2027-06-30 is its committed date. The Contractor shall sequence the east-area works accordingly. | 2026-09-22 | closed | rejected | none
TQ-017 | 2 | TQ-003 | Imaginary Electric | 2026-09-24 | process | Low gas pressure: booster compressor option vs load limitation | As requested: (a) booster compressor option, 2 x 100 % electric reciprocating units, 115,000 Sm3/h from 40 to 47 barg, about 1.3 MW each: EUR 6,800,000, 14 months delivery, no key-date impact if ordered by 2027-03-31. (b) Estimated operation below 45 barg: about 40 h/year based on the network data. (c) Zero-cost alternative: between 40 and 45 barg the GT reduces load to the pressure-limited load (about 60 % GT load at 40 barg) and stays on gas; transfer to LDO only below 40 barg. Which does the Owner choose? | Alternative (c): load limitation on gas between 40 and 45 barg, no compressor, no price change. | requirement:ER-03.03 requirement:ER-03.10 tie_in:TP-G1 source:SRC-OWNR-0003 | The Owner chooses alternative (c): no booster compressor. Between 40 and 45 barg the plant operates on gas at the pressure-limited load; automatic transfer to LDO only below 40 barg. ER-03.03 is revised. TQ-003 is closed by this answer. | 2026-09-26 | closed | contractor proposal accepted | technical_only |  | requirement/ER-03.03 clarification/TQ-003
TQ-018 | 2 | TQ-005 | Istanbul EPC | 2026-09-24 | commercial | LDO treatment - request to reconsider | ALP-OWN-FUL-002 lists Na+K <= 1.0 mg/kg 'as delivered, not guaranteed by supplier' in the specification table; our tender assumed the tabulated value, which the forwarding filters and water draining handle for most deliveries. The 1.8 mg/kg history is a note on other plants. The requirement 'if needed' is ambiguous for a lump-sum price. We propose a compromise. | Treatment (2 x 100 % centrifugal separators with water washing) included as mandatory scope; cost shared 50/50: EUR 950,000. The Owner adds to its LDO supply contract Na+K <= 1.0 mg/kg with sampling of each delivery. | requirement:ER-03.09 source:SRC-OWNR-0004 contract_clause:ALP-EPC-001_1.3 | Accepted as a compromise: fuel treatment (2 x 100 % centrifugal separators with water washing) becomes mandatory scope; cost shared, price adjustment EUR 950,000. The Owner will require Na+K <= 1.0 mg/kg with sampling of each delivery in its LDO supply contract (decision recorded). TQ-005 is closed by this answer. | 2026-09-26 | closed | price adjustment | cost | 950000 | requirement/ER-03.09 scope_item/SC-053 clarification/TQ-005 decision (LDO supply contract)
TQ-019 | 2 | TQ-009 | Istanbul EPC | 2026-09-24 | civil | Barge landing permit: submission and application dates | We will submit the barge landing permit design by 2027-03-31. Please confirm the Owner's application by 2027-04-30 and that the crossing of the public coastal strip by the intake and outfall pipelines is covered by the marine permit. | Dates as stated; crossing covered by the marine permit (TP-CW1/CW2). | tie_in:TP-M1 tie_in:TP-CW1 tie_in:TP-CW2 | Confirmed: the Owner applies for the coastal permit by 2027-04-30 provided the design is received by 2027-03-31; the crossing of the coastal strip by the intake and outfall pipelines is covered by the marine permit. TQ-009 is closed. | 2026-09-26 | closed | owner to provide | none |  | tie_in/TP-M1 clarification/TQ-009
TQ-020 | 2 | TQ-010 | Istanbul EPC | 2026-09-24 | electrical | Contractual status of the 380 kV line date 2028-07-15 | Please confirm that TP-E1 availability by 2028-07-15 is an Owner obligation under Sub-Clause 2.4 (so that a late line entitles the Contractor to an extension of time under Sub-Clause 9.4), and who coordinates the line energisation with the TSO. | Owner obligation; Owner energises the line with the TSO; Contractor coordinates the plant-side tests. | tie_in:TP-E1 contract_clause:ALP-EPC-001_2.4 contract_clause:ALP-EPC-001_9.4 requirement:ER-18.02 | Confirmed: availability of TP-E1 by 2028-07-15 is an Owner-furnished item under Sub-Clause 2.4; late availability entitles the Contractor to relief under Sub-Clause 9.4. The Owner energises the line with the TSO; the Contractor coordinates the plant-side protection settings and tests. TQ-010 is closed. | 2026-09-26 | closed | owner to provide | none |  | requirement/ER-18.02 clarification/TQ-010
TQ-021 | 2 |  | Imaginary Electric | 2026-09-24 | process | Demineralised water for LDO water injection | Water injection needs about 80 t/h of demineralised water at base load on LDO. ER-09.02 requires storage for 72 h of LDO operation (about 5,800 m3) on top of 3 days of cycle make-up: a very large tank for a fuel used less than 500 h/year. | Demin storage 2 x 1,250 m3 (cycle make-up plus about 24 h of water injection), demin plant sized for continuous water injection at 50 % LDO load, plus a connection for mobile demin trailers. No price change. | requirement:ER-09.02 requirement:ER-03.11 source:SRC-OWNR-0004 | Accepted as proposed: demin storage 2 x 1,250 m3, demin plant sized for continuous water injection at 50 % LDO load, and a connection for mobile demin trailers; no price change. | 2026-09-26 | closed | contractor proposal accepted | technical_only |  | requirement/ER-09.02
TQ-022 | 2 | TQ-001 | Imaginary Electric | 2026-09-24 | process | Seawater temperature correction in the performance test | Following TQ-001, please confirm that the performance test corrects from the measured seawater temperature during the test to the 16.0 degC reference using the agreed correction curves. | Confirmed as stated. | requirement:ER-16.04 requirement:ER-02.03 guarantee:PG-01 guarantee:PG-02 | Confirmed: corrections from the measured test seawater temperature to 16.0 degC with the agreed correction curves. | 2026-09-26 | closed | confirmed as is | none
TQ-023 | 3 |  | Imaginary Electric | 2026-09-26 | process | Reference LDO for the LDO performance guarantees | ALP-OWN-FUL-002 allows FAME (biodiesel) up to 7 % v/v and LHV 42.6-43.2 MJ/kg. PG-15/PG-16 refer to LHV 42.9 MJ/kg but not to FAME or water content, which affect output, heat rate and water injection. Please define the reference LDO for the guarantees. | Reference LDO: LHV 42.9 MJ/kg, FAME 0 %, water 100 mg/kg, H/C per the test fuel analysis; corrections for the actual test fuel by agreed curves. | guarantee:PG-15 guarantee:PG-16 source:SRC-OWNR-0004 requirement:ER-03.07 | Accepted as proposed; PG-15 and PG-16 conditions revised. | 2026-09-27 | closed | contractor proposal accepted | technical_only |  | guarantee/PG-15 guarantee/PG-16
TQ-024 | 3 |  | Istanbul EPC | 2026-09-26 | commercial | Consolidated price and incorporation of the clarifications | All technical queries TQ-001 to TQ-023 are closed or answered. Agreed price adjustments: TQ-007 EUR 180,000, TQ-008 EUR 350,000, TQ-018 EUR 950,000; total EUR 1,480,000 (onshore portion). No time impacts. We propose the Contract Price of EUR 532,480,000 and that the clarification register becomes Appendix I of the Contract, prevailing over Appendix A where it modifies it. Please confirm readiness for signature on 2026-10-15. | Contract Price EUR 532,480,000 (offshore 327,000,000; onshore 205,480,000); Appendix H Owner documents and Appendix I agreed clarifications added to the contract documents. | contract_clause:ALP-EPC-001_A3 contract_clause:ALP-EPC-001_A4 | Confirmed. Contract Price EUR 532,480,000 (offshore EUR 327,000,000; onshore EUR 205,480,000); Appendix H (Owner-provided documents) and Appendix I (agreed clarifications) are added to the contract documents in Article A3. The Contract is agreed and ready for signature on 2026-10-15. | 2026-09-27 | closed | price adjustment | cost | 0 | contract/ALP-EPC-001 contract_clause/ALP-EPC-001_A3 contract_clause/ALP-EPC-001_A4

## Summary
By round | Raised | Closed | Open | Price effect (EUR)
Round 1 | 16 | 16 | 0 | 530000
Round 2 | 6 | 6 | 0 | 950000
Round 3 | 2 | 2 | 0 | 0
Total | 24 | 24 | 0 | 1480000
By outcome | Count
confirmed as is | 3
contractor proposal accepted | 8
owner to provide | 5
price adjustment | 5
rejected | 1
requirement changed | 2