IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Division of Responsibility - Power Island (IEC) and Balance of Plant (EPC)

| Document number | IEC-ALP-DOR-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-27 |
| Status | Issued for EPC engineering (reference data) |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-09-27 | signed 2026-09-27 | signed 2026-09-27 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. Division of responsibility between IEC and the EPC

Design / Supply / Erection / Supervision (of erection) / Commissioning. 'IEC with EPC' = IEC leads, EPC provides labour, utilities and plant systems. Items not listed follow the consortium agreement: power island equipment by IEC (Owner contract items SC-006 to SC-010, SC-012 to SC-014, SC-029, SC-037, SC-054), everything else by EPC.

| No | Item | Design | Supply | Erection | Supervision | Commissioning | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1.1 | Gas turbine package incl. enclosure, lube oil, hydraulic and fuel skids | IEC | IEC | EPC | IEC | IEC with EPC |  |
| 1.2 | GT inlet air filter house, anti-icing, silencer, inlet duct | IEC | IEC | EPC | IEC | IEC | evaporative cooler: space provision only (not included) |
| 1.3 | GT exhaust diffuser and expansion joint to HRSG | IEC | IEC | EPC | IEC | IEC |  |
| 1.4 | Performance fuel gas heater and GT gas skid (from IF-01) | IEC | IEC | EPC | IEC | IEC |  |
| 1.5 | Gas receiving and metering station, start-up gas heating, final filtration 3 um | EPC | EPC | EPC | - | EPC | IEC fuel gas requirements per DS-101 |
| 1.6 | Liquid fuel skid, water injection skid, purge and recirculation (from IF-02/03) | IEC | IEC | EPC | IEC | IEC |  |
| 1.7 | LDO unloading, storage, forwarding and treatment | EPC | EPC | EPC | - | EPC |  |
| 1.8 | Compressor washing skid | IEC | IEC | EPC | IEC | IEC | demin water by EPC |
| 1.9 | GT enclosure fire suppression (CO2) and gas detection | IEC | IEC | EPC | IEC | IEC | fire alarm panel by EPC |
| 2.1 | HRSG pressure parts, casing, drums, platforms, CPH recirculation pumps | IEC | IEC | EPC | IEC | EPC with IEC |  |
| 2.2 | SCR catalyst, ammonia injection grid and skid, CO catalyst | IEC | IEC | EPC | IEC | EPC with IEC |  |
| 2.3 | Aqueous ammonia unloading, storage and forwarding | EPC | EPC | EPC | - | EPC | not in the Owner contract scope list |
| 2.4 | HRSG blowdown tanks, drain tanks, atmospheric flash tanks | EPC | EPC | EPC | - | EPC | IEC gives flows and conditions |
| 2.5 | Chemical dosing and steam/water sampling (SWAS) | EPC | EPC | EPC | - | EPC | IEC sample/dosing nozzles |
| 2.6 | Stack incl. silencer, CEMS, aviation lighting | EPC | EPC | EPC | - | EPC | 65 m (ER-06.06) |
| 3.1 | Steam turbine with valves, lube/EHC oil, gland steam system, turning gear | IEC | IEC | EPC | IEC | IEC |  |
| 3.2 | HP / IP / LP bypass valves with desuperheaters | IEC | IEC | EPC | IEC | IEC with EPC | loose supply |
| 3.3 | HP, cold reheat, hot reheat and LP steam piping HRSG - ST incl. supports | EPC | EPC | EPC | - | EPC | IEC: nozzle loads, pressure drop assumptions (PER-001 1) |
| 3.4 | Bypass piping and spray water piping | EPC | EPC | EPC | - | EPC |  |
| 3.5 | ST drains, drain collection and flash tank | EPC | EPC | EPC | - | EPC | IEC drain list |
| 4.1 | Condenser incl. dump devices, hotwell, vacuum pumps | IEC | IEC | EPC | IEC | EPC with IEC |  |
| 4.2 | Tube cleaning ball system and debris filters | EPC | EPC | EPC | - | EPC | required by ER-07.03 |
| 4.3 | Circulating water system, intake, pumps, outfall, electro-chlorination | EPC | EPC | EPC | - | EPC |  |
| 4.4 | Condensate pumps, boiler feed pumps, condensate polishing | EPC | EPC | EPC | - | EPC | IEC pressure assumptions PER-001 |
| 4.5 | Closed cooling water system | EPC | EPC | EPC | - | EPC | IEC cooler demands REQ-001 5.1 |
| 5.1 | GT and ST generators incl. excitation, neutral earthing | IEC | IEC | EPC | IEC | IEC |  |
| 5.2 | Generator circuit breakers, isolated phase busducts | IEC | IEC | EPC | IEC | IEC |  |
| 5.3 | GT and ST generator step-up transformers | IEC | IEC | EPC | IEC | IEC with EPC |  |
| 5.4 | SFC and isolation transformer | IEC | IEC | EPC | IEC | IEC |  |
| 5.5 | Generator and GSU protection panels | IEC | IEC | EPC | IEC | IEC with EPC |  |
| 5.6 | H2 and CO2 bottle racks and supply piping | EPC | EPC | EPC | - | EPC | IEC gas control panel |
| 5.7 | Unit auxiliary transformers, MV/LV switchgear, UPS/DC, cabling | EPC | EPC | EPC | - | EPC |  |
| 5.8 | 380 kV connection GSU - GIS, GIS switchyard | EPC | EPC | EPC | - | EPC |  |
| 6.1 | Turbine control system (TCS) for GT, ST, generators, HRSG protection (SIS) | IEC | IEC | EPC | IEC | IEC | stand-alone TCS with OPC UA gateway to the DCS |
| 6.2 | Plant DCS incl. HRSG and BOP control, operator stations | EPC | EPC | EPC | - | EPC | TCS HMI screens via gateway |
| 6.3 | CEMS | EPC | EPC | EPC | - | EPC |  |
| 6.4 | Vibration and performance monitoring, remote diagnostics | IEC | IEC | EPC | IEC | IEC | secure link by EPC (IEC 62443) |
| 7.1 | Foundations of IEC equipment (GT, generators, ST, HRSG, condenser, GSUs) | EPC | EPC | EPC | - | - | IEC load data, anchor bolts and sole plates |
| 7.2 | Turbine hall(s), cranes, HRSG access structures beyond IEC platforms | EPC | EPC | EPC | - | - |  |
| 8.1 | Transport of IEC equipment to site (incl. heavy transport, barge, SPMT) | - | IEC to port of discharge; EPC from port to foundation | - | - | - | barge landing TP-M1 by EPC |
| 8.2 | Performance test | EPC with IEC | EPC (test instruments) | - | IEC | EPC | ASME PTC 46 |
| 8.3 | Training of Owner staff on IEC equipment | IEC | IEC | - | - | - |  |