## Division of responsibility
IEC-ALP-DOR-001 Rev 0 - Division of responsibility
No | Item | Design | Supply | Erection | Supervision | Commissioning | Remarks
1.1 | Gas turbine package incl. enclosure, lube oil, hydraulic and fuel skids | IEC | IEC | EPC | IEC | IEC with EPC
1.2 | GT inlet air filter house, anti-icing, silencer, inlet duct | IEC | IEC | EPC | IEC | IEC | evaporative cooler: space provision only (not included)
1.3 | GT exhaust diffuser and expansion joint to HRSG | IEC | IEC | EPC | IEC | IEC
1.4 | Performance fuel gas heater and GT gas skid (from IF-01) | IEC | IEC | EPC | IEC | IEC
1.5 | Gas receiving and metering station, start-up gas heating, final filtration 3 um | EPC | EPC | EPC | - | EPC | IEC fuel gas requirements per DS-101
1.6 | Liquid fuel skid, water injection skid, purge and recirculation (from IF-02/03) | IEC | IEC | EPC | IEC | IEC
1.7 | LDO unloading, storage, forwarding and treatment | EPC | EPC | EPC | - | EPC
1.8 | Compressor washing skid | IEC | IEC | EPC | IEC | IEC | demin water by EPC
1.9 | GT enclosure fire suppression (CO2) and gas detection | IEC | IEC | EPC | IEC | IEC | fire alarm panel by EPC
2.1 | HRSG pressure parts, casing, drums, platforms, CPH recirculation pumps | IEC | IEC | EPC | IEC | EPC with IEC
2.2 | SCR catalyst, ammonia injection grid and skid, CO catalyst | IEC | IEC | EPC | IEC | EPC with IEC
2.3 | Aqueous ammonia unloading, storage and forwarding | EPC | EPC | EPC | - | EPC | not in the Owner contract scope list
2.4 | HRSG blowdown tanks, drain tanks, atmospheric flash tanks | EPC | EPC | EPC | - | EPC | IEC gives flows and conditions
2.5 | Chemical dosing and steam/water sampling (SWAS) | EPC | EPC | EPC | - | EPC | IEC sample/dosing nozzles
2.6 | Stack incl. silencer, CEMS, aviation lighting | EPC | EPC | EPC | - | EPC | 65 m (ER-06.06)
3.1 | Steam turbine with valves, lube/EHC oil, gland steam system, turning gear | IEC | IEC | EPC | IEC | IEC
3.2 | HP / IP / LP bypass valves with desuperheaters | IEC | IEC | EPC | IEC | IEC with EPC | loose supply
3.3 | HP, cold reheat, hot reheat and LP steam piping HRSG - ST incl. supports | EPC | EPC | EPC | - | EPC | IEC: nozzle loads, pressure drop assumptions (PER-001 1)
3.4 | Bypass piping and spray water piping | EPC | EPC | EPC | - | EPC
3.5 | ST drains, drain collection and flash tank | EPC | EPC | EPC | - | EPC | IEC drain list
4.1 | Condenser incl. dump devices, hotwell, vacuum pumps | IEC | IEC | EPC | IEC | EPC with IEC
4.2 | Tube cleaning ball system and debris filters | EPC | EPC | EPC | - | EPC | required by ER-07.03
4.3 | Circulating water system, intake, pumps, outfall, electro-chlorination | EPC | EPC | EPC | - | EPC
4.4 | Condensate pumps, boiler feed pumps, condensate polishing | EPC | EPC | EPC | - | EPC | IEC pressure assumptions PER-001
4.5 | Closed cooling water system | EPC | EPC | EPC | - | EPC | IEC cooler demands REQ-001 5.1
5.1 | GT and ST generators incl. excitation, neutral earthing | IEC | IEC | EPC | IEC | IEC
5.2 | Generator circuit breakers, isolated phase busducts | IEC | IEC | EPC | IEC | IEC
5.3 | GT and ST generator step-up transformers | IEC | IEC | EPC | IEC | IEC with EPC
5.4 | SFC and isolation transformer | IEC | IEC | EPC | IEC | IEC
5.5 | Generator and GSU protection panels | IEC | IEC | EPC | IEC | IEC with EPC
5.6 | H2 and CO2 bottle racks and supply piping | EPC | EPC | EPC | - | EPC | IEC gas control panel
5.7 | Unit auxiliary transformers, MV/LV switchgear, UPS/DC, cabling | EPC | EPC | EPC | - | EPC
5.8 | 380 kV connection GSU - GIS, GIS switchyard | EPC | EPC | EPC | - | EPC
6.1 | Turbine control system (TCS) for GT, ST, generators, HRSG protection (SIS) | IEC | IEC | EPC | IEC | IEC | stand-alone TCS with OPC UA gateway to the DCS
6.2 | Plant DCS incl. HRSG and BOP control, operator stations | EPC | EPC | EPC | - | EPC | TCS HMI screens via gateway
6.3 | CEMS | EPC | EPC | EPC | - | EPC
6.4 | Vibration and performance monitoring, remote diagnostics | IEC | IEC | EPC | IEC | IEC | secure link by EPC (IEC 62443)
7.1 | Foundations of IEC equipment (GT, generators, ST, HRSG, condenser, GSUs) | EPC | EPC | EPC | - | - | IEC load data, anchor bolts and sole plates
7.2 | Turbine hall(s), cranes, HRSG access structures beyond IEC platforms | EPC | EPC | EPC | - | -
8.1 | Transport of IEC equipment to site (incl. heavy transport, barge, SPMT) | - | IEC to port of discharge; EPC from port to foundation | - | - | - | barge landing TP-M1 by EPC
8.2 | Performance test | EPC with IEC | EPC (test instruments) | - | IEC | EPC | ASME PTC 46
8.3 | Training of Owner staff on IEC equipment | IEC | IEC | - | - | -