IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Gas Turbine IE-9H.02 - Datasheet

| Document number | IEC-ALP-DS-101 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-27 |
| Status | Issued for EPC engineering (reference data) |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-09-27 | signed 2026-09-27 | signed 2026-09-27 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. General

| Item | Data |
| --- | --- |
| Model | IE-9H.02 heavy-duty single-shaft gas turbine, 50 Hz, 3,000 rpm, cold-end drive, axial exhaust |
| Fleet experience | 11 units in commercial operation, lead unit 38,000 fired hours (ER-01.08: complies) |
| Compressor | 14 stages, pressure ratio 23.8:1, variable IGV + 3 rows of variable stator vanes |
| Combustion system | IE DLN-H2, 16 can-annular combustors, dual fuel (natural gas / LDO), water injection on LDO, up to 30 vol % H2 capable hardware (5 % without modification) |
| Turbine | 4 stages, air-cooled, single-crystal stage 1 blades, thermal barrier coatings |
| Starting | Static frequency converter (SFC) through the generator, 8.5 MW input from 10.5 kV |
| Enclosure | Acoustic enclosure 85 dB(A) at 1 m, ventilation 2 x 100 % fans, gas detection, CO2 fire suppression |
| Inlet air system | Filter house 3 stages: G4 weather louvre/coalescer, F9, EPA E12; anti-icing by compressor bleed; silencer. Evaporative cooler: space provision only, not included |

# 2. Ratings

| Condition | Output MW | Heat rate kJ/kWh | Efficiency % | Exhaust kg/s | Exhaust degC |
| --- | --- | --- | --- | --- | --- |
| ISO 2314 (15 degC, 60 %, 1013.25 mbar, no inlet/outlet losses), gas | 432.0 | 8,240 | 43.69 | 801.0 | 638.0 |
| SRC-NG-100 (10/36 mbar losses, fuel 215 degC) | 425.0 | 8,314 | 43.30 | 796.7 | 640.0 |
| SRC, LDO with water injection (base load) | 395.0 | 8,650 | 41.62 | 812.0 | 622.0 |
| Maximum output (cold ambient, generator/shaft limit) | 470.0 | - | - | - | - |

# 3. Fuel requirements (at IEC terminal points, see IEC-ALP-IF-001)

| Parameter | Natural gas (IF-01, performance gas heater inlet) | LDO (IF-02, liquid fuel skid inlet) |
| --- | --- | --- |
| Pressure | 36.5 barg minimum at base load; 41.0 barg maximum; max. rate of change 0.7 bar/s | 3.0 - 6.0 barg |
| Temperature | 5 - 40 degC and at least 28 K above the hydrocarbon and water dew points | 10 - 45 degC |
| Flow at base load (SRC) | 20.67 kg/s | 22.1 kg/s (+ demin water 22.5 kg/s at IF-03) |
| Quality | ALP-OWN-FUL-001 range; Wobbe index change <= 1 %/min; trace metals Na+K <= 0.02 mg/Sm3 equivalent; particulates filtered to 3 um absolute (EPC final filter) | ER-03.07 limits at the GT inlet; filtration 5 um (IEC skid) |
| Fuel heating | IEC performance gas heater to 215 degC with IP feedwater; start-up heating by EPC gas station (electric or water-bath heater, gas >= 28 K superheat) | - |

# 4. Emissions and noise

| Parameter | Natural gas | LDO |
| --- | --- | --- |
| NOx at GT outlet (15 % O2, dry), 40-100 % load | <= 50 mg/Nm3 | <= 90 mg/Nm3 (water/fuel ratio 1.02) |
| CO at GT outlet, 40-100 % load | <= 20 mg/Nm3 | <= 25 mg/Nm3 |
| Minimum emissions-compliant GT load (MECL) | 40 % GT load (with SCR) | 50 % GT load |
| Near-field noise, enclosure and inlet | 85 dB(A) at 1 m | 85 dB(A) at 1 m |

# 5. Operation and maintenance

| Item | Data |
| --- | --- |
| Start to base load (GT) | hot start 25 min, warm 35 min, cold 45 min (GT only; CC limited by HRSG/ST) |
| Load ramp (GT) | 40 MW/min normal, 65 MW/min fast |
| Combustion inspection / hot gas path / major inspection | 12,500 / 25,000 / 50,000 EOH, or 900 / 900 / 1,800 starts, whichever first |
| Equivalent operating hours (EOH) | EOH = fired hours + 20 x starts + 60 x trips from base load + 2 x h on LDO |
| Lube oil | ISO VG 32 mineral, tank 28 m3, 2 x 100 % AC pumps + DC emergency pump; cooling duty 1.6 MW |
| Compressor washing | on-line and off-line; detergent skid by IEC; demin water 5 m3 per off-line wash |

# 6. Dimensions, weights and transport

| Item | Dimensions L x W x H (m) | Weight (t) |
| --- | --- | --- |
| GT core engine (shipping, with transport frame) | 13.2 x 5.9 x 5.6 | 405 |
| Exhaust diffuser (2 pieces) | 8.5 x 7.2 x 7.0 | 2 x 62 |
| Inlet filter house (modules) | 18 modules | max. 28 per module |
| GT rotor (maintenance lift) | 11.0 x 3.2 x 3.2 | 112 |

The GT core engine exceeds the 120 t road limit (ALP-OWN-GEN-001): delivery by barge to the landing TP-M1; the EPC shall design the barge landing and the haul road for a 480 t gross transport (SPMT).

# 7. Auxiliary power (base load, SRC)

GT package auxiliaries 1,180 kW (lube oil, hydraulic, enclosure ventilation, fuel gas skid, filter house); SFC 8.5 MW during start-up only. See IEC-ALP-REQ-001 table 7.1.