IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Generator Step-up Transformers - Datasheet

| Document number | IEC-ALP-DS-106 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-27 |
| Status | Issued for EPC engineering (reference data) |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-09-27 | signed 2026-09-27 | signed 2026-09-27 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. Generator step-up transformers

| Item | GT GSU | ST GSU |
| --- | --- | --- |
| Rating | 560 MVA ONAF (336 MVA ONAN) | 270 MVA ONAF (162 MVA ONAN) |
| Voltage ratio / vector group | 400 +/- 8 x 1.25 % / 21 kV, YNd11, OLTC | 400 +/- 8 x 1.25 % / 15.75 kV, YNd11, OLTC |
| Impedance | 14.5 % | 13.5 % |
| No-load losses / load losses at rating | 190 kW / 1,150 kW | 110 kW / 620 kW |
| Losses at SRC-NG-100 load (P, pf 0.85) | 1,110 kW | 580 kW |
| Insulation level HV / neutral | LI 1425 kV / SI 1050 kV; neutral solidly earthed | same |
| Oil | natural ester (K-class) - fire risk reduction; oil volume 98 m3 | natural ester; 62 m3 |
| Transport weight (without oil, nitrogen-filled) / dimensions | 268 t / 11.2 x 4.1 x 4.6 m | 168 t / 9.4 x 3.8 x 4.3 m |
| Total weight | 395 t | 245 t |
| HV connection | HV bushings with air terminal; 380 kV connection to the GIS by EPC (IF-34/IF-35) | same |
| Monitoring | on-line DGA, bushing monitoring, fibre-optic hot-spot; IEC 61850 to the EPC substation system | same |

# 2. Interfaces

Transformer foundations, oil pits (110 % oil volume), fire walls and deluge system: by EPC (NFPA 850, IEC 61936-1).

380 kV HV connection from the bushings to the GIS, surge arresters at the HV bushings: by EPC.

IPB connection flanges at the LV bushings: by IEC.