IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Terminal Points and Interface Data - Power Island

| Document number | IEC-ALP-IF-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-27 |
| Status | Issued for EPC engineering (reference data) |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-09-27 | signed 2026-09-27 | signed 2026-09-27 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. Terminal points between IEC and the EPC

Each terminal point is the physical boundary between the IEC supply (power island) and the EPC's balance of plant. Design conditions are the IEC design values of the IEC component; the EPC side shall be designed for at least the same conditions. Nozzle load limits: attachment A (to follow with IEC-ALP-IF-001 Rev A, 8 weeks after NTP).

| Tag | Service | IEC side | EPC side | Medium | Size / rating | Design p / T | Operating (SRC) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| IF-01 | Natural gas to GT | performance gas heater inlet flange | gas from EPC gas receiving/metering station | natural gas | 12" ASME CL600 RF | 63 barg / 80 degC | 20.67 kg/s, 37.0 barg, 25 degC |
| IF-02 | LDO to GT | liquid fuel skid inlet flange | LDO forwarding/treatment system | LDO | 6" CL150 | 16 barg / 60 degC | 22.1 kg/s (LDO operation) |
| IF-03 | Demin water for water injection | water injection skid inlet | demin water storage/pumps | demin water | 4" CL150 | 16 barg / 50 degC | 22.5 kg/s (LDO operation) |
| IF-04 | Compressor wash water | wash skid inlet | demin water | demin water | 2" CL150 | 10 barg / 50 degC | 5 m3 per wash |
| IF-05 | HP steam | HRSG HP SH outlet stop valve, weld end | main steam piping (EPC) | steam | 12" (P91) weld end | 210 bar(a) / 610 degC | 100.16 kg/s, 187.0 bar(a), 600 degC |
| IF-06 | HP steam | ST main stop valve inlet, weld end | main steam piping (EPC) | steam | 12" (P91) weld end | 200 bar(a) / 605 degC | 180.0 bar(a), 597 degC |
| IF-07 | Cold reheat | HP turbine exhaust, weld end | cold reheat piping (EPC) | steam | 24" (P22/A106) weld end | 52 bar(a) / 420 degC | 40.2 bar(a), 366 degC |
| IF-08 | Cold reheat | HRSG reheater inlet, weld end | cold reheat piping (EPC) | steam | 24" weld end | 52 bar(a) / 420 degC | 39.4 bar(a), 365 degC |
| IF-09 | Hot reheat | HRSG reheater outlet stop valve, weld end | hot reheat piping (EPC) | steam | 28" (P91) weld end | 50 bar(a) / 610 degC | 117.50 kg/s, 37.6 bar(a) |
| IF-10 | Hot reheat | ST IP stop-control valve inlet | hot reheat piping (EPC) | steam | 28" (P91) weld end | 48 bar(a) / 605 degC | 36.0 bar(a), 597 degC |
| IF-11 | LP steam | HRSG LP SH outlet stop valve | LP steam piping (EPC) | steam | 20" weld end | 10 bar(a) / 330 degC | 11.39 kg/s, 5.40 bar(a) |
| IF-12 | LP steam | ST LP admission valve inlet | LP steam piping (EPC) | steam | 20" weld end | 8 bar(a) / 330 degC | 4.95 bar(a) |
| IF-13 | HP / IP / LP bypass valves | valves supplied loose by IEC (incl. desuperheating) | installation in EPC piping, spray water from BFP/CEP (EPC) | steam / water | per valve datasheets | - | start-up / trip |
| IF-14 | Bypass steam to condenser | condenser neck dump devices (IEC) | IP/LP bypass downstream piping (EPC) | steam | 2 x 36" + 1 x 28" | 16 bar(a) / 250 degC | start-up / trip |
| IF-15 | Condensate from hotwell | hotwell outlet nozzle | CEP suction piping (EPC) | condensate | 20" CL150 | full vacuum - 3.5 bar(a) / 80 degC | 128.89 kg/s, 26.3 degC |
| IF-16 | Condensate to CPH | HRSG CPH inlet | condensate line (EPC) | condensate | 12" CL300 | 25 bar(a) / 180 degC | 141.37 kg/s |
| IF-17 | BFP suction | HRSG LP drum downcomer outlet nozzle | BFP suction piping (EPC) | feedwater | 16" CL150 | 10 bar(a) / 185 degC | 129.98 kg/s, 158.1 degC |
| IF-18 | HP feedwater | HRSG HP ECO1 inlet | HP feedwater piping (EPC) | feedwater | 10" CL2500 | 235 bar(a) / 200 degC | 100.16 kg/s, 209 bar(a) |
| IF-19 | IP feedwater | HRSG IP ECO inlet | IP feedwater piping (EPC) | feedwater | 6" CL600 | 60 bar(a) / 200 degC | 29.82 kg/s, 46 bar(a) |
| IF-20 | FGH water return | performance gas heater water outlet | return line to condensate (EPC) | feedwater | 4" CL600 | 60 bar(a) / 260 degC | 12.48 kg/s, 75 degC |
| IF-21 | HRSG blowdown | continuous / intermittent blowdown valves outlet | blowdown tanks (EPC) | water | 2" / 3" | 210 bar(a) / 370 degC | 0 in normal operation |
| IF-22 | HRSG drains and vents | drain/vent valves outlet (IEC) | drain collection, flash tanks, silencers (EPC) | water/steam | various | - | start-up |
| IF-23 | Chemical dosing | dosing nozzles on drums/condensate | dosing skids and lines (EPC) | chemicals | 1" | - | - |
| IF-24 | Sampling | sample nozzles with root valves (IEC) | sample lines, coolers, SWAS (EPC) | water/steam | 1/2" | - | - |
| IF-25 | Aqueous ammonia | ammonia injection skid inlet (IEC) | storage, unloading, forwarding pumps (EPC) | NH4OH 24.5 % | 1" | 10 barg / 40 degC | 125 kg/h |
| IF-26 | Flue gas to stack | HRSG outlet transition flange | stack (EPC), CEMS (EPC) | flue gas | D 9.2 m | +/- 50 mbar / 200 degC | 796.7 kg/s, 80.5 degC |
| IF-27 | Circulating water | condenser water box flanges (2 inlets, 2 outlets) | CW pipes (EPC) | seawater | 4 x DN1800 | 4 barg / 40 degC | 36,050 m3/h |
| IF-28 | Closed cooling water | IEC coolers inlet/outlet flanges | CCW system (EPC) | demin water + inhibitor | various | 10 barg / 60 degC | see IEC-ALP-REQ-001 table 5.1 |
| IF-29 | Instrument and service air | IEC skids | compressed air system (EPC) | air | 1" - 2" | 10 barg | see REQ-001 6.1 |
| IF-30 | Nitrogen | HRSG lay-up / generator purge connections | N2 supply (EPC) | N2 | 1" | 10 barg | lay-up |
| IF-31 | Hydrogen / CO2 | GT generator gas control panel inlet | bottle racks and piping (EPC) | H2 / CO2 | 1/2" | 16 barg | 12 Nm3/day H2 |
| IF-32 | Auxiliary steam | gland steam header inlet (IEC) | auxiliary boiler steam (EPC) | steam | 4" | 16 bar(a) / 320 degC | 4.5 t/h at start-up |
| IF-33 | Fire protection | GT enclosure CO2 system (IEC) | fire detection/alarm, transformer deluge, hydrants (EPC) | - | - | - | signals to EPC fire alarm panel |
| IF-34 | GT GSU HV | GT GSU HV bushings | 380 kV connection to GIS (EPC) | electrical | 400 kV | - | 560 MVA |
| IF-35 | ST GSU HV | ST GSU HV bushings | 380 kV connection to GIS (EPC) | electrical | 400 kV | - | 270 MVA |
| IF-36 | UAT supply | IPB tap-off flange (GT and ST IPB) | UAT and MV busduct (EPC) | electrical | 21 kV / 15.75 kV | - | - |
| IF-37 | MV supplies | SFC isolation transformer, IEC MV consumers | 10.5 kV switchgear feeders (EPC) | electrical | 10.5 kV | - | SFC 8.5 MW at start |
| IF-38 | LV supplies | IEC MCCs incoming | 0.4 kV switchgear feeders (EPC) | electrical | 0.4 kV | - | see REQ-001 7.1 |
| IF-39 | DC and UPS | TCS, protection, emergency oil pumps | 220 V DC and 230 V AC UPS (EPC) | electrical | - | - | see REQ-001 7.2 |
| IF-40 | Control system interface | IEC turbine control system (TCS) gateway | plant DCS (EPC) | data | OPC UA + Modbus TCP, redundant; hardwired trips | - | about 2,500 signals |
| IF-41 | Protection interface | generator/GSU protection panels | switchyard protection and TSO SCADA (EPC) | signals | IEC 61850 + hardwired | - | - |
| IF-42 | Earthing | equipment earthing bosses | earthing grid (EPC) | electrical | - | - | - |
| IF-43 | Foundations | anchor bolts, sole plates, load data (IEC) | foundation design and construction (EPC) | civil | - | - | see REQ-001 section 9 |