## Terminal points
IEC-ALP-IF-001 Rev 0 - Terminal points
Tag | Service | IEC side | EPC side | Medium | Size / rating | Design p / T | Operating (SRC)
IF-01 | Natural gas to GT | performance gas heater inlet flange | gas from EPC gas receiving/metering station | natural gas | 12" ASME CL600 RF | 63 barg / 80 degC | 20.67 kg/s, 37.0 barg, 25 degC
IF-02 | LDO to GT | liquid fuel skid inlet flange | LDO forwarding/treatment system | LDO | 6" CL150 | 16 barg / 60 degC | 22.1 kg/s (LDO operation)
IF-03 | Demin water for water injection | water injection skid inlet | demin water storage/pumps | demin water | 4" CL150 | 16 barg / 50 degC | 22.5 kg/s (LDO operation)
IF-04 | Compressor wash water | wash skid inlet | demin water | demin water | 2" CL150 | 10 barg / 50 degC | 5 m3 per wash
IF-05 | HP steam | HRSG HP SH outlet stop valve, weld end | main steam piping (EPC) | steam | 12" (P91) weld end | 210 bar(a) / 610 degC | 100.16 kg/s, 187.0 bar(a), 600 degC
IF-06 | HP steam | ST main stop valve inlet, weld end | main steam piping (EPC) | steam | 12" (P91) weld end | 200 bar(a) / 605 degC | 180.0 bar(a), 597 degC
IF-07 | Cold reheat | HP turbine exhaust, weld end | cold reheat piping (EPC) | steam | 24" (P22/A106) weld end | 52 bar(a) / 420 degC | 40.2 bar(a), 366 degC
IF-08 | Cold reheat | HRSG reheater inlet, weld end | cold reheat piping (EPC) | steam | 24" weld end | 52 bar(a) / 420 degC | 39.4 bar(a), 365 degC
IF-09 | Hot reheat | HRSG reheater outlet stop valve, weld end | hot reheat piping (EPC) | steam | 28" (P91) weld end | 50 bar(a) / 610 degC | 117.50 kg/s, 37.6 bar(a)
IF-10 | Hot reheat | ST IP stop-control valve inlet | hot reheat piping (EPC) | steam | 28" (P91) weld end | 48 bar(a) / 605 degC | 36.0 bar(a), 597 degC
IF-11 | LP steam | HRSG LP SH outlet stop valve | LP steam piping (EPC) | steam | 20" weld end | 10 bar(a) / 330 degC | 11.39 kg/s, 5.40 bar(a)
IF-12 | LP steam | ST LP admission valve inlet | LP steam piping (EPC) | steam | 20" weld end | 8 bar(a) / 330 degC | 4.95 bar(a)
IF-13 | HP / IP / LP bypass valves | valves supplied loose by IEC (incl. desuperheating) | installation in EPC piping, spray water from BFP/CEP (EPC) | steam / water | per valve datasheets | - | start-up / trip
IF-14 | Bypass steam to condenser | condenser neck dump devices (IEC) | IP/LP bypass downstream piping (EPC) | steam | 2 x 36" + 1 x 28" | 16 bar(a) / 250 degC | start-up / trip
IF-15 | Condensate from hotwell | hotwell outlet nozzle | CEP suction piping (EPC) | condensate | 20" CL150 | full vacuum - 3.5 bar(a) / 80 degC | 128.89 kg/s, 26.3 degC
IF-16 | Condensate to CPH | HRSG CPH inlet | condensate line (EPC) | condensate | 12" CL300 | 25 bar(a) / 180 degC | 141.37 kg/s
IF-17 | BFP suction | HRSG LP drum downcomer outlet nozzle | BFP suction piping (EPC) | feedwater | 16" CL150 | 10 bar(a) / 185 degC | 129.98 kg/s, 158.1 degC
IF-18 | HP feedwater | HRSG HP ECO1 inlet | HP feedwater piping (EPC) | feedwater | 10" CL2500 | 235 bar(a) / 200 degC | 100.16 kg/s, 209 bar(a)
IF-19 | IP feedwater | HRSG IP ECO inlet | IP feedwater piping (EPC) | feedwater | 6" CL600 | 60 bar(a) / 200 degC | 29.82 kg/s, 46 bar(a)
IF-20 | FGH water return | performance gas heater water outlet | return line to condensate (EPC) | feedwater | 4" CL600 | 60 bar(a) / 260 degC | 12.48 kg/s, 75 degC
IF-21 | HRSG blowdown | continuous / intermittent blowdown valves outlet | blowdown tanks (EPC) | water | 2" / 3" | 210 bar(a) / 370 degC | 0 in normal operation
IF-22 | HRSG drains and vents | drain/vent valves outlet (IEC) | drain collection, flash tanks, silencers (EPC) | water/steam | various | - | start-up
IF-23 | Chemical dosing | dosing nozzles on drums/condensate | dosing skids and lines (EPC) | chemicals | 1" | - | -
IF-24 | Sampling | sample nozzles with root valves (IEC) | sample lines, coolers, SWAS (EPC) | water/steam | 1/2" | - | -
IF-25 | Aqueous ammonia | ammonia injection skid inlet (IEC) | storage, unloading, forwarding pumps (EPC) | NH4OH 24.5 % | 1" | 10 barg / 40 degC | 125 kg/h
IF-26 | Flue gas to stack | HRSG outlet transition flange | stack (EPC), CEMS (EPC) | flue gas | D 9.2 m | +/- 50 mbar / 200 degC | 796.7 kg/s, 80.5 degC
IF-27 | Circulating water | condenser water box flanges (2 inlets, 2 outlets) | CW pipes (EPC) | seawater | 4 x DN1800 | 4 barg / 40 degC | 36,050 m3/h
IF-28 | Closed cooling water | IEC coolers inlet/outlet flanges | CCW system (EPC) | demin water + inhibitor | various | 10 barg / 60 degC | see IEC-ALP-REQ-001 table 5.1
IF-29 | Instrument and service air | IEC skids | compressed air system (EPC) | air | 1" - 2" | 10 barg | see REQ-001 6.1
IF-30 | Nitrogen | HRSG lay-up / generator purge connections | N2 supply (EPC) | N2 | 1" | 10 barg | lay-up
IF-31 | Hydrogen / CO2 | GT generator gas control panel inlet | bottle racks and piping (EPC) | H2 / CO2 | 1/2" | 16 barg | 12 Nm3/day H2
IF-32 | Auxiliary steam | gland steam header inlet (IEC) | auxiliary boiler steam (EPC) | steam | 4" | 16 bar(a) / 320 degC | 4.5 t/h at start-up
IF-33 | Fire protection | GT enclosure CO2 system (IEC) | fire detection/alarm, transformer deluge, hydrants (EPC) | - | - | - | signals to EPC fire alarm panel
IF-34 | GT GSU HV | GT GSU HV bushings | 380 kV connection to GIS (EPC) | electrical | 400 kV | - | 560 MVA
IF-35 | ST GSU HV | ST GSU HV bushings | 380 kV connection to GIS (EPC) | electrical | 400 kV | - | 270 MVA
IF-36 | UAT supply | IPB tap-off flange (GT and ST IPB) | UAT and MV busduct (EPC) | electrical | 21 kV / 15.75 kV | - | -
IF-37 | MV supplies | SFC isolation transformer, IEC MV consumers | 10.5 kV switchgear feeders (EPC) | electrical | 10.5 kV | - | SFC 8.5 MW at start
IF-38 | LV supplies | IEC MCCs incoming | 0.4 kV switchgear feeders (EPC) | electrical | 0.4 kV | - | see REQ-001 7.1
IF-39 | DC and UPS | TCS, protection, emergency oil pumps | 220 V DC and 230 V AC UPS (EPC) | electrical | - | - | see REQ-001 7.2
IF-40 | Control system interface | IEC turbine control system (TCS) gateway | plant DCS (EPC) | data | OPC UA + Modbus TCP, redundant; hardwired trips | - | about 2,500 signals
IF-41 | Protection interface | generator/GSU protection panels | switchyard protection and TSO SCADA (EPC) | signals | IEC 61850 + hardwired | - | -
IF-42 | Earthing | equipment earthing bosses | earthing grid (EPC) | electrical | - | - | -
IF-43 | Foundations | anchor bolts, sole plates, load data (IEC) | foundation design and construction (EPC) | civil | - | - | see REQ-001 section 9