IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Power Island Thermal Performance Data (Heat Balance)

| Document number | IEC-ALP-PER-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-27 |
| Status | Issued for EPC engineering (reference data) |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-09-27 | signed 2026-09-27 | signed 2026-09-27 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. Purpose and basis

This document gives the expected thermal performance of the IEC power island (1 x IE-9H.02 gas turbine with generator, 1 x IE-HR3 triple-pressure reheat HRSG, 1 x IE-ST3R reheat steam turbine with generator, seawater condenser) for the EPC's plant heat and mass balance. Values are expected values, new and clean, without guarantee margins; IEC's guarantee values to the consortium are given in section 7.

Case SRC-NG-100: Site Reference Conditions per ER-02.03 - ambient 15.0 degC, 70 % RH, 1011.5 mbar; seawater 16.0 degC; base load on natural gas; power factor 0.85 lagging; 50.0 Hz.

Fuel: Owner reference composition ALP-OWN-FUL-001 / ER-03.02. LHV calculated per ISO 6976 from this composition: 47.48 MJ/kg (34.78 MJ/Sm3, 15 degC/15 degC). Heat input = fuel mass flow x this LHV. Fuel gas heated to 215 degC in the IEC performance gas heater with IP feedwater.

GT inlet pressure loss 10 mbar, exhaust back-pressure 36 mbar (HRSG 30 mbar + stack 6 mbar, stack by EPC).

Steam piping between HRSG and steam turbine is by EPC; IEC assumed pressure drops HP 7.0 bar, hot reheat 1.6 bar, cold reheat 0.8 bar, LP 0.45 bar, and temperature drops of 3 K (HP, HRH), 1 K (CRH), 2 K (LP). The EPC shall confirm or IEC will correct the performance.

Boiler feed pumps and condensate pumps are by EPC; IEC assumed BFP discharge 209 bar(a) (HP) / 46 bar(a) (IP), CEP discharge 16 bar(a).

Steam turbine gland leak-offs, valve stem leakages and HRSG blowdown are not shown in this summary heat balance (blowdown zero at design; leak-offs are internal to the ST).

# 2. Summary at SRC-NG-100

| Item | Value | Unit |
| --- | --- | --- |
| GT output at generator terminals | 425.00 | MW |
| GT heat rate (LHV) | 8,314.1 | kJ/kWh |
| GT heat input (LHV) | 981.52 | MW |
| Fuel gas flow | 20.672 kg/s = 101,596 | Sm3/h |
| Compressor inlet air flow | 776.01 | kg/s |
| GT exhaust flow / temperature | 796.68 / 640.0 | kg/s / degC |
| GT generator efficiency | 98.90 | % |
| GT losses other than generator (lube oil, radiation) | 3.80 | MW |
| Performance gas heater duty | 9.46 | MW |
| HRSG heat transferred to water/steam | 500.83 | MW |
| HRSG heat loss (casing, % of gas-side duty) | 0.4 | % |
| Stack temperature | 80.5 | degC |
| ST output at generator terminals | 200.31 | MW |
| ST mechanical / generator efficiency | 99.55 / 98.80 | % |
| Condenser pressure | 34.44 | mbar(a) |
| Condenser duty | 289.96 | MW |
| Circulating water flow (7 K rise) | 10,179 kg/s = 36,050 | m3/h |
| Power island gross output | 625.31 | MW |
| Power island gross heat rate (LHV) | 5,650.8 | kJ/kWh |

Net output and net heat rate depend on the EPC balance-of-plant auxiliary loads and transformer losses; IEC's auxiliary loads are listed in IEC-ALP-REQ-001 section 7.

# 3. Stream data at SRC-NG-100

Node codes: AMB ambient, FGS EPC fuel gas system, FGH IEC performance gas heater, GT gas turbine, HRSG, STK stack (EPC), PIPE steam piping HRSG-ST (EPC), ST steam turbine, COND condenser, CEP condensate pumps (EPC), CMIX condensate/FGH-return junction (EPC), BFP boiler feed pumps (EPC), SEA intake, OUT outfall.

| No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Ambient air to GT compressor inlet | air | AMB | GT | 776.01 | 1.01 | 15.0 | - |
| 2 | Fuel gas at performance gas heater inlet (IEC terminal point) | fuel_gas | FGS | FGH | 20.67 | 38.00 | 25.0 | - |
| 3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 20.67 | 35.50 | 215.0 | - |
| 4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 796.68 | 1.05 | 640.0 | - |
| 5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 796.68 | 1.01 | 80.5 | - |
| 6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 100.16 | 187.00 | 600.0 | - |
| 7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 100.16 | 180.00 | 597.0 | - |
| 8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 100.16 | 40.20 | 366.2 | - |
| 9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 100.16 | 39.40 | 365.2 | - |
| 10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 17.34 | 40.30 | 330.0 | - |
| 11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 117.50 | 37.60 | 600.0 | - |
| 12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 117.50 | 36.00 | 597.0 | - |
| 13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 11.39 | 5.40 | 300.0 | - |
| 14 | LP steam at ST LP admission | steam | PIPE | ST | 11.39 | 4.95 | 298.0 | - |
| 15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 117.50 | 4.95 | 308.8 | - |
| 16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 128.89 | 0.0344 | 26.4 | 2,360.4 |
| 17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 128.89 | 0.0344 | 26.3 | - |
| 18 | Condensate at CEP discharge | water | CEP | CMIX | 128.89 | 16.00 | 26.5 | - |
| 19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 12.48 | 43.00 | 75.0 | - |
| 20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 141.37 | 15.50 | 30.9 | - |
| 21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 129.98 | 5.90 | 158.1 | - |
| 22 | HP feedwater at BFP discharge | water | BFP | HRSG | 100.16 | 209.00 | 161.8 | - |
| 23 | IP feedwater at BFP interstage outlet | water | BFP | HRSG | 29.82 | 46.00 | 158.9 | - |
| 24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 12.48 | 43.30 | 248.0 | - |
| 25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10,179.10 | 2.50 | 16.0 | - |
| 26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10,179.10 | 1.70 | 23.0 | - |

# 4. GT exhaust gas composition at SRC-NG-100 (mol %, wet)

| N2 | O2 | Ar | CO2 | H2O |
| --- | --- | --- | --- | --- |
| 73.85 | 11.12 | 0.88 | 4.47 | 9.67 |

# 5. HRSG temperature profile at SRC-NG-100

| HRSG section (gas flow order) | Gas in degC | Gas out degC | Duty MW |
| --- | --- | --- | --- |
| HPSH / RH | 640.0 | 450.6 | 176.83 |
| HPEVAP | 450.6 | 371.6 | 71.39 |
| HPECO2 | 371.6 | 299.9 | 63.71 |
| IPSH | 299.9 | 295.1 | 4.19 |
| IPEVAP | 295.1 | 261.0 | 29.89 |
| HPECO1 / IPECO | 261.0 | 201.5 | 51.64 |
| LPSH | 201.5 | 197.4 | 3.51 |
| LPEVAP | 197.4 | 166.2 | 26.83 |
| CPH | 166.2 | 80.5 | 72.85 |

Pinch points HP/IP/LP: 8 / 8 / 8 K; approach temperatures at the economiser outlets: 5 / 5 / 5 K. Drum saturation temperatures HP/IP/LP: 363.6 / 253.0 / 158.2 degC. Steam turbine section outputs (shaft): HP 41.68 MW, IP 69.13 MW, LP 92.85 MW; LP exhaust moisture 7.74 %.

# 6. Performance at other ambient conditions and part load (estimates)

Base load on natural gas, seawater temperature as shown, other conditions as SRC. GT from the IE-9H.02 correction curves; the bottoming cycle is re-estimated with the design pinch/approach values. These are preliminary estimates, not off-design ratings of the fixed HRSG and condenser surfaces; rated off-design heat balances follow with the HRSG thermal design (IEC-ALP-DS-104 Rev A).

| Ambient degC | RH % | Seawater degC | GT MW | GT HR kJ/kWh | Exhaust kg/s | Exhaust degC | ST MW | Gross MW | Gross HR kJ/kWh | Condenser mbar | Gas Sm3/h | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| -8.0 | 80 | 6.9 | 470.0 | 8,089 | 823.5 | 634.0 | 210.6 | 680.6 | 5,586 | 19.8 | 109,310 | GT at output limit 470 MW |
| -4.8 | 80 | 8.0 | 470.0 | 8,131 | 832.5 | 635.7 | 213.0 | 683.0 | 5,595 | 21.2 | 109,874 | GT at output limit 470 MW |
| 5.0 | 75 | 11.0 | 452.8 | 8,217 | 829.2 | 634.8 | 209.3 | 662.1 | 5,620 | 25.5 | 106,984 |  |
| 15.0 | 70 | 16.0 | 425.0 | 8,314 | 796.7 | 640.0 | 200.3 | 625.3 | 5,651 | 34.4 | 101,596 |  |
| 25.0 | 55 | 22.0 | 397.2 | 8,411 | 761.8 | 645.2 | 190.0 | 587.2 | 5,689 | 48.7 | 96,053 |  |
| 32.8 | 45 | 24.0 | 372.8 | 8,501 | 729.5 | 649.3 | 182.9 | 555.7 | 5,703 | 54.4 | 91,121 |  |
| 40.0 | 35 | 27.0 | 348.2 | 8,595 | 695.9 | 653.0 | 174.3 | 522.5 | 5,728 | 64.2 | 86,055 |  |

GT output is limited to 470 MW at the generator terminals (generator and shaft limit) below about -1 degC; the GT then runs at part load with the IGV closing.

| GT load % | GT MW | GT HR kJ/kWh | Exhaust kg/s | Exhaust degC | ST MW | Gross MW | Gross HR kJ/kWh |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 100 | 425.0 | 8,314 | 796.7 | 640.0 | 200.3 | 625.3 | 5,651 |
| 80 | 340.0 | 8,746 | 696.5 | 640.0 | 174.8 | 514.8 | 5,776 |
| 60 | 255.0 | 9,436 | 593.1 | 640.0 | 148.5 | 403.5 | 5,963 |
| 50 | 212.5 | 9,894 | 541.0 | 632.0 | 132.4 | 344.9 | 6,096 |
| 40 | 170.0 | 10,600 | 496.9 | 615.0 | 115.7 | 285.7 | 6,307 |

Part load at SRC with the steam cycle at fixed pressure (sliding-pressure operation will be optimised in detailed design; values are conservative estimates).

# 7. IEC guarantees to the consortium (power island)

| Guarantee (SRC-NG-100, new and clean, per ASME PTC 46 / ISO 2314) | Value |
| --- | --- |
| Power island gross output at generator terminals | not less than 614.0 MW |
| Power island gross heat rate (LHV) | not more than 5,745 kJ/kWh |
| GT output at generator terminals | not less than 418.0 MW |
| Condenser pressure at 16.0 degC seawater, 36,050 m3/h | not more than 35.5 mbar(a) |
| IEC auxiliary loads (IEC-ALP-REQ-001 table 7.1, excl. GSU losses) | not more than 2,700 kW |
| NOx / CO at HRSG outlet (15 % O2, dry), 40-100 % GT load, natural gas | 30 / 30 mg/Nm3 |

Degradation is excluded from the values above; recoverable and non-recoverable degradation curves follow in IEC-ALP-PER-002.