IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Power Island Interface Requirements to the EPC (utilities, chemistry, electrical, civil, transport)

| Document number | IEC-ALP-REQ-001 |
| --- | --- |
| Revision | 0 |
| Date | 2026-09-27 |
| Status | Issued for EPC engineering (reference data) |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-09-27 | signed 2026-09-27 | signed 2026-09-27 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. Purpose

Requirements of IEC to the EPC for the design of the balance of plant around the power island. They complement the Owner's Employer's Requirements (Appendix A of ALP-EPC-001); where the Owner's requirement is stricter it prevails. Section 12 lists IEC's exceptions and clarifications to the Employer's Requirements.

# 2. Fuel gas at IF-01

Pressure 36.5 barg minimum at base load, 41.0 barg maximum, rate of change <= 0.7 bar/s; at 36.5 barg IEC requires 45 barg at TP-G1 less the EPC station losses (EPC to confirm about 4 bar).

Temperature 5 - 40 degC and >= 28 K superheat above the hydrocarbon and water dew points at all loads.

Final filtration 3 um absolute (beta 200) with coalescing filter-separator (EPC), no free liquids.

Trace metals: Na + K <= 0.02 mg/Sm3 equivalent, V <= 0.01, Pb <= 0.02, Ca <= 0.02 mg/Sm3 at IF-01; H2S + COS <= 5 mg/Sm3; total sulphur <= 30 mg S/Sm3.

Gas chromatograph signal (LHV, Wobbe index, H2) to the TCS for combustion tuning (update every <= 4 min).

# 3. LDO and water injection

LDO at IF-02 per ER-03.07 (GT inlet limits) after EPC treatment; 3.0 - 6.0 barg; 10 - 45 degC.

Demin water for water injection at IF-03: conductivity <= 0.2 uS/cm, Na+K <= 0.02 mg/kg, silica <= 0.02 mg/kg; 22.5 kg/s at base load on LDO.

# 4. Water/steam chemistry (IAPWS TGD, VGB-S-010)

| Parameter | Feedwater | HP steam | Unit |
| --- | --- | --- | --- |
| Cation conductivity (25 degC) | <= 0.2 | <= 0.2 | uS/cm |
| Sodium | <= 3 | <= 2 | ug/kg |
| Silica | <= 10 | <= 10 | ug/kg |
| Dissolved oxygen | <= 20 (AVT(O)) | - | ug/kg |
| pH (ammonia) | 9.4 - 9.8 | - | - |
| Iron / copper | <= 5 / <= 2 | - | ug/kg |

# 5. Closed cooling water demand

| Consumer | Duty kW | Flow m3/h | Max. supply temperature degC |
| --- | --- | --- | --- |
| GT lube oil coolers | 1,600 | 140 | 38 |
| GT generator H2 coolers and stator water coolers | 4,300 | 520 | 38 |
| ST lube oil coolers | 850 | 75 | 38 |
| ST generator TEWAC coolers | 2,200 | 260 | 36 |
| SFC, excitation cubicles, vacuum pump seal water | 450 | 60 | 38 |
| Total | 9,400 | 1,055 |  |

# 6. Utilities

| Utility | Requirement |
| --- | --- |
| Instrument air | dew point -40 degC at 7 barg, 350 Nm3/h continuous (valves, purge, pulse cleaning of filter house) |
| Service air | 150 Nm3/h intermittent |
| Nitrogen | HRSG and generator purge/lay-up: 3,000 Nm3 per event, 99.9 % |
| Hydrogen / CO2 | H2 99.9 %, 12 Nm3/day make-up; CO2 150 Nm3 per purge |
| Auxiliary steam | 4.5 t/h at 10 bar(a), 250 - 300 degC for gland sealing at start-up; HRSG sparging 3 t/h optional |

# 7. Electrical

| Consumer (IEC scope) | kW at base load, SRC |
| --- | --- |
| GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | 1,180 |
| GT generator auxiliaries (seal oil, stator water, excitation) | 420 |
| ST auxiliaries (lube oil, EHC, gland steam exhausters) | 380 |
| ST generator auxiliaries (excitation, TEWAC) | 260 |
| HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | 210 |
| Condenser vacuum pump (1 running) | 75 |
| Turbine control system and UPS load | 60 |
| Total IEC auxiliaries | 2,585 |
| GT GSU losses at SRC load | 1,110 |
| ST GSU losses at SRC load | 580 |

Largest IEC MV consumer: SFC 8.5 MW at 10.5 kV during start-up (30 min). DC: 220 V DC emergency oil pumps (GT 37 kW, ST 45 kW, 3 h autonomy). UPS 230 V AC: 45 kVA for the TCS.

# 8. Instrumentation and control

IEC TCS (IE-Control T3) controls and protects GT, ST, generators and the HRSG safety functions; it is a stand-alone system connected to the plant DCS through a redundant OPC UA gateway (Modbus TCP back-up) with hardwired trips and permissives.

Operator control of the power island from the DCS operator stations through the gateway (TCS HMI screens are also available on dedicated IEC stations in the central control room).

Time synchronisation GPS/PTP by EPC; cybersecurity zone and conduit design per IEC 62443-3-2 by EPC with IEC input.

# 9. Foundations and loads

| Equipment | Static load (t) | Dynamic / design data |
| --- | --- | --- |
| GT + generator train (common table-top or block foundation) | 1,050 | unbalance and short-circuit torque (4.8 x rated), natural frequencies +/- 20 % from 50 Hz |
| ST + generator (spring-mounted table-top) | 980 | same criteria; spring elements by EPC |
| HRSG (steel structure base plates) | 7,800 operating | wind 30 m/s, seismic PGA 0.45 g (TBDY 2018) |
| Condenser | 1,650 operating / 2,300 flooded | side-exhaust; expansion joint to ST by IEC |
| GT GSU / ST GSU | 395 / 245 | oil pits and fire walls by EPC |

# 10. Transport and erection

| Piece | Weight (t) | Dimensions (m) | Route |
| --- | --- | --- | --- |
| GT core engine | 405 | 13.2 x 5.9 x 5.6 | barge to TP-M1, SPMT to foundation |
| GT generator stator | 340 | 10.8 x 4.6 x 4.9 | barge, SPMT, jacking/skidding |
| GT GSU | 268 | 11.2 x 4.1 x 4.6 | barge, SPMT |
| HRSG HP evaporator module | 185 | 24.0 x 3.6 x 26.5 | barge, SPMT, heavy crane (by EPC) |
| ST generator stator | 185 | 8.6 x 4.1 x 4.2 | barge, SPMT, jacking |
| ST GSU | 168 | 9.4 x 3.8 x 4.3 | barge, SPMT |
| HRSG HP drum | 96 | 14.0 x 1.9 | barge or road (under 120 t) |

All pieces above 120 t exceed the road limit (ALP-OWN-GEN-001): the barge landing TP-M1 and the haul road shall take 480 t gross (SPMT) with ground bearing to be verified by the EPC.

# 11. Maintenance

GT hall crane: 120 t main hook (GT rotor 112 t), 20 t auxiliary; ST hall crane: 100 t (IP/LP rotor 86 t).

Laydown for GT major inspection: 900 m2 next to the GT, rated 10 t/m2.

# 12. IEC exceptions and clarifications to the Employer's Requirements

| No | Requirement | IEC position |
| --- | --- | --- |
| E-01 | ER-05.02 evaporative cooler provision | space provision only; cooler, water supply and drain not included |
| E-02 | SC-013 TCS 'integrated in' the plant DCS | stand-alone IEC TCS with OPC UA gateway to the EPC DCS (IEC standard, proven on the fleet) |
| E-03 | ER-07.03 automatic ball tube cleaning | not in IEC scope (EPC with the CW system); water boxes prepared |
| E-04 | ER-05.07 HGP >= 25,000 EOH | complies with IEC's EOH formula (starts count 20 EOH each, see DS-101 5) |
| E-05 | Main steam, reheat and LP steam piping | by EPC (not an IEC item in SC-006 to SC-014) |
| E-06 | H2/CO2 supply for the GT generator | by EPC |
| E-07 | ER-04.09 house load operation 60 min | complies for the GT; ST follows on bypass operation |
| E-08 | Guarantees | IEC guarantees are gross values of the power island (PER-001 section 7); net plant guarantees to the Owner remain with the consortium |