## Auxiliary loads
IEC-ALP-REQ-001 Rev 0 - Auxiliary loads
Consumer (IEC scope) | kW at base load, SRC
GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | 1180
GT generator auxiliaries (seal oil, stator water, excitation) | 420
ST auxiliaries (lube oil, EHC, gland steam exhausters) | 380
ST generator auxiliaries (excitation, TEWAC) | 260
HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | 210
Condenser vacuum pump (1 running) | 75
Turbine control system and UPS load | 60
Total IEC auxiliaries | 2585
GT GSU losses at SRC load | 1110
ST GSU losses at SRC load | 580

## Exceptions
IEC-ALP-REQ-001 Rev 0 - Exceptions
No | Requirement | IEC position
E-01 | ER-05.02 evaporative cooler provision | space provision only; cooler, water supply and drain not included
E-02 | SC-013 TCS 'integrated in' the plant DCS | stand-alone IEC TCS with OPC UA gateway to the EPC DCS (IEC standard, proven on the fleet)
E-03 | ER-07.03 automatic ball tube cleaning | not in IEC scope (EPC with the CW system); water boxes prepared
E-04 | ER-05.07 HGP >= 25,000 EOH | complies with IEC's EOH formula (starts count 20 EOH each, see DS-101 5)
E-05 | Main steam, reheat and LP steam piping | by EPC (not an IEC item in SC-006 to SC-014)
E-06 | H2/CO2 supply for the GT generator | by EPC
E-07 | ER-04.09 house load operation 60 min | complies for the GT; ST follows on bypass operation
E-08 | Guarantees | IEC guarantees are gross values of the power island (PER-001 section 7); net plant guarantees to the Owner remain with the consortium