# Alpilla 600 MW Combined Cycle Power Plant
KKS identification manual (project key list and tagging rules)

| Document number | ALP-EPC-00000-GE-PRC-0001 |
| --- | --- |
| Revision | draft - not yet issued (next issue: IFR rev A) |
| Originator | Istanbul EPC |
| Review class | approval (Basic Design Package) |
| Planned issue (workflow timeline) | IFR 2027-02-02, IFA 2027-03-09, IFC 2027-03-16 |
| Basis | requirement:ER-01.06 |

# 1. Purpose, scope and basis

This manual sets the plant identification of the project: systems, equipment, components, structures and the KKS part of every document number. It applies to the consortium members (Istanbul EPC, Imaginary Electric), their subsuppliers and subcontractors, for engineering, the 3D model, the engineering database, procurement, construction (AWP), commissioning and handover.

ER-01.06: All systems, equipment, instruments, cables and documents shall be identified according to KKS (VGB-B 105/106). The tag data shall be classified according to the AVEVA class library adopted by the Owner and delivered through the Owner's engineering database.

The identification follows VGB-S-811 (KKS) with the project key list of section 4. Agreement:

TQ-035 (closed, answered 2026-09-28 by Owner): (1) Accepted: the consortium numbering is the project numbering under ER-17.01; the Owner's EDMS will use it unchanged. (2) The KKS key list is approved for engineering. The Owner's Engineer verifies each key title against the VGB-S-811 key catalogue with the KKS manual review; until then keys stay flagged 'not verified'. (3) MDL accepted as baseline for the Basic Design Package. Review classes accepted with one change: logic diagrams (LOG) incl. cause and effect are safety relevant and are for approval. The MDL is updated monthly with the progress report. (4) AWP definitions accepted. The Owner requires every CWP to be released for construction only when its EWP is complete (all IFC) and its PWP materials are on site or have a confirmed delivery before the planned installation.

TQ-IEC-023 (closed, answered 2026-09-28 by Imaginary Electric): (1) Confirmed. IEC tags the power island with the project KKS to component level (B), systems and equipment units per the project key list; IEC part numbers are kept as vendor attributes below component level. IEC checks the key titles of its main groups against its VGB-S-811 licence copy and reports deviations with the KKS manual review (IFR). (2) Confirmed: project number primary, IEC number as vendor reference on the title block. (3) Confirmed: the VDRL dates in the MDL are the IEC commitment. (4) Confirmed with an improvement: generator shop tests are brought forward; the GT generators leave the works in week 49 together with the GT (sea transport 4 weeks), on site 2027-11-08. The ST generator follows the ST train (no change).

Decision: KKS per VGB-S-811 with the project key list (unit 0 common, 1 GT+HRSG, 2 ST); document numbers ALP-<ORG>-<KKS system|00000>-<DISC>-<TYPE>-<NNNN>; IEC 61355 class per document type; supplier numbers as vendor reference only. (DEC-EPCE-0005, agreed, OWNER / IEPC / IEC)

# 2. Code structure

Codes are written without separators in the database and on documents (e.g. 10MBA10AA001). Data character types: A = letter, N = digit.

| Level | Breakdown | Format | Meaning | Example |
| --- | --- | --- | --- | --- |
| 0 | G | N | Plant unit (project numbering, table below) | 1 |
| 1 | F0 | N | System prefix number (0 on this project) | 0 |
| 1 | F1 F2 F3 | AAA | Function / system key (key list, section 4.1); U = structures | MBA |
| 1 | FN FN | NN | System number: 10, 20, ... parallel trains; units 11, 12 ... subdivisions | 10 |
| 2 | A1 A2 | AA | Equipment unit key (section 4.2) | AP |
| 2 | AN AN AN | NNN | Equipment unit number: 001, 002 ... in flow direction | 001 |
| 3 | B1 B2 | AA | Component key (section 4.3) | KP |
| 3 | BN BN | NN | Component number | 01 |

| Unit (G) | Plant unit |
| --- | --- |
| 0 | common / balance of plant |
| 1 | GT + HRSG island |
| 2 | ST island |

A system record is identified by G F0 F1F2F3 (e.g. 10MBA) or its group G F0 F1F2 (e.g. 10MB); the system number FN is part of equipment tags only. Examples from the plant asset register:

| Tag | Breakdown |
| --- | --- |
| 00EGA10AP001 | unit 0 (common / balance of plant); system 00EGA10: Liquid fuel unloading; equipment unit AP001: Pump units - LDO unloading pump A |
| 00EGA10AP002 | unit 0 (common / balance of plant); system 00EGA10: Liquid fuel unloading; equipment unit AP002: Pump units - LDO unloading pump B |
| 00EGA10AP003 | unit 0 (common / balance of plant); system 00EGA10: Liquid fuel unloading; equipment unit AP003: Pump units - LDO unloading pump C |
| 00ACA10 | unit 0 (common / balance of plant); system 00ACA10: 380 kV switchgear (GIS) - 380 kV GIS, double busbar, 6 bays |
| 00BBA10 | unit 0 (common / balance of plant); system 00BBA10: MV switchgear 10.5 kV, normal supply - MV switchgear 10.5 kV, section A |
| 00EGA10AP001KP01 | unit 0 (common / balance of plant); system 00EGA10: Liquid fuel unloading; equipment unit AP001: Pump units; component KP01: Pump (hydraulic part) - component level (illustration) |

# 3. Tagging rules

Every system, item of equipment, instrument, electrical consumer, cable and structure receives a KKS code before it appears on a document; the code is created in the database first (engine CLI) and never typed on a drawing without a record.

Unit 0 is used for common / balance-of-plant systems, 1 for the GT + HRSG island, 2 for the ST island; the unit of a system follows the train it serves, not its location.

System numbers FN: 10 for the first train of a system, 20, 30 ... for parallel trains; 11, 12 ... for subdivisions of train 10. Equipment unit numbers AN: 001, 002 ... in flow direction; parallel units in the same system are numbered consecutively (e.g. pumps AP001 / AP002 for 2 x 100 %).

Components (level B, e.g. motors KP / MA) carry the tag of their equipment unit plus B1B2 BN BN.

Structures and buildings use the U function keys (section 4.1) with unit and system number, e.g. 10UMA.

Measuring circuits and electrical equipment units use the A-keys of section 4.2; instrument tags follow the same level-2 structure (e.g. 10LAB10CP001).

Supplier-internal part numbers are kept as vendor attributes below component level and never replace the KKS code (TQ-IEC-023).

A code is never reused for a different item; deleted items keep their code void in the change log.

Every tagged record carries its AVEVA class (ER-01.06) so the tag data can be exported to the Owner's engineering database (engine aveva_export).

# 4. Project key list

128 keys. 'Verified' means the key title has been checked against the licensed VGB-S-811 key catalogue by the Owner's Engineer (TQ-035); the key list itself is agreed for use.

## 4.1 Function keys (F1F2F3)

| Key | Main group | Title | Status | Verified | Agreed in |
| --- | --- | --- | --- | --- | --- |
| ACA | Grid and distribution systems | 380 kV switchgear (GIS) | agreed | no | TQ-035 |
| BAA | Power transmission and auxiliary power supply | Generator leads (isolated phase busduct) | agreed | no | TQ-035 |
| BAC | Power transmission and auxiliary power supply | Generator circuit breaker | agreed | no | TQ-035 |
| BAT | Power transmission and auxiliary power supply | Generator step-up transformer | agreed | no | TQ-035 |
| BBA | Power transmission and auxiliary power supply | MV switchgear 10.5 kV, normal supply | agreed | no | TQ-035 |
| BBT | Power transmission and auxiliary power supply | Unit auxiliary transformer | agreed | no | TQ-035 |
| BFA | Power transmission and auxiliary power supply | LV main switchgear 0.4 kV, normal supply | agreed | no | TQ-035 |
| BFT | Power transmission and auxiliary power supply | LV transformers | agreed | no | TQ-035 |
| BLA | Power transmission and auxiliary power supply | Lighting and small power | agreed | no | TQ-035 |
| BMA | Power transmission and auxiliary power supply | LV switchgear, emergency supply | agreed | no | TQ-035 |
| BRA | Power transmission and auxiliary power supply | UPS (uninterruptible AC) | agreed | no | TQ-035 |
| BTA | Power transmission and auxiliary power supply | Battery systems and DC distribution 220 V | agreed | no | TQ-035 |
| BXA | Power transmission and auxiliary power supply | Earthing and lightning protection | agreed | no | TQ-035 |
| CJA | Instrumentation and control | Plant distributed control system | agreed | no | TQ-035 |
| CJG | Instrumentation and control | Safety instrumented systems | agreed | no | TQ-035 |
| CKA | Instrumentation and control | Plant information, historian, performance monitoring, operator training simulator | agreed | no | TQ-035 |
| CQA | Instrumentation and control | Continuous emission monitoring | agreed | no | TQ-035 |
| CYA | Instrumentation and control | Communication, CCTV, access control and security | agreed | no | TQ-035 |
| EGA | Conventional fuel supply and residues disposal | Liquid fuel unloading | agreed | no | TQ-035 |
| EGB | Conventional fuel supply and residues disposal | Liquid fuel storage | agreed | no | TQ-035 |
| EGC | Conventional fuel supply and residues disposal | Liquid fuel forwarding and treatment | agreed | no | TQ-035 |
| EKA | Conventional fuel supply and residues disposal | Gas receiving, filtration and fiscal metering | agreed | no | TQ-035 |
| EKC | Conventional fuel supply and residues disposal | Fuel gas distribution to consumers | agreed | no | TQ-035 |
| GBA | Water supply and disposal | Seawater reverse osmosis (desalination) | agreed | no | TQ-035 |
| GCA | Water supply and disposal | Demineralisation | agreed | no | TQ-035 |
| GHA | Water supply and disposal | Demineralised water storage and distribution | agreed | no | TQ-035 |
| GKA | Water supply and disposal | Potable water supply | agreed | no | TQ-035 |
| GMA | Water supply and disposal | Process drains and waste water collection | agreed | no | TQ-035 |
| GNA | Water supply and disposal | Waste water treatment | agreed | no | TQ-035 |
| GQA | Water supply and disposal | Storm water drainage | agreed | no | TQ-035 |
| GUA | Water supply and disposal | Sanitary waste water treatment | agreed | no | TQ-035 |
| HAA | Conventional heat generation | HRSG pressure system (package) | agreed | no | TQ-035 |
| HAN | Conventional heat generation | HRSG blowdown and drains | agreed | no | TQ-035 |
| HNA | Conventional heat generation | Flue gas ducting | agreed | no | TQ-035 |
| HNE | Conventional heat generation | Stack | agreed | no | TQ-035 |
| HSA | Conventional heat generation | Selective catalytic reduction (SCR) | agreed | no | TQ-035 |
| HSB | Conventional heat generation | Ammonia storage and supply | agreed | no | TQ-035 |
| LAB | Steam, water, gas cycles | Feedwater piping | agreed | no | TQ-035 |
| LAC | Steam, water, gas cycles | Boiler feed pumps | agreed | no | TQ-035 |
| LAE | Steam, water, gas cycles | HP attemperation spray water | agreed | no | TQ-035 |
| LAF | Steam, water, gas cycles | Reheat attemperation spray water | agreed | no | TQ-035 |
| LBA | Steam, water, gas cycles | Main steam piping | agreed | no | TQ-035 |
| LBB | Steam, water, gas cycles | Hot reheat piping | agreed | no | TQ-035 |
| LBC | Steam, water, gas cycles | Cold reheat piping | agreed | no | TQ-035 |
| LBD | Steam, water, gas cycles | LP steam piping | agreed | no | TQ-035 |
| LBG | Steam, water, gas cycles | Auxiliary steam | agreed | no | TQ-035 |
| LCA | Steam, water, gas cycles | Main condensate piping | agreed | no | TQ-035 |
| LCB | Steam, water, gas cycles | Condensate extraction pumps | agreed | no | TQ-035 |
| LDA | Steam, water, gas cycles | Condensate polishing | agreed | no | TQ-035 |
| MAA | Main machine sets | HP turbine | agreed | no | TQ-035 |
| MAB | Main machine sets | IP/LP turbine | agreed | no | TQ-035 |
| MAG | Main machine sets | Condenser | agreed | no | TQ-035 |
| MAJ | Main machine sets | Condenser vacuum system | agreed | no | TQ-035 |
| MAN | Main machine sets | Turbine bypass stations | agreed | no | TQ-035 |
| MAV | Main machine sets | ST lube oil system | agreed | no | TQ-035 |
| MAW | Main machine sets | Gland steam system | agreed | no | TQ-035 |
| MAX | Main machine sets | ST control fluid system | agreed | no | TQ-035 |
| MAY | Main machine sets | ST control and protection | agreed | no | TQ-035 |
| MBA | Main machine sets | Gas turbine (compressor, combustor, turbine) | agreed | no | TQ-035 |
| MBL | Main machine sets | GT inlet air system | agreed | no | TQ-035 |
| MBN | Main machine sets | GT liquid fuel and water injection | agreed | no | TQ-035 |
| MBP | Main machine sets | GT fuel gas system incl. performance heater | agreed | no | TQ-035 |
| MBU | Main machine sets | GT compressor washing | agreed | no | TQ-035 |
| MBV | Main machine sets | GT lube oil system | agreed | no | TQ-035 |
| MBY | Main machine sets | GT control and protection (TCS) | agreed | no | TQ-035 |
| MKA | Main machine sets | Generator | agreed | no | TQ-035 |
| MKC | Main machine sets | Excitation and static frequency converter | agreed | no | TQ-035 |
| MKG | Main machine sets | Generator gas system (H2/CO2) | agreed | no | TQ-035 |
| PAA | Cooling water systems | CW intake, screens and outfall | agreed | no | TQ-035 |
| PAB | Cooling water systems | CW piping | agreed | no | TQ-035 |
| PAC | Cooling water systems | CW pumps | agreed | no | TQ-035 |
| PAH | Cooling water systems | Condenser tube cleaning | agreed | no | TQ-035 |
| PBA | Cooling water systems | Electro-chlorination | agreed | no | TQ-035 |
| PGA | Cooling water systems | Closed cooling water | agreed | no | TQ-035 |
| QCA | Auxiliary systems | Chemical dosing | agreed | no | TQ-035 |
| QEA | Auxiliary systems | Compressed air (service and instrument) | agreed | no | TQ-035 |
| QHA | Auxiliary systems | Auxiliary boiler | agreed | no | TQ-035 |
| QJA | Auxiliary systems | Nitrogen supply | agreed | no | TQ-035 |
| QJB | Auxiliary systems | Hydrogen and CO2 supply | agreed | no | TQ-035 |
| QUA | Auxiliary systems | Sampling and steam/water analysis | agreed | no | TQ-035 |
| SAA | Ancillary systems | Heating, ventilation and air conditioning | agreed | no | TQ-035 |
| SGA | Ancillary systems | Fire water system | agreed | no | TQ-035 |
| SGC | Ancillary systems | Deluge, spray and foam systems | agreed | no | TQ-035 |
| SGY | Ancillary systems | Fire detection and alarm | agreed | no | TQ-035 |
| SMA | Ancillary systems | Cranes and hoists | agreed | no | TQ-035 |
| UAC | Structures | GIS building | agreed | no | TQ-035 |
| UBA | Structures | Electrical building | agreed | no | TQ-035 |
| UBF | Structures | Transformer bays | agreed | no | TQ-035 |
| UCA | Structures | Control building | agreed | no | TQ-035 |
| UEG | Structures | Liquid fuel tank farm structures | agreed | no | TQ-035 |
| UEK | Structures | Gas station structures | agreed | no | TQ-035 |
| UGA | Structures | Water treatment building | agreed | no | TQ-035 |
| UHA | Structures | HRSG foundations and structures | agreed | no | TQ-035 |
| UHN | Structures | Stack foundation | agreed | no | TQ-035 |
| UMA | Structures | Gas turbine hall | agreed | no | TQ-035 |
| UMB | Structures | Steam turbine hall | agreed | no | TQ-035 |
| UPA | Structures | CW intake and outfall structures (marine) | agreed | no | TQ-035 |
| UPC | Structures | CW pump house | agreed | no | TQ-035 |
| UQA | Structures | Utility building (compressors, auxiliary boiler) | agreed | no | TQ-035 |
| USA | Structures | Workshop and warehouse | agreed | no | TQ-035 |
| UYA | Structures | Administration building | agreed | no | TQ-035 |
| UZA | Structures | Roads and paving | agreed | no | TQ-035 |
| UZB | Structures | Fencing and gates | agreed | no | TQ-035 |
| UZC | Structures | Site drainage and culverts | agreed | no | TQ-035 |
| UZD | structures | Pipe racks and pipe sleepers | agreed | no | TQ-036 |
| UZE | structures | Cable trenches and duct banks | agreed | no | TQ-036 |
| UZF | structures | Temporary barge landing (removed after heavy transport) | agreed | no | TQ-036 |
| XJA | Heavy machinery (not main machine sets) | Emergency diesel generator | agreed | no | TQ-035 |

## 4.2 Equipment unit keys (A1A2)

| Key | Main group | Title | Status | Verified | Agreed in |
| --- | --- | --- | --- | --- | --- |
| AA | equipment unit | Valves, dampers | agreed | no | TQ-035 |
| AC | equipment unit | Heat exchangers | agreed | no | TQ-035 |
| AN | equipment unit | Compressor units, fans | agreed | no | TQ-035 |
| AP | equipment unit | Pump units | agreed | no | TQ-035 |
| AT | equipment unit | Cleaning, drying, filtering units | agreed | no | TQ-035 |
| BB | equipment unit | Storage equipment (vessels, tanks) | agreed | no | TQ-035 |
| BN | equipment unit | Jet pumps, ejectors | agreed | no | TQ-035 |
| BP | equipment unit | Flow restrictors, orifices | agreed | no | TQ-035 |
| BR | equipment unit | Piping, ducting | agreed | no | TQ-035 |
| BS | equipment unit | Silencers | agreed | no | TQ-035 |
| CF | equipment unit | Direct measuring circuit - flow | agreed | no | TQ-035 |
| CL | equipment unit | Direct measuring circuit - level | agreed | no | TQ-035 |
| CP | equipment unit | Direct measuring circuit - pressure | agreed | no | TQ-035 |
| CQ | equipment unit | Direct measuring circuit - analysis | agreed | no | TQ-035 |
| CS | equipment unit | Direct measuring circuit - speed | agreed | no | TQ-035 |
| CT | equipment unit | Direct measuring circuit - temperature | agreed | no | TQ-035 |
| CY | equipment unit | Direct measuring circuit - vibration | agreed | no | TQ-035 |

## 4.3 Component keys (B1B2)

| Key | Main group | Title | Status | Verified | Agreed in |
| --- | --- | --- | --- | --- | --- |
| KA | component | Valve body / gate and globe valve component | agreed | no | TQ-035 |
| KP | component | Pump (hydraulic part) | agreed | no | TQ-035 |
| MA | component | Electric motor | agreed | no | TQ-035 |

# 5. System register

119 systems and groups. Scope = party responsible for the design of the system.

| Code | Title | Category | Scope | Parent | AVEVA class |
| --- | --- | --- | --- | --- | --- |
| 00ACA | 380 kV GIS switchyard | electrical hv | IEPC | - | System |
| 00BBA | MV switchgear 10.5 kV | electrical mv lv | IEPC | - | System |
| 00BFA | LV switchgear 0.4 kV | electrical mv lv | IEPC | - | System |
| 00BFT | LV transformers | electrical mv lv | IEPC | - | System |
| 00BLA | Lighting and small power | electrical mv lv | IEPC | - | System |
| 00BMA | Emergency LV switchgear | electrical mv lv | IEPC | - | System |
| 00BRA | UPS | electrical mv lv | IEPC | - | System |
| 00BTA | Batteries and DC 220 V | electrical mv lv | IEPC | - | System |
| 00BXA | Earthing and lightning protection | common | IEPC | - | System |
| 00CJA | Plant DCS | i and c | IEPC | - | System |
| 00CJG | Safety instrumented systems (BOP) | i and c | IEPC | - | System |
| 00CKA | Historian, performance monitoring and operator training simulator | i and c | IEPC | - | System |
| 00CQA | Continuous emission monitoring | i and c | IEPC | - | System |
| 00CYA | Telecom, CCTV, access control, security | i and c | IEPC | - | System |
| 00EGA | LDO unloading | fuel gas | IEPC | - | System |
| 00EGB | LDO storage | fuel gas | IEPC | - | System |
| 00EGC | LDO forwarding and treatment | fuel gas | IEPC | - | System |
| 00EKA | Gas receiving, filtration and fiscal metering station | fuel gas | IEPC | - | System |
| 00EKC | Fuel gas distribution to GT and auxiliary boiler | fuel gas | IEPC | - | System |
| 00GBA | Seawater reverse osmosis | water treatment | IEPC | - | System |
| 00GCA | Demineralisation | water treatment | IEPC | - | System |
| 00GHA | Demineralised water storage and distribution | water treatment | IEPC | - | System |
| 00GKA | Potable water | water treatment | IEPC | - | System |
| 00GMA | Process drains and waste water collection | water treatment | IEPC | - | System |
| 00GNA | Waste water treatment | water treatment | IEPC | - | System |
| 00GQA | Storm water drainage | civil structural | IEPC | - | System |
| 00GUA | Sanitary waste water treatment | water treatment | IEPC | - | System |
| 00LBG | Auxiliary steam | water steam cycle | IEPC | - | System |
| 00LDA | Condensate polishing | water treatment | IEPC | - | System |
| 00PAA | CW intake, screens and outfall | cooling | IEPC | - | System |
| 00PAB | CW piping | cooling | IEPC | - | System |
| 00PAC | CW pumps | cooling | IEPC | - | System |
| 00PAH | Condenser tube cleaning | cooling | IEPC | - | System |
| 00PBA | Electro-chlorination | cooling | IEPC | - | System |
| 00PGA | Closed cooling water | cooling | IEPC | - | System |
| 00QCA | Chemical dosing | auxiliary mechanical | IEPC | - | System |
| 00QEA | Compressed air | auxiliary mechanical | IEPC | - | System |
| 00QHA | Auxiliary boiler | auxiliary mechanical | IEPC | - | System |
| 00QJA | Nitrogen supply | auxiliary mechanical | IEPC | - | System |
| 00QJB | Hydrogen and CO2 supply | auxiliary mechanical | IEPC | - | System |
| 00QUA | Sampling and SWAS | auxiliary mechanical | IEPC | - | System |
| 00SAA | HVAC | hvac | IEPC | - | System |
| 00SGA | Fire water system | fire protection | IEPC | - | System |
| 00SGC | Deluge, spray and foam systems | fire protection | IEPC | - | System |
| 00SGY | Fire detection and alarm | i and c | IEPC | - | System |
| 00SMA | Cranes and hoists | other | IEPC | - | System |
| 00UAC | GIS building | civil structural | IEPC | - | System |
| 00UBA | Electrical building | civil structural | IEPC | - | System |
| 00UBF | Transformer bays | civil structural | IEPC | - | System |
| 00UCA | Control building | civil structural | IEPC | - | System |
| 00UEG | LDO tank farm structures | civil structural | IEPC | - | System |
| 00UEK | Gas station structures | civil structural | IEPC | - | System |
| 00UGA | Water treatment building and basins | civil structural | IEPC | - | System |
| 00UPA | CW intake and outfall marine structures | civil structural | IEPC | - | System |
| 00UPC | CW pump house | civil structural | IEPC | - | System |
| 00UQA | Utility building | civil structural | IEPC | - | System |
| 00USA | Workshop and warehouse | civil structural | IEPC | - | System |
| 00UYA | Administration building | civil structural | IEPC | - | System |
| 00UZA | Roads and paving | civil structural | IEPC | - | System |
| 00UZB | Fencing and gates | civil structural | IEPC | - | System |
| 00UZC | Site drainage and culverts | civil structural | IEPC | - | System |
| 00UZD | Pipe racks and pipe sleepers | civil structural | IEPC | - | System |
| 00UZE | Cable trenches and duct banks | civil structural | IEPC | - | System |
| 00UZF | Temporary barge landing | civil structural | IEPC | - | System |
| 00XJA | Emergency diesel generator | electrical mv lv | IEPC | - | System |
| 10BAA | GT generator busduct | electrical hv | IEC | - | System |
| 10BAC | GT generator circuit breaker | electrical hv | IEC | - | System |
| 10BAT | GT generator step-up transformer | electrical hv | IEC | - | System |
| 10BBT | GT unit auxiliary transformer | electrical mv lv | IEPC | - | System |
| 10HA | HRSG pressure system | hrsg | IEC | - | System |
| 10HAA | HRSG pressure system | hrsg | IEC | 10HA | System |
| 10HAN | HRSG blowdown and drains (EPC tanks and headers) | water steam cycle | IEPC | 10HA | System |
| 10HNA | HRSG flue gas ducting | hrsg | IEC | 10HA | System |
| 10HNE | Stack 65 m with CEMS platform and silencer | hrsg | IEPC | - | System |
| 10HSA | SCR catalyst and ammonia injection | hrsg | IEC | - | System |
| 10HSB | Ammonia storage and supply | auxiliary mechanical | IEPC | - | System |
| 10LAB | Feedwater piping | condensate feedwater | IEPC | - | System |
| 10LAC | Boiler feed pumps | condensate feedwater | IEPC | - | System |
| 10LAE | HP attemperation spray water | condensate feedwater | IEPC | - | System |
| 10LAF | Reheat attemperation spray water | condensate feedwater | IEPC | - | System |
| 10LBA | Main steam piping | water steam cycle | IEPC | - | System |
| 10LBB | Hot reheat piping | water steam cycle | IEPC | - | System |
| 10LBC | Cold reheat piping | water steam cycle | IEPC | - | System |
| 10LBD | LP steam piping | water steam cycle | IEPC | - | System |
| 10MB | Gas turbine plant | gas turbine | IEC | - | System |
| 10MBA | Gas turbine | gas turbine | IEC | 10MB | System |
| 10MBL | GT inlet air system | gas turbine | IEC | 10MB | System |
| 10MBN | GT liquid fuel and water injection | gas turbine | IEC | 10MB | System |
| 10MBP | GT fuel gas system incl. performance heater | gas turbine | IEC | 10MB | System |
| 10MBU | GT compressor washing | gas turbine | IEC | 10MB | System |
| 10MBV | GT lube oil system | gas turbine | IEC | 10MB | System |
| 10MBY | GT control and protection (TCS) | i and c | IEC | 10MB | System |
| 10MK | GT generator plant | generator | IEC | - | System |
| 10MKA | GT generator | generator | IEC | 10MK | System |
| 10MKC | GT excitation and static frequency converter | generator | IEC | 10MK | System |
| 10MKG | GT generator gas system (H2/CO2) | generator | IEC | 10MK | System |
| 10UHA | HRSG foundations and structures | civil structural | IEPC | - | System |
| 10UHN | Stack foundation | civil structural | IEPC | - | System |
| 10UMA | Gas turbine hall | civil structural | IEPC | - | System |
| 20BAA | ST generator busduct | electrical hv | IEC | - | System |
| 20BAC | ST generator circuit breaker | electrical hv | IEC | - | System |
| 20BAT | ST generator step-up transformer | electrical hv | IEC | - | System |
| 20BBT | ST unit auxiliary transformer | electrical mv lv | IEPC | - | System |
| 20LCA | Main condensate piping | condensate feedwater | IEPC | - | System |
| 20LCB | Condensate extraction pumps | condensate feedwater | IEPC | - | System |
| 20MA | Steam turbine plant | steam turbine | IEC | - | System |
| 20MAA | HP turbine | steam turbine | IEC | 20MA | System |
| 20MAB | IP/LP turbine | steam turbine | IEC | 20MA | System |
| 20MAG | Condensing system | water steam cycle | IEC | - | System |
| 20MAJ | Condenser vacuum system | steam turbine | IEC | 20MA | System |
| 20MAN | Turbine bypass stations and piping | water steam cycle | IEPC | 20MA | System |
| 20MAV | ST lube oil system | steam turbine | IEC | 20MA | System |
| 20MAW | Gland steam system | steam turbine | IEC | 20MA | System |
| 20MAX | ST control fluid system | steam turbine | IEC | 20MA | System |
| 20MAY | ST control and protection | i and c | IEC | 20MA | System |
| 20MK | ST generator plant | generator | IEC | - | System |
| 20MKA | ST generator | generator | IEC | 20MK | System |
| 20MKC | ST excitation | generator | IEC | 20MK | System |
| 20UMB | Steam turbine hall | civil structural | IEPC | - | System |

# 6. Plant asset register (equipment tags)

259 equipment items. CWA / CWP / MR assign each asset to its construction area, construction package and procurement package (AWP, ALP-EPC-00000-GE-PLN-0002).

| Tag | Description | AVEVA class | Supply | CWA | CWP | MR |
| --- | --- | --- | --- | --- | --- | --- |
| 00ACA10 | 380 kV GIS, double busbar, 6 bays | Switchgear And Controlgear | IEPC | CWA-04 | CWP-04-EL-01 | MR-EL-001 |
| 00BBA10 | MV switchgear 10.5 kV, section A | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-003 |
| 00BBA20 | MV switchgear 10.5 kV, section B | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-003 |
| 00BFA10 | LV main switchboard 0.4 kV, A | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BFA20 | LV main switchboard 0.4 kV, B | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BFA30 | LV MCC - power block | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BFA40 | LV MCC - CW pump house | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BFA50 | LV MCC - water treatment | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BFA60 | LV MCC - BOP utilities | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BFA70 | LV MCC - fuel gas and LDO | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BFA80 | LV MCC - buildings and HVAC | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BFT10 | LV transformer 10.5/0.4 kV 2.5 MVA, A | Power Transformer | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-004 |
| 00BFT20 | LV transformer 10.5/0.4 kV 2.5 MVA, B | Power Transformer | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-004 |
| 00BFT30 | LV transformer 10.5/0.4 kV 1.6 MVA - CW pump house | Power Transformer | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-004 |
| 00BFT40 | LV transformer 10.5/0.4 kV 1.6 MVA - water treatment | Power Transformer | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-004 |
| 00BMA10 | Emergency LV switchboard | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BMA20 | Emergency MCC - power block | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BRA10 | UPS 230 V AC (2 x 100 %) | UPS Unit | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-007 |
| 00BRA20 | DC 220 V distribution board | Switchgear And Controlgear | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-005 |
| 00BTA10 | Battery and charger 220 V DC (2 x 100 %) | Battery Back-Up Power Supply Unit | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-007 |
| 00CJA10 | Plant DCS (controllers, networks, operator stations) | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-001 |
| 00CJA20 | DCS remote I/O cabinets - power block | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-001 |
| 00CJA30 | DCS remote I/O cabinets - CW pump house | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-001 |
| 00CJA40 | DCS remote I/O cabinets - water treatment | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-001 |
| 00CJA50 | DCS remote I/O cabinets - BOP utilities | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-001 |
| 00CJA60 | DCS remote I/O cabinets - fuel gas and LDO | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-001 |
| 00CJG10 | BOP safety instrumented system (logic solver and cabinets) | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-008 |
| 00CKA10 | Historian, performance monitoring and operator training simulator | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-009 |
| 00CQA10 | Continuous emission monitoring system | Analyser | IEPC | CWA-01 | CWP-01-IC-01 | MR-IC-002 |
| 00CYA10 | Telecom, CCTV, access control and security system | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-007 |
| 00EGA10 | LDO unloading station (4 bays) | Equipment Package Skid | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGA10AP001 | LDO unloading pump A | Centrifugal Pump | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGA10AP002 | LDO unloading pump B | Centrifugal Pump | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGA10AP003 | LDO unloading pump C | Centrifugal Pump | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGA10AP004 | LDO unloading pump D | Centrifugal Pump | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGA10AT001 | LDO unloading basket filter A | Filter | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGA10AT002 | LDO unloading basket filter B | Filter | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGA10BB001 | LDO unloading slop tank | Tank | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGB10BB001 | LDO storage tank A 3,500 m3 | Fixed Roof Tank | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-017 |
| 00EGB10BB002 | LDO storage tank B 3,500 m3 | Fixed Roof Tank | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-017 |
| 00EGB10BB003 | LDO tank farm recovery sump | Tank | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-017 |
| 00EGC10 | LDO forwarding and treatment skid | Equipment Package Skid | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGC10AP001 | LDO forwarding pump A (3 x 50 %) | Centrifugal Pump | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGC10AP002 | LDO forwarding pump B (3 x 50 %) | Centrifugal Pump | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGC10AP003 | LDO forwarding pump C (3 x 50 %) | Centrifugal Pump | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGC10AT001 | LDO duplex filter A | Filter | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGC10AT002 | LDO duplex filter B | Filter | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EGC10AT003 | LDO treatment centrifuge | Filter | IEPC | CWA-10 | CWP-10-ME-01 | MR-ME-016 |
| 00EKA10 | Gas receiving, filtration and fiscal metering station | Equipment Package Skid | IEPC | CWA-09 | CWP-09-ME-01 | MR-ME-015 |
| 00EKA10AC001 | Gas preheater A (electric) | Plate Heat Exchanger | IEPC | CWA-09 | CWP-09-ME-01 | MR-ME-015 |
| 00EKA10AC002 | Gas preheater B (electric) | Plate Heat Exchanger | IEPC | CWA-09 | CWP-09-ME-01 | MR-ME-015 |
| 00EKA10AT001 | Gas filter separator A | Filter | IEPC | CWA-09 | CWP-09-ME-01 | MR-ME-015 |
| 00EKA10AT002 | Gas filter separator B | Filter | IEPC | CWA-09 | CWP-09-ME-01 | MR-ME-015 |
| 00EKA10BB001 | Gas station condensate drain vessel | Tank | IEPC | CWA-09 | CWP-09-ME-01 | MR-ME-015 |
| 00GBA10 | Seawater reverse osmosis package (2 x 100 %) | Equipment Package Skid | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AP001 | SWRO feed pump A | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AP002 | SWRO feed pump B | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AP003 | SWRO high-pressure pump A | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AP004 | SWRO high-pressure pump B | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AT001 | SWRO multimedia filter A | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AT002 | SWRO multimedia filter B | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AT003 | SWRO multimedia filter C | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AT004 | SWRO cartridge filter A | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10AT005 | SWRO cartridge filter B | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GBA10BB001 | SWRO permeate tank | Tank | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GCA10 | Demineralisation package (EDI / mixed bed) | Equipment Package Skid | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GCA10AP001 | EDI feed pump A | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GCA10AP002 | EDI feed pump B | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GCA10AT001 | EDI stack A | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GCA10AT002 | EDI stack B | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GCA10AT003 | Mixed bed polisher A | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GCA10AT004 | Mixed bed polisher B | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00GHA10AP001 | Demin water forwarding pump A | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-013 |
| 00GHA10AP002 | Demin water forwarding pump B | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-013 |
| 00GHA10BB001 | Demineralised water tank A | Tank | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-013 |
| 00GHA10BB002 | Demineralised water tank B | Tank | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-013 |
| 00GKA10AP001 | Potable water pump A | Centrifugal Pump | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-013 |
| 00GKA10AP002 | Potable water pump B | Centrifugal Pump | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-013 |
| 00GKA10AT001 | Potable water UV disinfection | Filter | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-013 |
| 00GKA10BB001 | Potable water tank | Tank | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-013 |
| 00GMA10AP001 | Process drain sump pump - power block A | Centrifugal Pump | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-014 |
| 00GMA10AP002 | Process drain sump pump - power block B | Centrifugal Pump | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-014 |
| 00GMA10AP003 | Oily water sump pump - transformer area | Centrifugal Pump | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-014 |
| 00GMA10AP004 | Oily water sump pump - LDO area | Centrifugal Pump | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-014 |
| 00GMA10AP005 | Chemical drain sump pump - water treatment | Centrifugal Pump | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-014 |
| 00GMA10AP006 | Drain sump pump - CW pump house | Centrifugal Pump | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-014 |
| 00GMA10AT001 | Oil separator (API / coalescing) | Filter | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-014 |
| 00GMA10BB001 | Neutralisation pit | Tank | IEPC | CWA-12 | CWP-12-EL-01 | MR-ME-014 |
| 00GNA10 | Waste water treatment package | Equipment Package Skid | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GNA10AP001 | Waste water transfer pump A | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GNA10AP002 | Waste water transfer pump B | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GNA10AP003 | Treated effluent pump A | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GNA10AP004 | Treated effluent pump B | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GNA10BB001 | Equalisation tank | Tank | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GNA10BB002 | Neutralisation tank | Tank | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GUA10 | Sanitary treatment package | Equipment Package Skid | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GUA10AP001 | Sanitary lift pump A | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00GUA10AP002 | Sanitary lift pump B | Centrifugal Pump | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-014 |
| 00LDA10 | Condensate polishing plant | Equipment Package Skid | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00LDA10AT001 | Condensate polisher vessel A | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00LDA10AT002 | Condensate polisher vessel B | Filter | IEPC | CWA-07 | CWP-07-ME-01 | MR-ME-012 |
| 00PAA10AA001 | Intake stop log / sluice gate A (motorised) | Butterfly Valve | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-004 |
| 00PAA10AA002 | Intake stop log / sluice gate B (motorised) | Butterfly Valve | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-004 |
| 00PAA10AP001 | Screen wash pump A | Centrifugal Pump | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-004 |
| 00PAA10AP002 | Screen wash pump B | Centrifugal Pump | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-004 |
| 00PAA10AT001 | Travelling band screen A | Filter | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-004 |
| 00PAA10AT002 | Travelling band screen B | Filter | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-004 |
| 00PAA10AT003 | Trash rake A | Filter | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-004 |
| 00PAA10AT004 | Trash rake B | Filter | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-004 |
| 00PAB10AA001 | CW pump discharge butterfly valve A DN2800 (motorised) | Butterfly Valve | IEPC | CWA-05 | CWP-05-ME-01 | MR-PI-004 |
| 00PAB10AA002 | CW pump discharge butterfly valve B DN2800 (motorised) | Butterfly Valve | IEPC | CWA-05 | CWP-05-ME-01 | MR-PI-004 |
| 00PAC10AP001 | CW pump A (2 x 50 %, vertical) | Centrifugal Pump | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-003 |
| 00PAC10AP002 | CW pump B (2 x 50 %, vertical) | Centrifugal Pump | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-003 |
| 00PAH10 | Condenser tube cleaning system (balls, strainers) | Equipment Package Skid | IEPC | CWA-02 | CWP-02-ME-01 | MR-ME-006 |
| 00PAH10AP001 | Ball recirculation pump A | Centrifugal Pump | IEPC | CWA-02 | CWP-02-ME-01 | MR-ME-006 |
| 00PAH10AP002 | Ball recirculation pump B | Centrifugal Pump | IEPC | CWA-02 | CWP-02-ME-01 | MR-ME-006 |
| 00PAH10AT001 | Debris filter A | Filter | IEPC | CWA-02 | CWP-02-ME-01 | MR-ME-006 |
| 00PAH10AT002 | Debris filter B | Filter | IEPC | CWA-02 | CWP-02-ME-01 | MR-ME-006 |
| 00PBA10 | Electro-chlorination package | Equipment Package Skid | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10AN001 | Hydrogen dilution fan A | Fan | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10AN002 | Hydrogen dilution fan B | Fan | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10AP001 | Chlorination seawater booster pump A | Centrifugal Pump | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10AP002 | Chlorination seawater booster pump B | Centrifugal Pump | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10AP003 | Hypochlorite dosing pump A | Centrifugal Pump | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10AP004 | Hypochlorite dosing pump B | Centrifugal Pump | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10AT001 | Electrolyser cell stack A | Filter | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10AT002 | Electrolyser cell stack B | Filter | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10BB001 | Hypochlorite storage tank A | Tank | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PBA10BB002 | Hypochlorite storage tank B | Tank | IEPC | CWA-05 | CWP-05-ME-01 | MR-ME-005 |
| 00PGA10AC001 | CCW plate heat exchanger A (2 x 100 %) | Plate Heat Exchanger | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-007 |
| 00PGA10AC002 | CCW plate heat exchanger B (2 x 100 %) | Plate Heat Exchanger | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-007 |
| 00PGA10AP001 | CCW pump A (2 x 100 %) | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-007 |
| 00PGA10AP002 | CCW pump B (2 x 100 %) | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-007 |
| 00PGA10AT001 | CCW side-stream filter | Filter | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-007 |
| 00PGA10BB001 | CCW expansion tank | Pressure Vessel | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-007 |
| 00PGA10BB002 | CCW chemical pot feeder | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-007 |
| 00QCA10 | Chemical dosing skid (ammonia, oxygen scavenger) | Equipment Package Skid | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10AP001 | Ammonia dosing pump A | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10AP002 | Ammonia dosing pump B | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10AP003 | Oxygen scavenger dosing pump A | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10AP004 | Oxygen scavenger dosing pump B | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10AP005 | Phosphate / caustic dosing pump A | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10AP006 | Phosphate / caustic dosing pump B | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10BB001 | Ammonia solution tank | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10BB002 | Oxygen scavenger tank | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QCA10BB003 | Caustic solution tank | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-011 |
| 00QEA10AN001 | Air compressor A (2 x 100 %) | Compressor | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-008 |
| 00QEA10AN002 | Air compressor B (2 x 100 %) | Compressor | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-008 |
| 00QEA10AN003 | Service air compressor | Compressor | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-008 |
| 00QEA10AT001 | Instrument air dryer (2 x 100 %) | Instrument Air Dryer | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-008 |
| 00QEA10AT003 | Instrument air after-filters | Filter | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-008 |
| 00QEA10BB001 | Instrument air receiver | Pressure Vessel | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-008 |
| 00QEA10BB002 | Service air receiver | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-008 |
| 00QHA10 | Auxiliary boiler 12 t/h, gas-fired | Boiler | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-009 |
| 00QHA10AN001 | Auxiliary boiler combustion air fan | Fan | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-009 |
| 00QHA10AP001 | Auxiliary boiler feed pump A | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-009 |
| 00QHA10AP002 | Auxiliary boiler feed pump B | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-009 |
| 00QHA10BB001 | Auxiliary boiler feed water tank / deaerator | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-009 |
| 00QHA10BB002 | Auxiliary boiler blowdown vessel | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-009 |
| 00QJA10 | Nitrogen supply package (bottle racks / generator) | Equipment Package Skid | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-010 |
| 00QJA10BB001 | Nitrogen buffer vessel | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-010 |
| 00QJB10 | Hydrogen and CO2 bottle racks | Equipment Package Skid | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-010 |
| 00QUA10 | Steam/water analysis system (SWAS) | Equipment Package Skid | IEPC | CWA-01 | CWP-01-ME-01 | MR-IC-003 |
| 00QUA10AC001 | Sample cooler rack | Plate Heat Exchanger | IEPC | CWA-01 | CWP-01-ME-01 | MR-IC-003 |
| 00SAA10 | HVAC plant (chillers, AHUs, pressurisation) | Equipment Package Skid | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA10AN001 | Chiller A | Compressor | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA10AN002 | Chiller B | Compressor | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA10AN003 | Chiller C | Compressor | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA10AP001 | Chilled water pump A | Centrifugal Pump | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA10AP002 | Chilled water pump B | Centrifugal Pump | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA11AN001 | AHU - control room | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA11AN002 | AHU - electronic rooms | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA11AN003 | AHU - electrical building MV rooms | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA11AN004 | AHU - electrical building LV rooms | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA11AN005 | AHU - GIS building | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA11AN006 | AHU - administration building | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA11AN007 | AHU - workshop | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA11AN008 | Pressurisation unit - control building | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA12AN001 | GT hall roof ventilator A | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA12AN002 | GT hall roof ventilator B | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA12AN003 | GT hall roof ventilator C | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA12AN004 | GT hall roof ventilator D | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA13AN001 | ST hall roof ventilator A | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA13AN002 | ST hall roof ventilator B | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA13AN003 | ST hall roof ventilator C | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA13AN004 | ST hall roof ventilator D | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA14AN001 | Battery room exhaust fan A | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SAA14AN002 | Battery room exhaust fan B | Fan | IEPC | CWA-03 | CWP-03-HV-01 | MR-HV-001 |
| 00SGA10AP001 | Electric fire pump | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGA10AP002 | Diesel fire pump | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGA10AP003 | Jockey pump | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGA10BB001 | Fire water tank | Fixed Roof Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-013 |
| 00SGA10BB002 | Fire water tank B | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA001 | Deluge valve set - GSU transformer GT | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA002 | Deluge valve set - GSU transformer ST | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA003 | Deluge valve set - unit auxiliary transformers | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA004 | Deluge valve set - GT lube oil module | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA005 | Deluge valve set - ST lube oil module | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA006 | Deluge valve set - LDO tank A | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA007 | Deluge valve set - LDO tank B | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA008 | Deluge valve set - LDO forwarding | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA009 | Deluge valve set - cable spreading room | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10AA010 | Foam proportioner - LDO unloading | Butterfly Valve | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGC10BB001 | Foam concentrate tank | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-020 |
| 00SGY10 | Fire alarm control panel and detection network | Control Cabinet | IEPC | CWA-11 | CWP-11-IC-01 | MR-IC-006 |
| 00SMA10 | GT hall EOT crane 120/20 t | Crane | IEPC | CWA-01 | CWP-01-SS-01 | MR-ME-021 |
| 00SMA20 | ST hall EOT crane 100 t | Crane | IEPC | CWA-02 | CWP-02-SS-01 | MR-ME-021 |
| 00SMA30 | CW pump house overhead crane 25 t | Crane | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-021 |
| 00SMA40 | Workshop overhead crane 10 t | Crane | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-021 |
| 00SMA50 | BFP maintenance hoist 10 t | Crane | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-021 |
| 00SMA60 | Water treatment building hoist 5 t | Crane | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-021 |
| 00XJA10 | Emergency diesel generator 1,250 kVA | Synchronous Generator | IEPC | CWA-03 | CWP-03-EL-01 | MR-EL-006 |
| 00XJA10BB001 | Emergency diesel generator day tank | Tank | IEPC | CWA-03 | CWP-03-HV-01 | MR-EL-006 |
| 10BAA10 | GT isolated phase busduct | Switchgear And Controlgear | IEC | CWA-01 | CWP-01-EL-01 | MR-EL-101 |
| 10BAC10 | GT generator circuit breaker | Switchgear And Controlgear | IEC | CWA-01 | CWP-01-EL-01 | MR-EL-101 |
| 10BAT10 | GT step-up transformer 560 MVA 400/21 kV | Power Transformer | IEC | CWA-01 | CWP-01-EL-01 | MR-EL-102 |
| 10BBT10 | GT unit auxiliary transformer 21/10.5 kV 31.5 MVA | Power Transformer | IEPC | CWA-01 | CWP-01-EL-01 | MR-EL-002 |
| 10HAA10 | Heat recovery steam generator, 3-pressure reheat | Steam Generator | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-102 |
| 10HAN10AP001 | HRSG drain pump A | Centrifugal Pump | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-019 |
| 10HAN10AP002 | HRSG drain pump B | Centrifugal Pump | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-019 |
| 10HAN10BB001 | HRSG blowdown tank | Tank | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-019 |
| 10HAN10BB002 | Atmospheric drain tank | Tank | IEPC | CWA-01 | CWP-01-ME-01 | MR-ME-019 |
| 10HNA10 | HRSG inlet duct and flue gas ducting | Equipment Package Skid | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-102 |
| 10HNE10 | Stack 65 m, D 9.2 m, with silencer and CEMS platform | Stack | IEPC | CWA-01 | CWP-01-ME-01 | MR-SS-002 |
| 10HSA10 | SCR catalyst and ammonia injection grid | Equipment Package Skid | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-102 |
| 10HSB10AP001 | Ammonia forwarding pump A | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-018 |
| 10HSB10AP002 | Ammonia forwarding pump B | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-018 |
| 10HSB10BB001 | Aqueous ammonia tank A 30 m3 | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-018 |
| 10HSB10BB002 | Aqueous ammonia tank B 30 m3 | Tank | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-018 |
| 10LAC10AP001 | Boiler feed pump A (2 x 100 %, VFD) | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-001 |
| 10LAC10AP002 | Boiler feed pump B (2 x 100 %, VFD) | Centrifugal Pump | IEPC | CWA-08 | CWP-08-ME-01 | MR-ME-001 |
| 10MBA10 | Gas turbine | Gas Turbine | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-101 |
| 10MBL10 | GT inlet air filter house | Equipment Package Skid | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-101 |
| 10MBN10 | GT liquid fuel and water injection module | Equipment Package Skid | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-101 |
| 10MBP10 | GT fuel gas module incl. performance heater | Equipment Package Skid | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-101 |
| 10MBU10 | GT compressor wash skid | Equipment Package Skid | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-101 |
| 10MBV10 | GT lube oil module | Equipment Package Skid | IEC | CWA-01 | CWP-01-ME-01 | MR-ME-101 |
| 10MBY10 | GT control and protection cabinets (TCS) | Control Cabinet | IEC | CWA-01 | CWP-01-IC-01 | MR-IC-101 |
| 10MKA10 | GT generator 560 MVA, H2-cooled | Synchronous Generator | IEC | CWA-01 | CWP-01-ME-01 | MR-EL-101 |
| 10MKC10 | GT static excitation | Switchgear And Controlgear | IEC | CWA-01 | CWP-01-EL-01 | MR-EL-101 |
| 10MKC20 | GT static frequency converter | Switchgear And Controlgear | IEC | CWA-01 | CWP-01-EL-01 | MR-EL-101 |
| 10MKG10 | GT generator gas unit (H2/CO2) | Equipment Package Skid | IEC | CWA-01 | CWP-01-ME-01 | MR-EL-101 |
| 20BAA10 | ST isolated phase busduct | Switchgear And Controlgear | IEC | CWA-02 | CWP-02-EL-01 | MR-EL-101 |
| 20BAC10 | ST generator circuit breaker | Switchgear And Controlgear | IEC | CWA-02 | CWP-02-EL-01 | MR-EL-101 |
| 20BAT10 | ST step-up transformer 270 MVA 400/15.75 kV | Power Transformer | IEC | CWA-02 | CWP-02-EL-01 | MR-EL-102 |
| 20BBT10 | ST unit auxiliary transformer 15.75/10.5 kV 16 MVA | Power Transformer | IEPC | CWA-02 | CWP-02-EL-01 | MR-EL-002 |
| 20LCB10AP001 | Condensate extraction pump A (2 x 100 %) | Centrifugal Pump | IEPC | CWA-02 | CWP-02-ME-01 | MR-ME-002 |
| 20LCB10AP002 | Condensate extraction pump B (2 x 100 %) | Centrifugal Pump | IEPC | CWA-02 | CWP-02-ME-01 | MR-ME-002 |
| 20MAA10 | Steam turbine, reheat condensing, 2 casings | Steam Turbine | IEC | CWA-02 | CWP-02-ME-01 | MR-ME-103 |
| 20MAB10 | IP/LP steam turbine | Equipment Package Skid | IEC | CWA-02 | CWP-02-ME-01 | MR-ME-103 |
| 20MAG10 | Surface condenser, titanium tubes, 15,200 m2 | Condenser | IEC | CWA-02 | CWP-02-ME-01 | MR-ME-103 |
| 20MAJ10AP001 | Condenser vacuum pump A | Centrifugal Pump | IEC | CWA-02 | CWP-02-ME-01 | MR-ME-103 |
| 20MAJ10AP002 | Condenser vacuum pump B | Centrifugal Pump | IEC | CWA-02 | CWP-02-ME-01 | MR-ME-103 |
| 20MAV10 | ST lube oil module | Equipment Package Skid | IEC | CWA-02 | CWP-02-ME-01 | MR-ME-103 |
| 20MAW10 | Gland steam condenser and exhausters | Equipment Package Skid | IEC | CWA-02 | CWP-02-ME-01 | MR-ME-103 |
| 20MAX10 | ST control fluid unit | Equipment Package Skid | IEC | CWA-02 | CWP-02-ME-01 | MR-ME-103 |
| 20MAY10 | ST control and protection cabinets | Control Cabinet | IEC | CWA-02 | CWP-02-IC-01 | MR-IC-101 |
| 20MKA10 | ST generator 270 MVA, TEWAC | Synchronous Generator | IEC | CWA-02 | CWP-02-ME-01 | MR-EL-101 |
| 20MKC10 | ST static excitation | Switchgear And Controlgear | IEC | CWA-02 | CWP-02-EL-01 | MR-EL-101 |

# 7. Tools and control

Check or explain a code: python -m engine kks <tag | system | document number>.

Create tags only via python -m engine db add equipment ... --reason (classify with --set aveva_class=...).

The engineering_plan engine checks every system code and equipment tag against the key list at each run; findings are listed below and in the MDL workbook.

Changes to the key list: new key record (status proposed) -> Owner agreement by TQ -> status agreed.

# Check results (engine)

3 OK, 1 INFO, 0 WARN (checks: AVEVA class, KKS key list, KKS system, KKS tag). WARN must be resolved before the next issue; INFO is noted.

| Item | Check | Result | Detail |
| --- | --- | --- | --- |
| - | KKS key list | INFO | 128 key titles not yet verified against the licensed VGB key list |
| - | AVEVA class | OK | 259 of 259 equipment records classified |
| - | AVEVA class | OK | 119 of 119 system records classified |
| - | AVEVA class | OK | 2205 of 2205 document records classified |