# Alpilla 600 MW Combined Cycle Power Plant
Tie-in and Terminal Point Register

62 points: 16 Owner/Contractor terminal points (TP-) under ALP-EPC-001 and 46 interfaces between the consortium members (IF-) under ALP-CA-001. 62 agreed or frozen, 0 draft. Checks: 0 warning(s), 21 note(s).

# 1. Conventions

TP- points: Owner side / Contractor side under the EPC contract. IF- points: Istanbul EPC side / Imaginary Electric side under the consortium agreement. The scope break states who supplies the flange or weld end, counter-flange, gasket, bolts, the closing weld and its NDT/PWHT, supports and cable terminations; 'available by' is the date the providing side has its side ready, 'needed by' the date the receiving side needs it.

Pressures in barg (vacuum as negative barg; HMB stream pressures in bar(a) are converted with 1.01325 bar), temperatures in degC. Design values are the mechanical design of the receiving connection.

Operating envelope = the range the providing side guarantees at the point. It is checked against the HMB streams of all 9 HMB cases (MAX-NG-100, MIN-NG-100, SRC-LDO-100, SRC-NG-060, SRC-NG-100, SRC-NG-GT80, SRC-NG-MEL, SUM-NG-100, WIN-NG-100).

Chain = point fed from an upstream point through passive equipment: the minimum upstream pressure less the agreed pressure loss (chain dp) must cover this point's minimum pressure; a higher upstream design pressure or temperature requires a declared protection (relief, slam-shut, safety valve set points).

Status: draft (proposed), agreed (confirmed in writing by both sides, TQ reference), frozen (change only by TQ).

# 2. Overview

| ID | Category | Service | Size / rating | Operating envelope | Available | Needed | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TP-A1 | land access | Temporary construction area (5 ha) | - | - | 2027-02-01 | 2027-03-01 | agreed |
| TP-A2 | land access | Site (plot) handover | - | - | 2026-11-02 | 2026-11-16 | agreed |
| TP-CW1 | marine | Seawater intake head | about 2 x DN2200 (Contractor to size) | 7-27 degC; max 40,000 m3/h | 2027-04-30 | 2027-10-01 | agreed |
| TP-CW2 | marine | Outfall diffuser | - | 12-34 degC; max 40,000 m3/h | 2027-04-30 | 2027-10-01 | agreed |
| TP-D1 | civil | Storm water discharge | - | max 2.00 m3/s | 2026-11-02 | 2027-01-15 | agreed |
| TP-E1 | electrical | Grid connection 380 kV | 380 kV, 2 circuits | 380.0 kV (342.0-420.0); max 640 MW | 2028-07-15 | 2028-07-22 | agreed |
| TP-E2 | electrical | Construction power | 34.5 kV / 5 MVA | 34.5 kV (31.1-38.0); max 5.00 MVA | 2027-02-28 | 2027-03-15 | agreed |
| TP-G1 | process | Natural gas supply | 16 in (DN400), CL600 | 45.0-70.0 barg; 5-25 degC; max 115,000 Sm3/h | 2028-06-30 | 2028-08-15 | agreed |
| TP-L1 | process | LDO supply | 4 in tanker coupling (API RP 1004 bottom loading / dry-break) | 0.0-3.0 barg; 0-40 degC; max 150 m3/h | 2028-09-01 | 2028-11-01 | agreed |
| TP-M1 | marine | Temporary barge landing | - | - | 2027-09-30 | 2027-11-01 | agreed |
| TP-R1 | land access | Road access | - | - | 2026-11-02 | 2026-11-16 | agreed |
| TP-S1 | permit service | Sanitary wastewater | - | - | - | - | agreed |
| TP-T1 | control | Telecommunication | - | - | 2027-06-30 | 2028-05-01 | agreed |
| TP-T2 | control | Emission data link to the environmental authority | - | - | 2028-08-01 | 2028-10-02 | agreed |
| TP-T3 | control | TSO SCADA and revenue metering link | - | - | 2028-05-01 | 2028-06-01 | agreed |
| TP-W1 | utility | Potable water | DN150 | 2.5-6.0 barg; 5-25 degC; max 20.00 m3/h | 2027-02-28 | 2027-03-15 | agreed |
| IF-01 | process | Natural gas to GT | 12 in (DN300) CL600 | 36.5-41.0 barg; 5-40 degC; max 23.00 kg/s | 2028-08-31 | 2028-09-18 | agreed |
| IF-02 | process | LDO to GT | 6 in (DN150) CL150 | 3.0-6.0 barg; 10-45 degC; max 24.00 kg/s | 2028-11-15 | 2028-12-01 | agreed |
| IF-03 | process | Demin water for water injection | 4 in (DN100) CL150 | 3.0-6.0 barg; 10-40 degC; max 15.00 kg/s | 2028-11-15 | 2028-12-01 | agreed |
| IF-04 | utility | Compressor wash water | 2 in (DN50) CL150 | 3.0-6.0 barg; 10-40 degC; max 10.00 m3/h | 2028-09-15 | 2028-12-15 | agreed |
| IF-05 | process | HP steam | 12 in P91 (SA-335 P91) | 59.0-192.0 barg; 560-600 degC; max 105 kg/s | 2028-09-30 | 2028-10-16 | agreed |
| IF-06 | process | HP steam | 12 in P91 (SA-335 P91) | 52.0-186.0 barg; 560-600 degC; max 105 kg/s | 2028-09-30 | 2028-10-16 | agreed |
| IF-07 | process | Cold reheat | 24 in SA-335 P22 | 18.0-41.0 barg; 340-395 degC; max 105 kg/s | 2028-09-30 | 2028-10-16 | agreed |
| IF-08 | process | Cold reheat | 24 in SA-335 P22 | 17.0-41.0 barg; 340-395 degC; max 105 kg/s | 2028-09-30 | 2028-10-16 | agreed |
| IF-09 | process | Hot reheat | 28 in P91 (SA-335 P91) | 17.0-38.5 barg; 550-600 degC; max 125 kg/s | 2028-09-30 | 2028-10-16 | agreed |
| IF-10 | process | Hot reheat | 28 in P91 (SA-335 P91) | 15.5-38.5 barg; 550-600 degC; max 125 kg/s | 2028-09-30 | 2028-10-16 | agreed |
| IF-11 | process | LP steam | 20 in SA-106 C | 1.5-5.0 barg; 210-260 degC; max 16.50 kg/s | 2028-09-30 | 2028-10-16 | agreed |
| IF-12 | process | LP steam | 20 in SA-106 C | 1.1-5.0 barg; 210-260 degC; max 16.50 kg/s | 2028-09-30 | 2028-10-16 | agreed |
| IF-13 | process | HP / IP / LP bypass valves | HP 12 in / IP 28 in / LP 20 in (per valve datasheets) | 1.0-192.0 barg; 150-600 degC; max 125 kg/s | 2028-02-01 | 2028-03-01 | agreed |
| IF-14 | process | Bypass steam to condenser | 2 x 36 in + 1 x 28 in | -1.0-12.0 barg; 40-250 degC; max 142 kg/s | 2028-05-01 | 2028-06-01 | agreed |
| IF-15 | process | Condensate from hotwell | 20 in (DN500) CL150 | -1.0--0.9 barg; 15-40 degC; max 140 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-16 | process | Condensate to CPH | 12 in (DN300) CL300 | 12.0-21.0 barg; 15-45 degC; max 150 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-17 | process | BFP suction | 16 in (DN400) CL150 | 1.5-6.0 barg; 130-165 degC; max 140 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-18 | process | HP feedwater | 10 in (DN250) CL2500 | 95.0-215.0 barg; 130-170 degC; max 110 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-19 | process | IP feedwater | 6 in (DN150) CL600 | 20.0-48.0 barg; 130-165 degC; max 33.00 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-20 | process | FGH water return | 4 in (DN100) CL600 | 18.0-46.0 barg; 60-90 degC; max 14.50 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-21 | process | HRSG blowdown | 2 in / 3 in | 0.0-5.0 barg; 100-370 degC; max 5.00 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-22 | process | HRSG drains and vents | various (1 in - 3 in) | 0.0-1.0 barg; 40-610 degC; max 10.00 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-23 | utility | Chemical dosing | 1 in | 3.0-215.0 barg; 5-40 degC; max 0.10 m3/h | 2028-09-01 | 2028-09-15 | agreed |
| IF-24 | utility | Sampling | 1/2 in | -1.0-215.0 barg; 20-600 degC; max 0.50 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-25 | utility | Aqueous ammonia | 1 in | 3.0-7.0 barg; 5-40 degC; max 0.50 t/h | 2028-11-01 | 2028-11-15 | agreed |
| IF-26 | process | Flue gas to stack | D 9.2 m | 0.0-0.0 barg; 60-120 degC; max 850 kg/s | 2028-06-30 | 2028-09-15 | agreed |
| IF-27 | process | Circulating water | 4 x DN1800 | 0.5-3.0 barg; 5-35 degC; max 38,000 m3/h | 2028-09-01 | 2028-09-15 | agreed |
| IF-28 | utility | Closed cooling water | various (DN50 - DN400) | 3.0-6.0 barg; 20-36 degC; max 1,160 m3/h | 2028-08-09 | 2028-08-16 | agreed |
| IF-29 | utility | Instrument and service air | 1 in - 2 in | 6.0-8.0 barg; 5-45 degC; max 500 Nm3/h | 2028-08-09 | 2028-08-16 | agreed |
| IF-30 | utility | Nitrogen | 1 in | 5.0-8.0 barg; 5-40 degC; max 1,000 Nm3/h | 2028-09-01 | 2028-09-15 | agreed |
| IF-31 | utility | Hydrogen / CO2 | 1/2 in | 8.0-12.0 barg; 5-40 degC; max 60.00 Nm3/h | 2028-08-25 | 2028-09-01 | agreed |
| IF-32 | utility | Auxiliary steam | 4 in (DN100) CL300 | 8.0-9.5 barg; 250-300 degC; max 7.50 t/h | 2028-09-30 | 2028-10-16 | agreed |
| IF-33 | control | Fire protection | - | - | 2028-08-17 | 2028-08-24 | agreed |
| IF-34 | electrical | GT GSU HV | 560 MVA | 380.0 kV (342.0-420.0); max 560 MVA | 2028-07-29 | 2028-08-02 | agreed |
| IF-35 | electrical | ST GSU HV | 270 MVA | 380.0 kV (342.0-420.0); max 270 MVA | 2028-07-29 | 2028-08-02 | agreed |
| IF-36 | electrical | UAT supply | 21 kV (GT) / 15.75 kV (ST) | 21.0 kV (19.9-22.1); max 31.50 MVA | 2028-08-09 | 2028-08-16 | agreed |
| IF-37 | electrical | MV supplies | 10.5 kV feeders | 10.5 kV (9.4-11.6); max 10.00 MVA | 2028-08-09 | 2028-08-16 | agreed |
| IF-38 | electrical | LV supplies | 0.4 kV feeders | 0.4 kV (0.4-0.4) | 2028-08-09 | 2028-08-16 | agreed |
| IF-39 | electrical | DC and UPS | 220 V DC / 230 V AC UPS | 0.2 kV (0.2-0.2) | 2028-08-09 | 2028-08-16 | agreed |
| IF-40 | control | Control system interface | OPC UA + Modbus TCP, redundant; hardwired trips | - | 2028-06-01 | 2028-06-15 | agreed |
| IF-41 | control | Protection interface | IEC 61850 + hardwired | - | 2028-07-29 | 2028-08-02 | agreed |
| IF-42 | civil | Earthing | - | - | 2027-10-15 | 2027-11-15 | agreed |
| IF-43 | civil | Foundations | - | - | 2027-11-01 | 2027-11-15 | agreed |
| IF-44 | process | Condenser tube cleaning balls | 2 x DN150 per inlet half | 0.5-3.5 barg; 5-35 degC; max 200 m3/h | 2028-09-01 | 2028-09-15 | agreed |
| IF-45 | process | HP attemperation spray water | 3 in (DN80) CL2500 | 95.0-215.0 barg; 130-170 degC; max 5.00 kg/s | 2028-09-01 | 2028-09-15 | agreed |
| IF-46 | process | Reheat attemperation spray water | 2 in (DN50) CL600 | 20.0-48.0 barg; 130-170 degC; max 3.00 kg/s | 2028-09-01 | 2028-09-15 | agreed |

# 3. Tie-in data cards

## TP-A1  Temporary construction area (5 ha)

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / land_access |
| --- | --- |
| Medium / location | land / E 0-180, N 320-600 (5.04 ha), north of the plot, west of the access road (E 90.0, N 460.0, EL +15.00 m) |
| Size / connection | - / Fenced 5.04 ha field E 0-180, N 320-600 |
| Scope break | Owner: lease of the field until Taking-Over, free of charge to the Contractor. Contractor: fencing, surfacing, drainage, temporary facilities and restoration to the original condition. |
| Owner side | Lease of the 5 ha field until Taking-Over, free of charge to the Contractor |
| Contractor side | Laydown, pre-assembly, contractor facilities; restoration at the end |
| Isolation | - |
| Protection | - |
| Dates | available by 2027-02-01; needed by 2027-03-01 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Remarks | Lease starts 2027-02-01 (TQ-030). |
| Checks (engine) | OK completeness: land_access: complete OK dates: available 2027-02-01, needed 2027-03-01: float 28 d |

## TP-A2  Site (plot) handover

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / land_access |
| --- | --- |
| Medium / location | land / Plot E 0-400, N 0-300 (plant grid), levelled to +15.0 m (E 200.0, N 150.0, EL +15.00 m) |
| Size / connection | - / Plot boundary per land-use plan with boundary survey monuments |
| Scope break | Owner: plot per land-use plan, levelled to +15.0 m with compaction records, boundary monuments, free of encumbrances except the buried 11 kV utility cable along the east boundary (E 390, N 0-300), which the Owner relocates outside the plot by 2027-06-30; the east strip E 370-400 is not available to the Contractor before then. Contractor: everything within the plot boundary from the access date, incl. demolition of the abandoned foundations (E 300-360, N 20-60) and the 10 m channel buffer. |
| Owner side | Plot free of encumbrances, levelled to +15.0 m, boundary monuments; relocation of the buried 11 kV cable (E 390) by 2027-06-30 |
| Contractor side | All works within the plot from the access date |
| Isolation | - |
| Protection | - |
| Conditions (text) | East strip E 370-400 available 2027-06-30 (needed by the Contractor 2027-09-01 for the gas station civil works). |
| Dates | available by 2026-11-02; needed by 2026-11-16 |
| Scope items | SC-001 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: land_access: complete OK dates: available 2026-11-02, needed 2026-11-16: float 14 d |

## TP-CW1  Seawater intake head

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / marine |
| --- | --- |
| Medium / location | seawater / About 650 m offshore at -12 m (E 150.0, N -710.0, EL -12.00 m) |
| Size / connection | about 2 x DN2200 (Contractor to size) / Offshore intake head with velocity cap at -12 m |
| Scope break | Owner: seabed survey and marine permit for the intake location. Contractor: intake head (velocity cap <= 0.15 m/s), pipelines, screens and pump house (SC-016, SC-042). |
| Owner side | Seabed survey and marine permit |
| Contractor side | Intake head, pipelines, pump house |
| Isolation | - |
| Protection | - |
| Operating envelope | - to - barg; 7 to 27 degC |
| Flow | normal 36,050.00 / max 40,000.00 m3/h (density 1025.0 kg/m3) |
| HMB envelope (all cases) | stream 25 (flow_temperature check): 10196.80-10196.80 kg/s, 1.487-1.487 barg, 6.9-27.0 degC |
| Quality / specification | source:SRC-OWNR-0002, requirement:ER-02.04 |
| Conditions (text) | 6.9-27.0 degC |
| Dates | available by 2027-04-30; needed by 2027-10-01 |
| Scope items | SC-016 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Remarks | Capacity includes about 2,000 m3/h for SWRO and electro-chlorination in addition to the 38,000 m3/h CW design flow; pressure at the intake is hydrostatic (HMB pressure check not applicable). |
| Checks (engine) | OK completeness: marine: complete OK HMB flow: stream 25 max 10196.80 kg/s (WIN-NG-100) <= capacity 11388.89 kg/s (margin +10.5 %), 9 cases OK HMB temperature: stream 25: 6.9 - 27.0 degC within 6.9 - 27.0 degC (design None) INFO HMB scope: stream 25: flow + temperature checked only - see remarks OK dates: available 2027-04-30, needed 2027-10-01: float 154 d |

## TP-CW2  Outfall diffuser

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / marine |
| --- | --- |
| Medium / location | seawater / About 350 m offshore, at least 250 m from the intake (E 260.0, N -410.0, EL -8.00 m) |
| Size / connection | - / Outfall diffuser about 350 m offshore at -8 m |
| Scope break | Owner: marine permit and discharge permit (EIA conditions). Contractor: outfall pipeline and diffuser; treated effluents (SC-020, SC-057) join the outfall upstream of the discharge monitoring. |
| Owner side | Marine permit |
| Contractor side | Outfall pipeline and diffuser |
| Isolation | - |
| Protection | - |
| Operating envelope | - to - barg; 12 to 34 degC |
| Flow | normal 36,050.00 / max 40,000.00 m3/h (density 1025.0 kg/m3) |
| HMB envelope (all cases) | stream 26 (flow_temperature check): 10196.80-10196.80 kg/s, 0.687-0.687 barg, 14.1-33.4 degC |
| Quality / specification | requirement:ER-08.04, requirement:ER-08.05, source:SRC-OWNR-0007 |
| Dates | available by 2027-04-30; needed by 2027-10-01 |
| Scope items | SC-016, SC-020, SC-057 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Remarks | Discharge limits: <= 3 K excess at the edge of the 100 m mixing zone, residual chlorine <= 0.1 mg/l; pressure at the diffuser is hydrostatic (HMB pressure check not applicable). |
| Checks (engine) | OK completeness: marine: complete OK HMB flow: stream 26 max 10196.80 kg/s (WIN-NG-100) <= capacity 11388.89 kg/s (margin +10.5 %), 9 cases OK HMB temperature: stream 26: 14.1 - 33.4 degC within 12.0 - 34.5 degC (design None) INFO HMB scope: stream 26: flow + temperature checked only - see remarks OK dates: available 2027-04-30, needed 2027-10-01: float 154 d |

## TP-D1  Storm water discharge

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / civil |
| --- | --- |
| Medium / location | storm water / Western stream channel (max 2 m3/s) or to sea (E 0.0, N 150.0, EL +13.00 m) |
| Size / connection | - / Contractor outlet structure with energy dissipation at the western stream channel |
| Scope break | Owner: water authority consent for the discharge. Contractor: separate clean/oily drainage, oil interceptors (ER-09.06), outlet structure on the plot boundary and the channel protection within 5 m of the outlet. |
| Owner side | Water authority consent |
| Contractor side | Site drainage, oil interceptors, outlet structure |
| Isolation | - |
| Protection | - |
| Flow | normal - / max 2.00 m3/s (density 1000.0 kg/m3) |
| Quality / specification | requirement:ER-09.06, source:SRC-OWNR-0007 |
| Dates | available by 2026-11-02; needed by 2027-01-15 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: civil: complete OK dates: available 2026-11-02, needed 2027-01-15: float 74 d |

## TP-E1  Grid connection 380 kV

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / electrical |
| --- | --- |
| Medium / location | electricity / Line gantry at the north-west corner (E 30.0, N 290.0, EL +15.00 m) |
| Size / connection | 380 kV, 2 circuits / Line-side terminals of the Contractor's tension insulator strings on the gantry |
| Scope break | Owner (line contractor): OHL, conductors and OPGW strung to the tension insulator strings on the Contractor's line gantry, incl. the line clamps. Contractor: gantry, insulator strings and hardware, jumpers and downleads to the GIS outdoor bushings, surge arresters, OPGW joint box on the gantry and fibre to the telecom room. |
| Owner side | Double-circuit 380 kV OHL up to the dead-end tower, conductors to the gantry |
| Contractor side | Gantry, GIS switchyard, protection and metering |
| Isolation | Contractor GIS line bay circuit breaker, line disconnector and line earthing switch; Owner/TSO breaker at the remote end (Kiyi substation). |
| Protection | Export limiter in the plant control system: 640 MW net at the 380 kV revenue meters (TQ-027); line differential 87L main 1 / main 2 with the remote end (plant end by the Contractor, remote end by the Owner), settings coordinated with the TSO (ER-18.02). |
| Metering | Revenue metering class 0.2S on both line bays (SC-035), TSO approved. |
| Flow | normal - / max 640.00 MW - actively limited |
| Electrical | 380.00 kV (342.0-420.0 kV); Isc 50.0 kA, rating 50.0 kA |
| HMB power | net |
| Quality / specification | source:SRC-OWNR-0006, requirement:ER-11.01 |
| Conditions (text) | 380 kV nominal, 420 kV highest; 360-410 kV normal, 342-420 kV up to 30 min; 49.0-51.0 Hz; short-circuit 12-40 kA (2029), 50 kA (2035 planning); connection capacity 640 MW export / 40 MW import (ALP-OWN-ELE-001). |
| Dates | available by 2028-07-15; needed by 2028-07-22 |
| Scope items | SC-030, SC-031, SC-048 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0009, source:SRC-OWNR-0010 |
| Remarks | Short-circuit values include the Alpilla generators' contribution (TSO, TQ-031). Reactive capability per ER-04.08 at the generator terminals (TQ-032). |
| Checks (engine) | OK completeness: electrical: complete OK short circuit: prospective 50.0 kA <= rating 50.0 kA INFO HMB power: max net 665.3 MW (WIN-NG-100) > 640 MW (margin -3.9 %); limited to 640 MW at this point: Export limiter in the plant control system: 640 MW net at the 380 kV revenue meters (TQ-027); line differential 87L main 1 / main 2 with the remote end (plant end by the Contractor, remote end by the Owner), settings coordinated with the TSO (ER-18.02). INFO dates: available 2028-07-15, needed 2028-07-22: float 7 d (tight) |

## TP-E2  Construction power

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / electrical |
| --- | --- |
| Medium / location | electricity / North gate (E 200.0, N 300.0, EL +15.00 m) |
| Size / connection | 34.5 kV / 5 MVA / 34.5 kV cable terminations at the outgoing side of the utility metering kiosk |
| Scope break | Owner (distribution company): 34.5 kV line/cable to the metering kiosk at the north gate, incl. the utility meter and load-break switch. Contractor: cable from the kiosk outgoing terminals, 34.5 kV ring main unit and construction substations. |
| Owner side | 34.5 kV connection, 5 MVA, metering |
| Contractor side | Construction substations and distribution |
| Isolation | Utility load-break switch in the kiosk; Contractor RMU incoming switch with earthing switch. |
| Protection | Contractor RMU incoming circuit breaker (overcurrent / earth fault) graded with the utility. |
| Metering | Utility meter in the kiosk (construction energy paid by the Contractor, SC-045). |
| Flow | normal - / max 5.00 MVA |
| Electrical | 34.50 kV (31.1-38.0 kV); Isc 12.5 kA, rating 16.0 kA |
| Conditions (text) | 34.5 kV +/- 10 %, 5 MVA, prospective short-circuit 12.5 kA (distribution company). |
| Dates | available by 2027-02-28; needed by 2027-03-15 |
| Scope items | SC-045, SC-045 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0009, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: electrical: complete OK short circuit: prospective 12.5 kA <= rating 16.0 kA OK dates: available 2027-02-28, needed 2027-03-15: float 15 d |

## TP-G1  Natural gas supply

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / process |
| --- | --- |
| Medium / location | natural gas / North-east plot corner, flange at EL +14.0 (E 380.0, N 300.0, EL +14.00 m) |
| Size / connection | 16 in (DN400), CL600 / ASME B16.5 CL600 RF weld-neck flange, 16 in |
| Scope break | Owner: spur line, tap valve station, remotely operable isolation valve and monolithic insulating joint; scope break at the downstream flange of the insulating joint. Contractor: counter-flange, gasket, stud bolts and everything downstream (gas receiving and metering station, SC-028). The Owner's cathodic protection ends at the insulating joint; plant earthing starts downstream. |
| Owner side | 16-inch spur line (4.5 km), tap valve station, isolation valve and insulating joint |
| Contractor side | Gas receiving and metering station from the inlet flange |
| Isolation | Owner boundary isolation valve (operated by the network operator); Contractor station inlet ESD valve. |
| Protection | Owner pipeline MAOP 75 barg; the Contractor's station is designed for 75 barg up to the regulators. |
| Metering | Fiscal metering by the Contractor in the station, approved by the network operator (ER-18.03). |
| Design | 75.0 barg / 50 degC |
| Operating envelope | 45.0 to 70.0 barg; 5 to 25 degC |
| Flow | normal 101,600.00 / max 115,000.00 Sm3/h (density 0.7325 kg/m3) |
| Quality / specification | source:SRC-OWNR-0003, requirement:ER-03.06 |
| Conditions (text) | Normal 55-65 barg; minimum 45 barg for full load; exceptional 40 barg up to 72 h/year (GT load limited, ER-03.03); MOP 70 / MAOP 75 barg; 5-25 degC; 115,000 Sm3/h firm (density 0.7325 kg/Sm3 at 15 degC, reference gas). |
| Dates | available by 2028-06-30; needed by 2028-08-15 |
| Scope items | SC-028, SC-027, SC-047 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0009, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: process: complete OK dates: available 2028-06-30, needed 2028-08-15: float 46 d |

## TP-L1  LDO supply

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / process |
| --- | --- |
| Medium / location | light diesel oil / North gate (road tankers) (E 200.0, N 300.0, EL +15.00 m) |
| Size / connection | 4 in tanker coupling (API RP 1004 bottom loading / dry-break) / Dry-break tanker coupling at the Contractor's unloading bays |
| Scope break | Owner (LDO supplier): road tankers delivered to the unloading bays, tanker hoses and coupling halves on the tanker, first fill of the storage tanks (SC-055). Contractor: unloading bays, coupling halves on the plant side, pumps, metering, storage and treatment. |
| Owner side | LDO supply contract (up to 25 trucks/day), first fill |
| Contractor side | Unloading station and storage |
| Isolation | Tanker bottom valve (supplier); Contractor unloading valve and ESD at each bay. |
| Protection | Contractor unloading pumps relief; bay earthing and overfill interlock (tanker earthing permissive). |
| Metering | Contractor unloading flow meter per bay; tanker delivery notes (Owner supplier). |
| Design | 10.0 barg / 50 degC |
| Operating envelope | 0.000 to 3.0 barg; 0 to 40 degC |
| Flow | normal 100.00 / max 150.00 m3/h (density 835.0 kg/m3) |
| Quality / specification | source:SRC-OWNR-0004, requirement:ER-03.07 |
| Conditions (text) | Up to 25 trucks/day (about 30 m3 each); 4 bays at about 100 m3/h each unloading pump set; LDO per TS EN 590 based specification. |
| Dates | available by 2028-09-01; needed by 2028-11-01 |
| Scope items | SC-052, SC-055, SC-052 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: process: complete OK dates: available 2028-09-01, needed 2028-11-01: float 61 d |

## TP-M1  Temporary barge landing

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / marine |
| --- | --- |
| Medium / location | heavy transport / Public coastal strip south of the plot (E 120.0, N -40.0, EL +1.50 m) |
| Size / connection | - / Temporary ro-ro barge landing on the public coastal strip |
| Scope break | Owner: coastal permit (application by 2027-04-30 based on the Contractor's design). Contractor: design, construction, operation, removal and reinstatement of the barge landing; heavy haul road to the site. |
| Owner side | Coastal permit: application by 2027-04-30 if the Contractor's permit design is received by 2027-03-31; permit targeted by 2027-09-30 |
| Contractor side | Design, construction, operation and removal of the landing; marine works only 1 October - 30 April |
| Isolation | - |
| Protection | - |
| Conditions (text) | Heaviest pieces (IEC-ALP-REQ-001 section 10): GT core engine 405 t (13.2 x 5.9 x 5.6 m, about 480 t gross on SPMT), GT generator stator 340 t, GT GSU 268 t; landing and haul road designed for 480 t gross SPMT loads. |
| Dates | available by 2027-09-30; needed by 2027-11-01 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0007, source:SRC-OWNR-0009, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: marine: complete OK dates: available 2027-09-30, needed 2027-11-01: float 32 d |

## TP-R1  Road access

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / land_access |
| --- | --- |
| Medium / location | road / North gate (E 200.0, N 300.0, EL +15.00 m) |
| Size / connection | - / Existing 6 m asphalt road at the north gate (E 200, N 300) |
| Scope break | Owner: existing road to the state road up to the north gate. Contractor: site roads from the gate, road condition survey before and after construction and repair of construction damage; abnormal loads via TP-M1. |
| Owner side | Existing 6 m asphalt road to the state road |
| Contractor side | Site roads and gate |
| Isolation | - |
| Protection | - |
| Conditions (text) | 6 m asphalt, state road bridges limited to 120 t gross vehicle weight; components above about 90 t via the barge landing TP-M1 (ALP-OWN-GEN-001 section 3). |
| Dates | available by 2026-11-02; needed by 2026-11-16 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0009, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: land_access: complete OK dates: available 2026-11-02, needed 2026-11-16: float 14 d |

## TP-S1  Sanitary wastewater

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / permit_service |
| --- | --- |
| Medium / location | sewage / None - no municipal sewer available |
| Size / connection | - / - |
| Scope break | No physical connection (no municipal sewer). The Contractor's packaged sanitary treatment plant (SC-057) discharges treated effluent into the outfall (TP-CW2) within the Owner's discharge permit. |
| Owner side | Nothing (no sewer) |
| Contractor side | Packaged sanitary treatment plant (SC-057); treated effluent to the outfall |
| Isolation | - |
| Protection | - |
| Quality / specification | source:SRC-OWNR-0007 |
| Dates | available by -; needed by - |
| Scope items | SC-057, SC-020 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: permit_service: complete |

## TP-T1  Telecommunication

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / control |
| --- | --- |
| Medium / location | fibre / North gate (E 200.0, N 300.0, EL +14.00 m) |
| Size / connection | - / 2 x HDPE ducts with draw pits at the plot boundary (two operators) |
| Scope break | Owner: operators' fibre in ducts up to the boundary draw pits. Contractor: ducts and fibre from the draw pits to the telecom room, telecom equipment. |
| Owner side | Fibre ducts of two operators to the plot boundary |
| Contractor side | Site telecom network and SCADA links |
| Isolation | - |
| Protection | - |
| Dates | available by 2027-06-30; needed by 2028-05-01 |
| Scope items | SC-035, SC-044 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0009, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: control: complete OK dates: available 2027-06-30, needed 2028-05-01: float 306 d |

## TP-T2  Emission data link to the environmental authority

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / control |
| --- | --- |
| Medium / location | data / CEMS data logger in the control building |
| Size / connection | - / Authority continuous emission monitoring protocol over the public network (VPN), per the Ministry's data-link rules |
| Scope break | Owner: registration with the Ministry of Environment continuous emission monitoring centre, the operator credentials and the data-link agreement. Contractor: CEMS (SC-038), data acquisition system, firewall and VPN router in the control building; scope break at the router's public network port. |
| Owner side | Registration of the plant with the Ministry's continuous emission monitoring centre, credentials, connection agreement |
| Contractor side | CEMS, data acquisition and the data link (SC-038) up to the Ministry server interface |
| Isolation | - |
| Protection | - |
| Dates | available by 2028-08-01; needed by 2028-10-02 |
| Scope items | SC-038 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: control: complete OK dates: available 2028-08-01, needed 2028-10-02: float 62 d |

## TP-T3  TSO SCADA and revenue metering link

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / control |
| --- | --- |
| Medium / location | data / TSO RTU and metering cubicle in the control building |
| Size / connection | - / IEC 60870-5-104 over OPGW fibre (TP-E1) and a second path via the operator fibre (TP-T1) |
| Scope break | Owner/TSO: signal list, IEC 60870-5-104 profile, TSO end equipment and the OPGW up to the joint box on the Contractor's gantry. Contractor: joint box, fibre to the telecom room, RTU, revenue meters and SCADA tests with the TSO. |
| Owner side | TSO signal list and protocol, TSO end of the link, OPGW on the Owner's line |
| Contractor side | RTU, revenue meters, fibre from the gantry joint box, telecom equipment (SC-035) |
| Isolation | - |
| Protection | - |
| Dates | available by 2028-05-01; needed by 2028-06-01 |
| Scope items | SC-035 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | source:SRC-OWNR-0005, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: control: complete OK dates: available 2028-05-01, needed 2028-06-01: float 31 d |

## TP-W1  Potable water

| Contract / category | ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant / utility |
| --- | --- |
| Medium / location | water / North gate (E 200.0, N 300.0, EL +14.00 m) |
| Size / connection | DN150 / DN150 PN16 EN 1092-1 flange at the outlet of the Owner's meter pit valve |
| Scope break | Owner: municipal main, connection, meter, backflow preventer and outlet valve in the meter pit at the north gate. Contractor: from the outlet flange (counter-flange, gasket, bolts) to storage and distribution. |
| Owner side | DN150 municipal main connection and meter, 3 barg, 20 m3/h |
| Contractor side | Potable water storage and distribution |
| Isolation | Owner valves before and after the meter; Contractor isolation valve downstream. |
| Protection | Owner backflow preventer (TS EN 1717). |
| Metering | Municipal meter in the pit. |
| Design | 10.0 barg / 30 degC |
| Operating envelope | 2.5 to 6.0 barg; 5 to 25 degC |
| Flow | normal 10.00 / max 20.00 m3/h (density 1000.0 kg/m3) |
| Quality / specification | source:SRC-OWNR-0005 |
| Conditions (text) | 2.5-6.0 barg at the meter outlet, 20 m3/h (municipal supply), potable quality per the Turkish drinking water regulation. |
| Dates | available by 2027-02-28; needed by 2027-03-15 |
| Scope items | SC-043, SC-045 |
| Agreement | agreed by Owner, Istanbul EPC in TQ-030 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-OWNR-0005, source:SRC-OWNR-0009, source:SRC-OWNR-0010 |
| Checks (engine) | OK completeness: utility: complete OK dates: available 2027-02-28, needed 2027-03-15: float 15 d |

## IF-01  Natural gas to GT

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | natural gas / performance gas heater inlet flange |
| Size / connection | 12 in (DN300) CL600 / ASME B16.5 CL600 RF weld-neck flange |
| Scope break | IEC supplies the performance gas heater inlet flange; EPC supplies the counter-flange, gasket (spiral wound, 316L/graphite), stud bolts and the pipe support nearest the flange, and makes the joint. Hydrotest up to the flange by each party; joint leak test with gas-in by EPC. |
| Istanbul EPC side | EPC: gas from EPC gas receiving/metering station |
| Imaginary Electric side | IEC: performance gas heater inlet flange |
| Isolation | EPC: gas station outlet ESD valve (fail-closed, SIL 2, closed by the TCS gas trip) and manual valve with spectacle blind upstream of IF-01. IEC: gas skid stop and control valves. |
| Protection | EPC gas station pressure control: monitor + active regulator, slam-shut set 46 barg, token relief 44 barg; downstream design 63 barg (EN 12186 / ASME B31.8). |
| Metering | Fiscal metering (ultrasonic 2 x 100 % + gas chromatograph) in the EPC gas station; IEC skid flow meter for control only. |
| Design | 63.0 barg / 80 degC |
| Operating envelope | 36.5 to 41.0 barg; 5 to 40 degC |
| Flow | normal 20.67 / max 23.00 kg/s |
| HMB envelope (all cases) | stream 2 (full check): 8.68-22.36 kg/s, 36.987-36.987 barg, 25.0-25.0 degC |
| Fed from | TP-G1 (chain dp 4.7 bar) |
| Quality / specification | requirement:ER-03.06, source:SRC-OWNR-0003, source:SRC-EPCE-0010 |
| Conditions (text) | Pressure rate of change <= 0.7 bar/s; >= 28 K superheat above hydrocarbon and water dew points; filtration 3 um absolute; below 36.5 barg the TCS load limiter applies (DEC-EPCE-0003). |
| Dates | available by 2028-08-31; needed by 2028-09-18 |
| Scope items | SC-029 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 2 max 22.36 kg/s (WIN-NG-100) <= capacity 23.00 kg/s (margin +2.8 %), 8 cases OK HMB pressure: stream 2: 36.987 - 36.987 barg within 36.5 - 41.0 barg (design 63.0) OK HMB temperature: stream 2: 25.0 - 25.0 degC within 5.0 - 40.0 degC (design 80.0) OK chain pressure: TP-G1 min 45.0 barg - 4.7 bar = 40.30 barg >= required 36.5 barg OK chain design: TP-G1 design 75 barg > 63.0 barg here: protected - EPC gas station pressure control: monitor + active regulator, slam-shut set 46 barg, token relief 44 barg; downstream de OK chain flow: capacity here 23.00 kg/s <= TP-G1 23.40 kg/s OK dates: available 2028-08-31, needed 2028-09-18: float 18 d |

## IF-02  LDO to GT

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | LDO / liquid fuel skid inlet flange |
| Size / connection | 6 in (DN150) CL150 / ASME B16.5 CL150 RF flange |
| Scope break | IEC supplies the liquid fuel skid inlet flange; EPC supplies counter-flange, gasket, bolts, the last pipe support and the joint. |
| Istanbul EPC side | EPC: LDO forwarding/treatment system |
| Imaginary Electric side | IEC: liquid fuel skid inlet flange |
| Isolation | EPC: LDO ESD valve (fail-closed) and manual valve with spectacle blind at the skid boundary. IEC: skid stop valve. |
| Protection | EPC forwarding pumps: discharge relief to tank set 12 barg (< 16 barg design). |
| Metering | EPC Coriolis meter on the forwarding skid (consumption and performance tests). |
| Design | 16.0 barg / 60 degC |
| Operating envelope | 3.0 to 6.0 barg; 10 to 45 degC |
| Flow | normal 22.41 / max 24.00 kg/s |
| HMB envelope (all cases) | stream 27 (full check): 22.41-22.41 kg/s, 3.987-3.987 barg, 30.0-30.0 degC |
| Quality / specification | requirement:ER-03.07, source:SRC-OWNR-0004, source:SRC-EPCE-0010 |
| Conditions (text) | LDO treated by the EPC to the GT inlet limits (ER-03.07); filtration 5 um. |
| Dates | available by 2028-11-15; needed by 2028-12-01 |
| Scope items | SC-053, SC-054 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 27 max 22.41 kg/s (SRC-LDO-100) <= capacity 24.00 kg/s (margin +6.6 %), 1 cases OK HMB pressure: stream 27: 3.987 - 3.987 barg within 3.0 - 6.0 barg (design 16.0) OK HMB temperature: stream 27: 30.0 - 30.0 degC within 10.0 - 45.0 degC (design 60.0) OK dates: available 2028-11-15, needed 2028-12-01: float 16 d |

## IF-03  Demin water for water injection

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | demin water / water injection skid inlet |
| Size / connection | 4 in (DN100) CL150 / ASME B16.5 CL150 RF flange |
| Scope break | IEC supplies the water injection skid inlet flange (skid with high-pressure pumps by IEC); EPC supplies counter-flange, gasket, bolts and the demin water forwarding pumps. |
| Istanbul EPC side | EPC: demin water storage/pumps |
| Imaginary Electric side | IEC: water injection skid inlet |
| Isolation | EPC manual isolation valve and spectacle blind; IEC skid inlet valve. |
| Protection | EPC demin forwarding pumps shut-off head <= 12 barg (< 16 barg design). |
| Design | 16.0 barg / 50 degC |
| Operating envelope | 3.0 to 6.0 barg; 10 to 40 degC |
| Flow | normal 13.44 / max 15.00 kg/s |
| HMB envelope (all cases) | stream 28 (flow_temperature check): 13.44-13.44 kg/s, 58.987-58.987 barg, 30.0-30.0 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | Water/fuel ratio 0.60 on LDO (TQ-IEC-018). HMB stream 28 is at the IEC skid discharge (60 bar(a)); pressure at IF-03 is 3.0-6.0 barg. |
| Dates | available by 2028-11-15; needed by 2028-12-01 |
| Scope items | SC-054 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Remarks | HMB pressure check not applicable: PER-003 stream 28 is downstream of the IEC injection pumps (TQ-IEC-021 item 3); the injection pump power is part of the IEC GT auxiliaries. |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 28 max 13.44 kg/s (SRC-LDO-100) <= capacity 15.00 kg/s (margin +10.4 %), 1 cases OK HMB temperature: stream 28: 30.0 - 30.0 degC within 10.0 - 40.0 degC (design 50.0) INFO HMB scope: stream 28: flow + temperature checked only - see remarks OK dates: available 2028-11-15, needed 2028-12-01: float 16 d |

## IF-04  Compressor wash water

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | demin water / wash skid inlet |
| Size / connection | 2 in (DN50) CL150 / ASME B16.5 CL150 RF flange |
| Scope break | IEC wash skid inlet flange; EPC demin water line, counter-flange, gasket and bolts. |
| Istanbul EPC side | EPC: demin water |
| Imaginary Electric side | IEC: wash skid inlet |
| Isolation | EPC manual valve; IEC skid inlet valve. |
| Protection | EPC demin pumps shut-off <= 8 barg. |
| Design | 10.0 barg / 50 degC |
| Operating envelope | 3.0 to 6.0 barg; 10 to 40 degC |
| Flow | normal 5.00 / max 10.00 m3/h (density 1000.0 kg/m3) |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | 5 m3 per wash (off-line), tank filling at up to 10 m3/h. |
| Dates | available by 2028-09-15; needed by 2028-12-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete OK dates: available 2028-09-15, needed 2028-12-15: float 91 d |

## IF-05  HP steam

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / HRSG HP SH outlet stop valve, weld end |
| Size / connection | 12 in P91 (SA-335 P91) / butt-weld end ASME B16.25, IEC pup piece 300 mm |
| Scope break | IEC supplies the HP SH outlet stop valve with a 300 mm pup piece (matching material and wall); the field weld, its PWHT and 100 % RT/UT are by EPC, witnessed by IEC. |
| Istanbul EPC side | EPC: main steam piping (EPC) |
| Imaginary Electric side | IEC: HRSG HP SH outlet stop valve, weld end |
| Isolation | IEC HP SH outlet motor-operated stop valve and non-return valve. |
| Protection | IEC HRSG HP SH safety valves set <= 196 bar(a), electromatic relief 194 bar(a). |
| Design | 209.0 barg / 610 degC |
| Operating envelope | 59.0 to 192.0 barg; 560 to 600 degC |
| Flow | normal 100.16 / max 105.00 kg/s |
| HMB envelope (all cases) | stream 6 (full check): 50.31-103.34 kg/s, 92.706-191.071 barg, 577.4-600.0 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | Sliding pressure 60-193 bar(a); attemperation to 600 degC. |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 6 max 103.34 kg/s (WIN-NG-100) <= capacity 105.00 kg/s (margin +1.6 %), 9 cases OK HMB pressure: stream 6: 92.706 - 191.071 barg within 59.0 - 192.0 barg (design 209.0) OK HMB temperature: stream 6: 577.4 - 600.0 degC within 560.0 - 600.0 degC (design 610.0) OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-06  HP steam

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / ST main stop valve inlet, weld end |
| Size / connection | 12 in P91 (SA-335 P91) / butt-weld end ASME B16.25, IEC pup piece 300 mm |
| Scope break | IEC supplies the ST main stop valve with pup piece; field weld, PWHT and NDT by EPC. |
| Istanbul EPC side | EPC: main steam piping (EPC) |
| Imaginary Electric side | IEC: ST main stop valve inlet, weld end |
| Isolation | IEC main stop valve (ST trip). |
| Protection | Upstream HRSG HP SH safety valves (IF-05) <= 196 bar(a); MSV casing design 215 bar(a) / 610 degC (TQ-IEC-021 item 1). |
| Design | 214.0 barg / 610 degC |
| Operating envelope | 52.0 to 186.0 barg; 560 to 600 degC |
| Flow | normal 100.16 / max 105.00 kg/s |
| HMB envelope (all cases) | stream 7 (full check): 50.31-103.34 kg/s, 89.936-185.369 barg, 575.9-598.5 degC |
| Fed from | IF-05 (chain dp 6.0 bar) |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | ST rated inlet 180 bar(a) / 598 degC per IEC 60045-1; main steam line pressure drop <= 6.0 bar at 105 kg/s. |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 7 max 103.34 kg/s (WIN-NG-100) <= capacity 105.00 kg/s (margin +1.6 %), 9 cases OK HMB pressure: stream 7: 89.936 - 185.369 barg within 52.0 - 186.0 barg (design 214.0) OK HMB temperature: stream 7: 575.9 - 598.5 degC within 560.0 - 600.0 degC (design 610.0) OK chain pressure: IF-05 min 59.0 barg - 6.0 bar = 53.00 barg >= required 52.0 barg OK chain flow: capacity here 105.00 kg/s <= IF-05 105.00 kg/s OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-07  Cold reheat

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / HP turbine exhaust, weld end |
| Size / connection | 24 in SA-335 P22 / butt-weld end, IEC pup piece |
| Scope break | IEC supplies the HP turbine exhaust nozzle with pup piece and the CRH non-return valve; field weld by EPC. |
| Istanbul EPC side | EPC: cold reheat piping (EPC) |
| Imaginary Electric side | IEC: HP turbine exhaust, weld end |
| Isolation | IEC CRH non-return valve (power assisted). |
| Protection | Reheater safety valves on the HRSG (IEC). |
| Design | 51.0 barg / 420 degC |
| Operating envelope | 18.0 to 41.0 barg; 340 to 395 degC |
| Flow | normal 100.16 / max 105.00 kg/s |
| HMB envelope (all cases) | stream 8 (full check): 50.31-103.34 kg/s, 19.633-40.476 barg, 357.1-387.6 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 8 max 103.34 kg/s (WIN-NG-100) <= capacity 105.00 kg/s (margin +1.6 %), 9 cases OK HMB pressure: stream 8: 19.633 - 40.476 barg within 18.0 - 41.0 barg (design 51.0) OK HMB temperature: stream 8: 357.1 - 387.6 degC within 340.0 - 395.0 degC (design 420.0) OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-08  Cold reheat

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / HRSG reheater inlet, weld end |
| Size / connection | 24 in SA-335 P22 / butt-weld end, IEC pup piece |
| Scope break | IEC supplies the HRSG reheater inlet with pup piece and the CRH safety valves; field weld by EPC. |
| Istanbul EPC side | EPC: cold reheat piping (EPC) |
| Imaginary Electric side | IEC: HRSG reheater inlet, weld end |
| Isolation | None at the HRSG inlet (CRH non-return valve at IF-07). |
| Protection | IEC cold reheat safety valves set 50 bar(a). |
| Design | 51.0 barg / 420 degC |
| Operating envelope | 17.0 to 41.0 barg; 340 to 395 degC |
| Flow | normal 100.16 / max 105.00 kg/s |
| HMB envelope (all cases) | stream 9 (full check): 50.31-103.34 kg/s, 19.289-39.754 barg, 356.1-386.6 degC |
| Fed from | IF-07 (chain dp 1.0 bar) |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 9 max 103.34 kg/s (WIN-NG-100) <= capacity 105.00 kg/s (margin +1.6 %), 9 cases OK HMB pressure: stream 9: 19.289 - 39.754 barg within 17.0 - 41.0 barg (design 51.0) OK HMB temperature: stream 9: 356.1 - 386.6 degC within 340.0 - 395.0 degC (design 420.0) OK chain pressure: IF-07 min 18.0 barg - 1.0 bar = 17.00 barg >= required 17.0 barg OK chain flow: capacity here 105.00 kg/s <= IF-07 105.00 kg/s OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-09  Hot reheat

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / HRSG reheater outlet stop valve, weld end |
| Size / connection | 28 in P91 (SA-335 P91) / butt-weld end, IEC pup piece |
| Scope break | IEC supplies the HRSG reheater outlet stop valve with pup piece; field weld, PWHT, NDT by EPC. |
| Istanbul EPC side | EPC: hot reheat piping (EPC) |
| Imaginary Electric side | IEC: HRSG reheater outlet stop valve, weld end |
| Isolation | IEC HRH outlet stop valve. |
| Protection | IEC hot reheat safety valves set <= 48 bar(a). |
| Design | 49.0 barg / 610 degC |
| Operating envelope | 17.0 to 38.5 barg; 550 to 600 degC |
| Flow | normal 117.50 / max 125.00 kg/s |
| HMB envelope (all cases) | stream 11 (full check): 60.92-121.56 kg/s, 18.294-37.783 barg, 566.0-600.0 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 11 max 121.56 kg/s (WIN-NG-100) <= capacity 125.00 kg/s (margin +2.8 %), 9 cases OK HMB pressure: stream 11: 18.294 - 37.783 barg within 17.0 - 38.5 barg (design 49.0) OK HMB temperature: stream 11: 566.0 - 600.0 degC within 550.0 - 600.0 degC (design 610.0) OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-10  Hot reheat

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / ST IP stop-control valve inlet |
| Size / connection | 28 in P91 (SA-335 P91) / butt-weld end, IEC pup piece |
| Scope break | IEC supplies the ST IP stop/control valve with pup piece; field weld, PWHT, NDT by EPC. |
| Istanbul EPC side | EPC: hot reheat piping (EPC) |
| Imaginary Electric side | IEC: ST IP stop-control valve inlet |
| Isolation | IEC IP stop valve (ST trip). |
| Protection | Upstream HRH safety valves (IF-09) <= 48 bar(a); IP valve casing design 52 bar(a) / 610 degC (TQ-IEC-021 item 1). |
| Design | 51.0 barg / 610 degC |
| Operating envelope | 15.5 to 38.5 barg; 550 to 600 degC |
| Flow | normal 117.50 / max 125.00 kg/s |
| HMB envelope (all cases) | stream 12 (full check): 60.92-121.56 kg/s, 17.561-36.331 barg, 564.5-598.5 degC |
| Fed from | IF-09 (chain dp 1.5 bar) |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 12 max 121.56 kg/s (WIN-NG-100) <= capacity 125.00 kg/s (margin +2.8 %), 9 cases OK HMB pressure: stream 12: 17.561 - 36.331 barg within 15.5 - 38.5 barg (design 51.0) OK HMB temperature: stream 12: 564.5 - 598.5 degC within 550.0 - 600.0 degC (design 610.0) OK chain pressure: IF-09 min 17.0 barg - 1.5 bar = 15.50 barg >= required 15.5 barg OK chain flow: capacity here 125.00 kg/s <= IF-09 125.00 kg/s OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-11  LP steam

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / HRSG LP SH outlet stop valve |
| Size / connection | 20 in SA-106 C / butt-weld end |
| Scope break | IEC supplies the LP SH outlet stop valve with pup piece; field weld by EPC. |
| Istanbul EPC side | EPC: LP steam piping (EPC) |
| Imaginary Electric side | IEC: HRSG LP SH outlet stop valve |
| Isolation | IEC LP SH outlet stop valve and non-return valve. |
| Protection | IEC LP SH safety valve set 8.0 bar(a). |
| Design | 9.0 barg / 330 degC |
| Operating envelope | 1.5 to 5.0 barg; 210 to 260 degC |
| Flow | normal 11.39 / max 16.50 kg/s |
| HMB envelope (all cases) | stream 13 (full check): 6.36-15.27 kg/s, 1.783-4.586 barg, 218.7-251.8 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 13 max 15.27 kg/s (SRC-LDO-100) <= capacity 16.50 kg/s (margin +7.5 %), 9 cases OK HMB pressure: stream 13: 1.783 - 4.586 barg within 1.5 - 5.0 barg (design 9.0) OK HMB temperature: stream 13: 218.7 - 251.8 degC within 210.0 - 260.0 degC (design 330.0) OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-12  LP steam

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / ST LP admission valve inlet |
| Size / connection | 20 in SA-106 C / butt-weld end |
| Scope break | IEC supplies the ST LP admission valve with pup piece; field weld by EPC. |
| Istanbul EPC side | EPC: LP steam piping (EPC) |
| Imaginary Electric side | IEC: ST LP admission valve inlet |
| Isolation | IEC LP admission stop valve. |
| Protection | Upstream LP SH safety valve (IF-11) 8.0 bar(a); admission valve casing design 10 bar(a) / 330 degC (TQ-IEC-021 item 1). |
| Design | 9.0 barg / 330 degC |
| Operating envelope | 1.1 to 5.0 barg; 210 to 260 degC |
| Flow | normal 11.39 / max 16.50 kg/s |
| HMB envelope (all cases) | stream 14 (full check): 6.36-15.27 kg/s, 1.589-4.219 barg, 217.7-250.8 degC |
| Fed from | IF-11 (chain dp 0.4 bar) |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 14 max 15.27 kg/s (SRC-LDO-100) <= capacity 16.50 kg/s (margin +7.5 %), 9 cases OK HMB pressure: stream 14: 1.589 - 4.219 barg within 1.1 - 5.0 barg (design 9.0) OK HMB temperature: stream 14: 217.7 - 250.8 degC within 210.0 - 260.0 degC (design 330.0) OK chain pressure: IF-11 min 1.5 barg - 0.4 bar = 1.10 barg >= required 1.1 barg OK chain flow: capacity here 16.50 kg/s <= IF-11 16.50 kg/s OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-13  HP / IP / LP bypass valves

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / water / valves supplied loose by IEC (incl. desuperheating) |
| Size / connection | HP 12 in / IP 28 in / LP 20 in (per valve datasheets) / butt-weld ends; spray water flanges CL2500 (HP) / CL600 (IP, LP) |
| Scope break | Loose supply: IEC supplies HP, IP and LP bypass valves with desuperheaters (free issue to site); EPC installs them in its piping, supplies the spray water lines from the BFP discharge/interstage and CEP discharge and all welds. |
| Istanbul EPC side | EPC: installation in EPC piping, spray water from BFP/CEP (EPC) |
| Imaginary Electric side | IEC: valves supplied loose by IEC (incl. desuperheating) |
| Isolation | EPC isolation on the spray water lines; bypass valves close on loss of spray water (IEC logic). |
| Protection | HP bypass downstream design 52 bar(a) (CRH); IP/LP bypass downstream 16 bar(a) (IF-14). |
| Design | 214.0 barg / 610 degC |
| Operating envelope | 1.0 to 192.0 barg; 150 to 600 degC |
| Flow | normal - / max 125.00 kg/s |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | Inlet side most onerous (HP bypass inlet); delivery of the loose valves by 2028-02-01 for piping erection. |
| Dates | available by 2028-02-01; needed by 2028-03-01 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK dates: available 2028-02-01, needed 2028-03-01: float 29 d |

## IF-14  Bypass steam to condenser

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | steam / condenser neck dump devices (IEC) |
| Size / connection | 2 x 36 in + 1 x 28 in / butt-weld end at the condenser neck dump devices |
| Scope break | IEC supplies the dump devices in the condenser neck with weld ends; EPC supplies the IP/LP bypass downstream piping and the welds. |
| Istanbul EPC side | EPC: IP/LP bypass downstream piping (EPC) |
| Imaginary Electric side | IEC: condenser neck dump devices (IEC) |
| Isolation | Bypass valves (IF-13). |
| Protection | Condenser rupture discs (IEC) and bypass trip on high condenser pressure. |
| Design | 15.0 barg / 250 degC |
| Operating envelope | -1.0 to 12.0 barg; 40 to 250 degC |
| Flow | normal - / max 141.50 kg/s |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | Start-up and trip only; 100 % HRH + LP flow. |
| Dates | available by 2028-05-01; needed by 2028-06-01 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK dates: available 2028-05-01, needed 2028-06-01: float 31 d |

## IF-15  Condensate from hotwell

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | condensate / hotwell outlet nozzle |
| Size / connection | 20 in (DN500) CL150 / ASME B16.5 CL150 RF flange, vacuum-tight |
| Scope break | IEC hotwell outlet nozzle flange; EPC counter-flange, spiral-wound gasket, bolts and CEP suction piping. |
| Istanbul EPC side | EPC: CEP suction piping (EPC) |
| Imaginary Electric side | IEC: hotwell outlet nozzle |
| Isolation | EPC motor-operated suction valve per CEP. |
| Protection | Full vacuum design both sides. |
| Design | 2.5 barg / 80 degC |
| Operating envelope | -0.995 to -0.900 barg; 15 to 40 degC |
| Flow | normal 128.00 / max 140.00 kg/s |
| HMB envelope (all cases) | stream 17 (full check): 67.28-133.94 kg/s, -0.993--0.952 barg, 17.5-36.5 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | Full vacuum to 3.5 bar(a). |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 17 max 133.94 kg/s (WIN-NG-100) <= capacity 140.00 kg/s (margin +4.3 %), 9 cases OK HMB pressure: stream 17: -0.993 - -0.952 barg within -0.995 - -0.9 barg (design 2.5) OK HMB temperature: stream 17: 17.5 - 36.5 degC within 15.0 - 40.0 degC (design 80.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-16  Condensate to CPH

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | condensate / HRSG CPH inlet |
| Size / connection | 12 in (DN300) CL300 / ASME B16.5 CL300 RF flange |
| Scope break | IEC HRSG condensate preheater inlet flange; EPC condensate line, counter-flange, gasket, bolts. |
| Istanbul EPC side | EPC: condensate line (EPC) |
| Imaginary Electric side | IEC: HRSG CPH inlet |
| Isolation | EPC motor-operated isolation valve. |
| Protection | EPC CEP shut-off head <= 22 bar(a) at maximum speed (< 25 bar(a) design), verified at pump FAT. |
| Design | 24.0 barg / 180 degC |
| Operating envelope | 12.0 to 21.0 barg; 15 to 45 degC |
| Flow | normal 141.37 / max 150.00 kg/s |
| HMB envelope (all cases) | stream 20 (full check): 73.89-147.33 kg/s, 14.487-14.487 barg, 23.0-40.0 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 20 max 147.33 kg/s (WIN-NG-100) <= capacity 150.00 kg/s (margin +1.8 %), 9 cases OK HMB pressure: stream 20: 14.487 - 14.487 barg within 12.0 - 21.0 barg (design 24.0) OK HMB temperature: stream 20: 23.0 - 40.0 degC within 15.0 - 45.0 degC (design 180.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-17  BFP suction

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | feedwater / HRSG LP drum downcomer outlet nozzle |
| Size / connection | 16 in (DN400) CL150 / ASME B16.5 CL150 RF flange |
| Scope break | IEC LP drum downcomer outlet nozzle flange; EPC BFP suction piping, counter-flange, gasket, bolts. |
| Istanbul EPC side | EPC: BFP suction piping (EPC) |
| Imaginary Electric side | IEC: HRSG LP drum downcomer outlet nozzle |
| Isolation | EPC suction isolation valve per BFP. |
| Protection | IEC LP drum safety valves. |
| Design | 9.0 barg / 185 degC |
| Operating envelope | 1.5 to 6.0 barg; 130 to 165 degC |
| Flow | normal 129.98 / max 140.00 kg/s |
| HMB envelope (all cases) | stream 21 (full check): 67.54-134.94 kg/s, 2.059-5.294 barg, 134.3-160.7 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | LP drum normal water level EL +31.5 m; the EPC confirms BFP NPSH with the drum level and suction losses. |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 21 max 134.94 kg/s (WIN-NG-100) <= capacity 140.00 kg/s (margin +3.6 %), 9 cases OK HMB pressure: stream 21: 2.059 - 5.294 barg within 1.5 - 6.0 barg (design 9.0) OK HMB temperature: stream 21: 134.3 - 160.7 degC within 130.0 - 165.0 degC (design 185.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-18  HP feedwater

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | feedwater / HRSG HP ECO1 inlet |
| Size / connection | 10 in (DN250) CL2500 / butt-weld end (SA-106 C / SA-335 P11) |
| Scope break | IEC HRSG HP economiser 1 inlet with pup piece; field weld by EPC. |
| Istanbul EPC side | EPC: HP feedwater piping (EPC) |
| Imaginary Electric side | IEC: HRSG HP ECO1 inlet |
| Isolation | EPC HP feedwater motor-operated isolation valve and non-return valve. |
| Protection | EPC BFP shut-off head at maximum speed <= 234 barg (VFD speed limit), verified at pump FAT; minimum-flow recirculation valve. |
| Design | 234.0 barg / 200 degC |
| Operating envelope | 95.0 to 215.0 barg; 130 to 170 degC |
| Flow | normal 100.16 / max 110.00 kg/s |
| HMB envelope (all cases) | stream 22 (full check): 50.31-103.34 kg/s, 100.266-214.270 barg, 135.9-163.9 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 22 max 103.34 kg/s (WIN-NG-100) <= capacity 110.00 kg/s (margin +6.1 %), 9 cases OK HMB pressure: stream 22: 100.266 - 214.270 barg within 95.0 - 215.0 barg (design 234.0) OK HMB temperature: stream 22: 135.9 - 163.9 degC within 130.0 - 170.0 degC (design 200.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-19  IP feedwater

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | feedwater / HRSG IP ECO inlet |
| Size / connection | 6 in (DN150) CL600 / butt-weld end |
| Scope break | IEC HRSG IP economiser inlet with pup piece; field weld by EPC. |
| Istanbul EPC side | EPC: IP feedwater piping (EPC) |
| Imaginary Electric side | IEC: HRSG IP ECO inlet |
| Isolation | EPC IP feedwater isolation and non-return valve. |
| Protection | EPC BFP interstage pressure at shut-off <= 58 bar(a), verified at FAT. |
| Design | 59.0 barg / 200 degC |
| Operating envelope | 20.0 to 48.0 barg; 130 to 165 degC |
| Flow | normal 29.82 / max 33.00 kg/s |
| HMB envelope (all cases) | stream 23 (full check): 17.23-31.59 kg/s, 22.358-46.927 barg, 134.6-161.4 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 23 max 31.59 kg/s (WIN-NG-100) <= capacity 33.00 kg/s (margin +4.3 %), 9 cases OK HMB pressure: stream 23: 22.358 - 46.927 barg within 20.0 - 48.0 barg (design 59.0) OK HMB temperature: stream 23: 134.6 - 161.4 degC within 130.0 - 165.0 degC (design 200.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-20  FGH water return

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | feedwater / performance gas heater water outlet |
| Size / connection | 4 in (DN100) CL600 / ASME B16.5 CL600 RF flange |
| Scope break | IEC performance gas heater water outlet flange; EPC return line to the condensate system. |
| Istanbul EPC side | EPC: return line to condensate (EPC) |
| Imaginary Electric side | IEC: performance gas heater water outlet |
| Isolation | EPC isolation valve; IEC FGH outlet control valve. |
| Protection | EPC return line designed 60 bar(a) / 260 degC up to and including its pressure-reducing valve at the condensate connection; condensate system relief valve downstream (EPC). |
| Design | 59.0 barg / 260 degC |
| Operating envelope | 18.0 to 46.0 barg; 60 to 90 degC |
| Flow | normal 12.48 / max 14.50 kg/s |
| HMB envelope (all cases) | stream 19 (full check): 6.62-13.40 kg/s, 19.358-43.927 barg, 75.0-75.0 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 19 max 13.40 kg/s (MIN-NG-100) <= capacity 14.50 kg/s (margin +7.6 %), 8 cases OK HMB pressure: stream 19: 19.358 - 43.927 barg within 18.0 - 46.0 barg (design 59.0) OK HMB temperature: stream 19: 75.0 - 75.0 degC within 60.0 - 90.0 degC (design 260.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-21  HRSG blowdown

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | water / continuous / intermittent blowdown valves outlet |
| Size / connection | 2 in / 3 in / socket-weld / butt-weld ends |
| Scope break | IEC supplies the continuous and intermittent blowdown valves (two in series); scope break at the outlet weld of the second valve; EPC blowdown piping, flash tanks and silencers. |
| Istanbul EPC side | EPC: blowdown tanks (EPC) |
| Imaginary Electric side | IEC: continuous / intermittent blowdown valves outlet |
| Isolation | IEC two valves in series (ASME I PG-58.3.6). |
| Protection | EPC blowdown piping designed for the drum design pressure up to the flash tank inlet. |
| Design | 209.0 barg / 370 degC |
| Operating envelope | 0.000 to 5.0 barg; 100 to 370 degC |
| Flow | normal 1.00 / max 5.00 kg/s |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | Continuous blowdown up to 1 % of HP flow; intermittent 5 kg/s for 30 s. |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-22  HRSG drains and vents

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | water/steam / drain/vent valves outlet (IEC) |
| Size / connection | various (1 in - 3 in) / socket-weld / butt-weld ends |
| Scope break | Scope break at the outlet weld of the IEC drain/vent valve (second isolation); EPC drain collection, atmospheric flash tanks and vent silencers. |
| Istanbul EPC side | EPC: drain collection, flash tanks, silencers (EPC) |
| Imaginary Electric side | IEC: drain/vent valves outlet (IEC) |
| Isolation | IEC two valves in series on all pressure part drains. |
| Protection | EPC drain headers designed for the highest upstream design up to the first flash tank. |
| Design | 209.0 barg / 610 degC |
| Operating envelope | 0.000 to 1.0 barg; 40 to 610 degC |
| Flow | normal - / max 10.00 kg/s |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | Start-up drains. |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-23  Chemical dosing

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | chemicals / dosing nozzles on drums/condensate |
| Size / connection | 1 in / socket-weld, IEC root valve |
| Scope break | IEC dosing nozzles with root valves on the drums; EPC dosing skids and lines. |
| Istanbul EPC side | EPC: dosing skids and lines (EPC) |
| Imaginary Electric side | IEC: dosing nozzles on drums/condensate |
| Isolation | IEC root valve + EPC isolation and check valve. |
| Protection | EPC dosing pump relief set below the line design. |
| Design | 234.0 barg / 100 degC |
| Operating envelope | 3.0 to 215.0 barg; 5 to 40 degC |
| Flow | normal - / max 0.10 m3/h (density 1000.0 kg/m3) |
| Quality / specification | source:SRC-EPCE-0010 |
| Conditions (text) | Lay-up and optional drum dosing; AVT(O) ammonia dosing into the condensate by EPC. |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-24  Sampling

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | water/steam / sample nozzles with root valves (IEC) |
| Size / connection | 1/2 in / socket-weld, IEC root valve |
| Scope break | IEC sample nozzles with root valves; EPC sample lines, coolers and the SWAS. |
| Istanbul EPC side | EPC: sample lines, coolers, SWAS (EPC) |
| Imaginary Electric side | IEC: sample nozzles with root valves (IEC) |
| Isolation | IEC root valve; EPC isolation at the SWAS. |
| Protection | EPC sample line design = upstream design. |
| Design | 234.0 barg / 610 degC |
| Operating envelope | -1.0 to 215.0 barg; 20 to 600 degC |
| Flow | normal - / max 0.50 kg/s |
| Quality / specification | source:SRC-EPCE-0010 |
| Conditions (text) | Sample points per IEC-ALP-REQ-001 section 4. |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-25  Aqueous ammonia

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | NH4OH 24.5 % / ammonia injection skid inlet (IEC) |
| Size / connection | 1 in / ASME B16.5 CL150 RF flange (316L) |
| Scope break | IEC ammonia injection skid inlet flange; EPC storage, unloading and forwarding pumps. |
| Istanbul EPC side | EPC: storage, unloading, forwarding pumps (EPC) |
| Imaginary Electric side | IEC: ammonia injection skid inlet (IEC) |
| Isolation | EPC ESD valve (fail-closed) and manual valve. |
| Protection | EPC forwarding pump relief 9 barg. |
| Design | 10.0 barg / 40 degC |
| Operating envelope | 3.0 to 7.0 barg; 5 to 40 degC |
| Flow | normal 0.12 / max 0.50 t/h |
| Quality / specification | requirement:ER-06.03, source:SRC-EPCE-0010 |
| Conditions (text) | Aqueous ammonia 24.5 %: 125 kg/h on gas, 480 kg/h on LDO (TQ-IEC-018). |
| Dates | available by 2028-11-01; needed by 2028-11-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete OK dates: available 2028-11-01, needed 2028-11-15: float 14 d |

## IF-26  Flue gas to stack

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | flue gas / HRSG outlet transition flange |
| Size / connection | D 9.2 m / bolted flange with EPC fabric expansion joint |
| Scope break | IEC HRSG outlet transition duct flange (drilled); EPC fabric expansion joint, stack, silencer, CEMS and damper (if any). |
| Istanbul EPC side | EPC: stack (EPC), CEMS (EPC) |
| Imaginary Electric side | IEC: HRSG outlet transition flange |
| Isolation | None (no stack damper). |
| Protection | HRSG casing design +/- 50 mbar. |
| Design | 0.050 barg / 200 degC |
| Operating envelope | 0.000 to 0.030 barg; 60 to 120 degC |
| Flow | normal 796.70 / max 850.00 kg/s |
| HMB envelope (all cases) | stream 5 (full check): 441.95-832.46 kg/s, 0.001-0.001 barg, 68.2-89.7 degC |
| Quality / specification | requirement:ER-14.02 |
| Dates | available by 2028-06-30; needed by 2028-09-15 |
| Scope items | SC-010, SC-011 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 5 max 832.46 kg/s (WIN-NG-100) <= capacity 850.00 kg/s (margin +2.1 %), 9 cases OK HMB pressure: stream 5: 0.001 - 0.001 barg within 0.0 - 0.03 barg (design 0.05) OK HMB temperature: stream 5: 68.2 - 89.7 degC within 60.0 - 120.0 degC (design 200.0) OK dates: available 2028-06-30, needed 2028-09-15: float 77 d |

## IF-27  Circulating water

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | seawater / condenser water box flanges (2 inlets, 2 outlets) |
| Size / connection | 4 x DN1800 / EN 1092-1 PN6 flanges, rubber-lined water boxes |
| Scope break | IEC condenser water box inlet/outlet flanges; EPC CW piping (GRP), expansion joints, counter-flanges and bolts. |
| Istanbul EPC side | EPC: CW pipes (EPC) |
| Imaginary Electric side | IEC: condenser water box flanges (2 inlets, 2 outlets) |
| Isolation | EPC butterfly valves per inlet and outlet half (condenser half-side operation). |
| Protection | EPC CW pump shut-off head <= 3.5 barg at the condenser; surge analysis for pump trip <= 4 barg; vacuum breaker at the outlet high point. |
| Design | 4.0 barg / 40 degC |
| Operating envelope | 0.500 to 3.0 barg; 5 to 35 degC |
| Flow | normal 36,050.00 / max 38,000.00 m3/h (density 1025.0 kg/m3) |
| HMB envelope (all cases) | stream 25 (full check): 10196.80-10196.80 kg/s, 1.487-1.487 barg, 6.9-27.0 degC |
| Quality / specification | source:SRC-OWNR-0002, requirement:ER-02.04 |
| Conditions (text) | Design flow 38,000 m3/h (DEC-EPCE-0002); condenser pressure drop 0.62 bar clean. |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Scope items | SC-012 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0005, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 25 max 10196.80 kg/s (WIN-NG-100) <= capacity 10819.44 kg/s (margin +5.8 %), 9 cases OK HMB pressure: stream 25: 1.487 - 1.487 barg within 0.5 - 3.0 barg (design 4.0) OK HMB temperature: stream 25: 6.9 - 27.0 degC within 5.0 - 35.0 degC (design 40.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-28  Closed cooling water

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | demin water + inhibitor / IEC coolers inlet/outlet flanges |
| Size / connection | various (DN50 - DN400) / ASME B16.5 CL150 RF flanges |
| Scope break | IEC cooler inlet/outlet flanges; EPC CCW system. |
| Istanbul EPC side | EPC: CCW system (EPC) |
| Imaginary Electric side | IEC: IEC coolers inlet/outlet flanges |
| Isolation | EPC valves per consumer. |
| Protection | EPC CCW pump shut-off <= 8 barg. |
| Design | 10.0 barg / 60 degC |
| Operating envelope | 3.0 to 6.0 barg; 20 to 36 degC |
| Flow | normal 1,055.00 / max 1,160.00 m3/h (density 1000.0 kg/m3) |
| Quality / specification | source:SRC-EPCE-0010 |
| Conditions (text) | 9,400 kW; supply <= 36 degC (ST TEWAC) / 38 degC (others). |
| Dates | available by 2028-08-09; needed by 2028-08-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete INFO dates: available 2028-08-09, needed 2028-08-16: float 7 d (tight) |

## IF-29  Instrument and service air

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | air / IEC skids |
| Size / connection | 1 in - 2 in / ASME B16.5 CL150 RF flanges |
| Scope break | IEC skid inlet flanges; EPC compressed air system. |
| Istanbul EPC side | EPC: compressed air system (EPC) |
| Imaginary Electric side | IEC: IEC skids |
| Isolation | EPC valve per skid. |
| Protection | EPC air receivers relief 10 barg. |
| Design | 10.0 barg / 50 degC |
| Operating envelope | 6.0 to 8.0 barg; 5 to 45 degC |
| Flow | normal 350.00 / max 500.00 Nm3/h (density 1.293 kg/m3) |
| Quality / specification | source:SRC-EPCE-0010 |
| Conditions (text) | Instrument air dew point -40 degC at 7 barg (ISO 8573-1 class 1.2.1). |
| Dates | available by 2028-08-09; needed by 2028-08-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete INFO dates: available 2028-08-09, needed 2028-08-16: float 7 d (tight) |

## IF-30  Nitrogen

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | N2 / HRSG lay-up / generator purge connections |
| Size / connection | 1 in / ASME B16.5 CL150 RF flange |
| Scope break | IEC lay-up / purge connections; EPC nitrogen supply. |
| Istanbul EPC side | EPC: N2 supply (EPC) |
| Imaginary Electric side | IEC: HRSG lay-up / generator purge connections |
| Isolation | EPC valve + IEC valve. |
| Protection | EPC pressure regulator + relief 9 barg. |
| Design | 10.0 barg / 50 degC |
| Operating envelope | 5.0 to 8.0 barg; 5 to 40 degC |
| Flow | normal - / max 1,000.00 Nm3/h (density 1.25 kg/m3) |
| Quality / specification | source:SRC-EPCE-0010 |
| Conditions (text) | 99.9 % N2; 3,000 Nm3 per lay-up event. |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-31  Hydrogen / CO2

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | H2 / CO2 / GT generator gas control panel inlet |
| Size / connection | 1/2 in / compression fitting (316L) |
| Scope break | IEC generator gas control panel inlet; EPC bottle racks, regulators and piping. |
| Istanbul EPC side | EPC: bottle racks and piping (EPC) |
| Imaginary Electric side | IEC: GT generator gas control panel inlet |
| Isolation | EPC valves at the racks. |
| Protection | EPC regulator + relief 14 barg. |
| Design | 16.0 barg / 50 degC |
| Operating envelope | 8.0 to 12.0 barg; 5 to 40 degC |
| Flow | normal - / max 60.00 Nm3/h |
| Quality / specification | source:SRC-EPCE-0010 |
| Conditions (text) | H2 99.9 %, 12 Nm3/day; CO2 150 Nm3 per purge. |
| Dates | available by 2028-08-25; needed by 2028-09-01 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete INFO dates: available 2028-08-25, needed 2028-09-01: float 7 d (tight) |

## IF-32  Auxiliary steam

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / utility |
| --- | --- |
| Medium / location | steam / gland steam header inlet (IEC) |
| Size / connection | 4 in (DN100) CL300 / butt-weld end |
| Scope break | IEC gland steam header inlet; EPC auxiliary steam line from the auxiliary boiler. |
| Istanbul EPC side | EPC: auxiliary boiler steam (EPC) |
| Imaginary Electric side | IEC: gland steam header inlet (IEC) |
| Isolation | EPC isolation valve. |
| Protection | EPC auxiliary steam header relief set 15 barg. |
| Design | 15.0 barg / 320 degC |
| Operating envelope | 8.0 to 9.5 barg; 250 to 300 degC |
| Flow | normal 4.50 / max 7.50 t/h |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Conditions (text) | 4.5 t/h gland sealing, 3 t/h HRSG sparging (optional). |
| Dates | available by 2028-09-30; needed by 2028-10-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: utility: complete OK dates: available 2028-09-30, needed 2028-10-16: float 16 d |

## IF-33  Fire protection

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / control |
| --- | --- |
| Medium / location | - / GT enclosure CO2 system (IEC) |
| Size / connection | - / hardwired volt-free contacts + Modbus TCP summary |
| Scope break | IEC GT enclosure CO2 fire protection panel terminals; EPC fire alarm panel (NFPA 72), cables, transformer deluge, hydrants. |
| Istanbul EPC side | EPC: fire detection/alarm, transformer deluge, hydrants (EPC) |
| Imaginary Electric side | IEC: GT enclosure CO2 system (IEC) |
| Isolation | - |
| Protection | - |
| Dates | available by 2028-08-17; needed by 2028-08-24 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: control: complete INFO dates: available 2028-08-17, needed 2028-08-24: float 7 d (tight) |

## IF-34  GT GSU HV

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / electrical |
| --- | --- |
| Medium / location | electrical / GT GSU HV bushings |
| Size / connection | 560 MVA / GSU HV air bushings, EPC 420 kV connection to the GIS |
| Scope break | IEC GSU HV bushing terminals; EPC conductors/cable, clamps, surge arresters at the bushings and the GIS bay. |
| Istanbul EPC side | EPC: 380 kV connection to GIS (EPC) |
| Imaginary Electric side | IEC: GT GSU HV bushings |
| Isolation | EPC GIS generator transformer bay circuit breaker, disconnector and earthing switch; IEC GCB on the LV side. |
| Protection | GSU differential (87T) and overall differential (87G-T) by IEC; GIS bay protection by EPC; trip matrix per IF-41. |
| Flow | normal - / max 560.00 MVA |
| Electrical | 380.00 kV (342.0-420.0 kV); Isc 50.0 kA, rating 50.0 kA; pf 0.85 |
| HMB power | gt_output |
| Fed from | TP-E1 (chain dp - bar) |
| Conditions (text) | OLTC 400 +/- 8 x 1.25 % (360-440 kV) with generator 21 kV +/- 5 % covers 342-420 kV. |
| Dates | available by 2028-07-29; needed by 2028-08-02 |
| Scope items | SC-014 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: electrical: complete OK short circuit: prospective 50.0 kA <= rating 50.0 kA OK HMB power: max gt_output 470.0 MW (WIN-NG-100) / pf 0.85 = 552.9 MVA <= 560 MVA (margin +1.3 %) OK chain voltage: TP-E1 342.0-420.0 kV within 342.0-420.0 kV here OK chain short circuit: TP-E1 50.0 kA <= rating 50.0 kA here INFO dates: available 2028-07-29, needed 2028-08-02: float 4 d (tight) |

## IF-35  ST GSU HV

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / electrical |
| --- | --- |
| Medium / location | electrical / ST GSU HV bushings |
| Size / connection | 270 MVA / GSU HV air bushings, EPC 420 kV connection to the GIS |
| Scope break | As IF-34 for the ST GSU. |
| Istanbul EPC side | EPC: 380 kV connection to GIS (EPC) |
| Imaginary Electric side | IEC: ST GSU HV bushings |
| Isolation | As IF-34. |
| Protection | As IF-34. |
| Flow | normal - / max 270.00 MVA |
| Electrical | 380.00 kV (342.0-420.0 kV); Isc 50.0 kA, rating 50.0 kA; pf 0.85 |
| HMB power | st_output |
| Fed from | TP-E1 (chain dp - bar) |
| Conditions (text) | OLTC 400 +/- 8 x 1.25 % with generator 15.75 kV +/- 5 %. |
| Dates | available by 2028-07-29; needed by 2028-08-02 |
| Scope items | SC-014 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: electrical: complete OK short circuit: prospective 50.0 kA <= rating 50.0 kA OK HMB power: max st_output 207.9 MW (WIN-NG-100) / pf 0.85 = 244.6 MVA <= 270 MVA (margin +9.4 %) OK chain voltage: TP-E1 342.0-420.0 kV within 342.0-420.0 kV here OK chain short circuit: TP-E1 50.0 kA <= rating 50.0 kA here INFO dates: available 2028-07-29, needed 2028-08-02: float 4 d (tight) |

## IF-36  UAT supply

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / electrical |
| --- | --- |
| Medium / location | electrical / IPB tap-off flange (GT and ST IPB) |
| Size / connection | 21 kV (GT) / 15.75 kV (ST) / IPB tap-off flange (IEC), EPC MV busduct |
| Scope break | IEC IPB tap-off flange between GCB and GSU; EPC UAT, UAT busduct and flexible links. |
| Istanbul EPC side | EPC: UAT and MV busduct (EPC) |
| Imaginary Electric side | IEC: IPB tap-off flange (GT and ST IPB) |
| Isolation | IEC tap-off disconnector link; EPC UAT MV circuit breaker. |
| Protection | UAT differential and overcurrent by EPC, integrated in the IEC unit trip matrix. |
| Flow | normal - / max 31.50 MVA |
| Electrical | 21.00 kV (19.9-22.1 kV); Isc 169.0 kA, rating 200.0 kA |
| Conditions (text) | Prospective 169 kA at the GT generator bus (96 kA via GSU + 73 kA generator); ST bus 125 kA. IPB tap-off rated 200 kA sym / 550 kA peak (TQ-IEC-021 item 4). |
| Dates | available by 2028-08-09; needed by 2028-08-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: electrical: complete OK short circuit: prospective 169.0 kA <= rating 200.0 kA INFO dates: available 2028-08-09, needed 2028-08-16: float 7 d (tight) |

## IF-37  MV supplies

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / electrical |
| --- | --- |
| Medium / location | electrical / SFC isolation transformer, IEC MV consumers |
| Size / connection | 10.5 kV feeders / cable terminations at the IEC equipment (lugs by EPC) |
| Scope break | EPC 10.5 kV feeders and cables up to and including the terminations at the IEC equipment. |
| Istanbul EPC side | EPC: 10.5 kV switchgear feeders (EPC) |
| Imaginary Electric side | IEC: SFC isolation transformer, IEC MV consumers |
| Isolation | EPC feeder circuit breaker with earthing switch. |
| Protection | EPC feeder protection. |
| Flow | normal - / max 10.00 MVA |
| Electrical | 10.50 kV (9.4-11.6 kV); Isc 35.0 kA, rating 40.0 kA |
| Conditions (text) | SFC 8.5 MW for 30 min at start-up. |
| Dates | available by 2028-08-09; needed by 2028-08-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: electrical: complete OK short circuit: prospective 35.0 kA <= rating 40.0 kA INFO dates: available 2028-08-09, needed 2028-08-16: float 7 d (tight) |

## IF-38  LV supplies

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / electrical |
| --- | --- |
| Medium / location | electrical / IEC MCCs incoming |
| Size / connection | 0.4 kV feeders / IEC MCC incoming terminals |
| Scope break | EPC 0.4 kV feeders and cables up to the IEC MCC incoming terminals. |
| Istanbul EPC side | EPC: 0.4 kV switchgear feeders (EPC) |
| Imaginary Electric side | IEC: IEC MCCs incoming |
| Isolation | EPC feeder breaker; IEC MCC incomer. |
| Protection | EPC feeder protection selective with IEC MCC. |
| Electrical | 0.40 kV (0.4-0.4 kV); Isc 50.0 kA, rating 50.0 kA |
| Conditions (text) | Loads per IEC-ALP-REQ-001 section 7.1. |
| Dates | available by 2028-08-09; needed by 2028-08-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: electrical: complete OK short circuit: prospective 50.0 kA <= rating 50.0 kA INFO dates: available 2028-08-09, needed 2028-08-16: float 7 d (tight) |

## IF-39  DC and UPS

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / electrical |
| --- | --- |
| Medium / location | electrical / TCS, protection, emergency oil pumps |
| Size / connection | 220 V DC / 230 V AC UPS / IEC panel incoming terminals |
| Scope break | EPC DC and UPS distribution feeders up to the IEC panel terminals. |
| Istanbul EPC side | EPC: 220 V DC and 230 V AC UPS (EPC) |
| Imaginary Electric side | IEC: TCS, protection, emergency oil pumps |
| Isolation | EPC feeder MCB/fuse. |
| Protection | EPC selective fusing. |
| Electrical | 0.22 kV (0.2-0.2 kV); Isc - kA, rating - kA |
| Conditions (text) | GT 37 kW / ST 45 kW DC emergency oil pumps, 3 h autonomy; 45 kVA UPS for the TCS. |
| Dates | available by 2028-08-09; needed by 2028-08-16 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: electrical: complete INFO dates: available 2028-08-09, needed 2028-08-16: float 7 d (tight) |

## IF-40  Control system interface

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / control |
| --- | --- |
| Medium / location | data / IEC turbine control system (TCS) gateway |
| Size / connection | OPC UA + Modbus TCP, redundant; hardwired trips / OPC UA + Modbus TCP, redundant fibre; hardwired trips |
| Scope break | IEC TCS gateway ports and fibre patch panel in the IEC electronic room; EPC fibre cables, DCS and the firewall between the zones (IEC 62443 zone/conduit). |
| Istanbul EPC side | EPC: plant DCS (EPC) |
| Imaginary Electric side | IEC: IEC turbine control system (TCS) gateway |
| Isolation | - |
| Protection | - |
| Conditions (text) | About 2,500 signals. |
| Dates | available by 2028-06-01; needed by 2028-06-15 |
| Scope items | SC-013 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: control: complete OK dates: available 2028-06-01, needed 2028-06-15: float 14 d |

## IF-41  Protection interface

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / control |
| --- | --- |
| Medium / location | signals / generator/GSU protection panels |
| Size / connection | IEC 61850 + hardwired / IEC 61850 (GOOSE/MMS) + hardwired trips |
| Scope break | IEC generator/GSU protection panel terminals; EPC switchyard protection, substation automation and TSO SCADA. |
| Istanbul EPC side | EPC: switchyard protection and TSO SCADA (EPC) |
| Imaginary Electric side | IEC: generator/GSU protection panels |
| Isolation | - |
| Protection | - |
| Dates | available by 2028-07-29; needed by 2028-08-02 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: control: complete INFO dates: available 2028-07-29, needed 2028-08-02: float 4 d (tight) |

## IF-42  Earthing

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / civil |
| --- | --- |
| Medium / location | electrical / equipment earthing bosses |
| Size / connection | - / bolted earthing pads (IEC), EPC 240 mm2 Cu risers |
| Scope break | IEC equipment earthing pads and internal earthing; EPC earthing grid (IEEE 80) and risers. |
| Istanbul EPC side | EPC: earthing grid (EPC) |
| Imaginary Electric side | IEC: equipment earthing bosses |
| Isolation | - |
| Protection | - |
| Dates | available by 2027-10-15; needed by 2027-11-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: civil: complete OK dates: available 2027-10-15, needed 2027-11-15: float 31 d |

## IF-43  Foundations

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / civil |
| --- | --- |
| Medium / location | civil / anchor bolts, sole plates, load data (IEC) |
| Size / connection | - / anchor bolts / sole plates (IEC supply), grout by EPC to IEC specification |
| Scope break | IEC load data, anchor bolts, sole plates and grouting specification; EPC foundation design, construction, cast-in of anchor bolts and grouting. |
| Istanbul EPC side | EPC: foundation design and construction (EPC) |
| Imaginary Electric side | IEC: anchor bolts, sole plates, load data (IEC) |
| Isolation | - |
| Protection | - |
| Conditions (text) | Loads per IEC-ALP-REQ-001 section 9. |
| Dates | available by 2027-11-01; needed by 2027-11-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Checks (engine) | OK completeness: civil: complete OK dates: available 2027-11-01, needed 2027-11-15: float 14 d |

## IF-44  Condenser tube cleaning balls

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | seawater + sponge balls / condenser inlet water boxes (injection) and outlet water box flanges (strainers) |
| Size / connection | 2 x DN150 per inlet half / EN 1092-1 PN10 flanges |
| Scope break | IEC ball injection nozzles on the condenser inlet water boxes; EPC tube cleaning system (ball strainers in the outlet lines, recirculation pumps, collectors). |
| Istanbul EPC side | EPC: ball recirculation units, strainers, debris filters, controls |
| Imaginary Electric side | IEC: injection nozzles and outlet flanges on the water boxes |
| Isolation | EPC valves at the nozzles. |
| Protection | As IF-27. |
| Design | 4.0 barg / 40 degC |
| Operating envelope | 0.500 to 3.5 barg; 5 to 35 degC |
| Flow | normal - / max 200.00 m3/h (density 1025.0 kg/m3) |
| Quality / specification | source:SRC-OWNR-0002, requirement:ER-02.04 |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | decision:DEC-EPCE-0004, source:SRC-IECE-0008 |
| Remarks | added by TQ-IEC-005 |
| Checks (engine) | OK completeness: process: complete OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-45  HP attemperation spray water

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | feedwater / HRSG HP attemperator spray control station inlet |
| Size / connection | 3 in (DN80) CL2500 / butt-weld end |
| Scope break | IEC HP attemperator spray control station inlet (station with control and block valves by IEC); EPC spray water line from the BFP discharge and the weld. |
| Istanbul EPC side | EPC: spray water line from the BFP discharge |
| Imaginary Electric side | IEC: HP attemperator spray control station |
| Isolation | EPC isolation valve at the BFP discharge header; IEC block valve. |
| Protection | As IF-18 (BFP shut-off <= 234 barg). |
| Design | 234.0 barg / 200 degC |
| Operating envelope | 95.0 to 215.0 barg; 130 to 170 degC |
| Flow | normal - / max 5.00 kg/s |
| HMB envelope (all cases) | stream 29 (full check): 1.39-2.06 kg/s, 143.744-194.605 barg, 147.6-158.7 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | source:SRC-IECE-0008, source:SRC-IECE-0005, decision:DEC-EPCE-0004 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 29 max 2.06 kg/s (MAX-NG-100) <= capacity 5.00 kg/s (margin +58.8 %), 4 cases OK HMB pressure: stream 29: 143.744 - 194.605 barg within 95.0 - 215.0 barg (design 234.0) OK HMB temperature: stream 29: 147.6 - 158.7 degC within 130.0 - 170.0 degC (design 200.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

## IF-46  Reheat attemperation spray water

| Contract / category | ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility / process |
| --- | --- |
| Medium / location | feedwater / HRSG reheat attemperator spray control station inlet |
| Size / connection | 2 in (DN50) CL600 / butt-weld end |
| Scope break | IEC reheat attemperator spray control station inlet; EPC spray water line from the BFP interstage. |
| Istanbul EPC side | EPC: spray water line from the BFP interstage |
| Imaginary Electric side | IEC: reheat attemperator spray control station |
| Isolation | EPC isolation valve at the interstage header; IEC block valve. |
| Protection | As IF-19 (interstage <= 58 bar(a)). |
| Design | 59.0 barg / 200 degC |
| Operating envelope | 20.0 to 48.0 barg; 130 to 170 degC |
| Flow | normal - / max 3.00 kg/s |
| HMB envelope (all cases) | stream 30 (full check): 0.30-0.95 kg/s, 31.811-41.799 barg, 145.7-155.9 degC |
| Quality / specification | requirement:ER-09.03, source:SRC-EPCE-0010 |
| Dates | available by 2028-09-01; needed by 2028-09-15 |
| Agreement | agreed by Istanbul EPC, Imaginary Electric in TQ-IEC-021 (2026-09-28) |
| Basis | source:SRC-IECE-0008, source:SRC-IECE-0005, decision:DEC-EPCE-0004 |
| Checks (engine) | OK completeness: process: complete OK HMB flow: stream 30 max 0.95 kg/s (MAX-NG-100) <= capacity 3.00 kg/s (margin +68.4 %), 4 cases OK HMB pressure: stream 30: 31.811 - 41.799 barg within 20.0 - 48.0 barg (design 59.0) OK HMB temperature: stream 30: 145.7 - 155.9 degC within 130.0 - 170.0 degC (design 200.0) OK dates: available 2028-09-01, needed 2028-09-15: float 14 d |

# 4. Check results

WARN = to be resolved before the point is frozen; INFO = noted; OK rows are listed in the Excel register.

| Point | Check | Result | Detail |
| --- | --- | --- | --- |
| IF-03 | HMB scope | INFO | stream 28: flow + temperature checked only - see remarks |
| IF-28 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight) |
| IF-29 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight) |
| IF-31 | dates | INFO | available 2028-08-25, needed 2028-09-01: float 7 d (tight) |
| IF-33 | dates | INFO | available 2028-08-17, needed 2028-08-24: float 7 d (tight) |
| IF-34 | dates | INFO | available 2028-07-29, needed 2028-08-02: float 4 d (tight) |
| IF-35 | dates | INFO | available 2028-07-29, needed 2028-08-02: float 4 d (tight) |
| IF-36 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight) |
| IF-37 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight) |
| IF-38 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight) |
| IF-39 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight) |
| IF-41 | dates | INFO | available 2028-07-29, needed 2028-08-02: float 4 d (tight) |
| TP-CW1 | HMB scope | INFO | stream 25: flow + temperature checked only - see remarks |
| TP-CW2 | HMB scope | INFO | stream 26: flow + temperature checked only - see remarks |
| TP-E1 | HMB power | INFO | max net 665.3 MW (WIN-NG-100) > 640 MW (margin -3.9 %); limited to 640 MW at this point: Export limiter in the plant control system: 640 MW net at the 380 kV revenue meters (TQ-027); line differential 87L main 1 / main 2 with the remote end (plant end by the Contractor, remote end by the Owner), settings coordinated with the TSO (ER-18.02). |
| TP-E1 | dates | INFO | available 2028-07-15, needed 2028-07-22: float 7 d (tight) |
| - | HMB coverage | INFO | streams not mapped to a tie-in (internal to one scope, else an interface is missing): 1 Ambient air to GT compressor inlet; 3 Heated fuel gas to GT combustion system; 4 GT exhaust gas to HRSG inlet; 10 IP superheated steam (joins cold reheat inside the HRSG); 15 IP turbine exhaust (crossover, internal); 16 LP turbine exhaust to condenser (UEEP); 18 Condensate at CEP discharge; 24 IP economiser water to performance fuel gas heater |
| - | coverage | INFO | SC-006 terminal point 'GT exhaust flange to HRSG inlet duct' not referenced by a tie-in |
| - | coverage | INFO | SC-007 terminal point 'Generator terminals (IPB connection)' not referenced by a tie-in |
| - | coverage | INFO | SC-009 terminal point 'Generator terminals' not referenced by a tie-in |
| - | coverage | INFO | SC-051 terminal point 'Owner's warehouse' not referenced by a tie-in |