## Streams
ALP-HMB-SUM-NG-100 - streams
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 710.98 | 1.012 | 32.8 |  | 7.92 | 5.633 | preliminary | source:SRC-IECE-0005
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | fuel_gas | FGS | FGH | 18.541 | 38 | 25 |  | 0 | 0 | preliminary | source:SRC-IECE-0005
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 18.541 | 35.5 | 215 |  | 457.77 | 8.487 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 729.521 | 1.042 | 649.26 |  | 704.17 | 513.704 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 729.521 | 1.014 | 81.7 |  | 60.28 | 43.976 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 94.41 | 176.274 | 600 |  | 3560.33 | 336.131 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 94.41 | 171.089 | 598.5 |  | 3560.88 | 336.182 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 94.41 | 37.942 | 367.31 |  | 3140.29 | 296.475 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 94.41 | 37.283 | 366.31 |  | 3139.25 | 296.377 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 15.807 | 37.988 | 328.31 |  | 3043.53 | 48.109 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 110.898 | 35.49 | 600 |  | 3678.44 | 407.932 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 110.898 | 34.168 | 598.5 |  | 3676.07 | 407.669 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 10.742 | 5.039 | 247.3 |  | 2955.38 | 31.747 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 10.742 | 4.735 | 246.3 |  | 2954.37 | 31.736 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 110.898 | 4.653 | 309.17 |  | 3084.37 | 342.051 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 121.641 | 0.05271 | 33.82 | 0.93138 | 2396.36 | 291.496 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 121.641 | 0.05271 | 33.77 |  | 141.5 | 17.213 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 121.641 | 16 | 33.95 |  | 143.69 | 17.479 | preliminary | source:SRC-IECE-0005
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 11.418 | 39.812 | 75 |  | 317.15 | 3.621 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 133.059 | 15.5 | 37.53 |  | 158.6 | 21.103 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 122.317 | 5.476 | 155.24 |  | 654.92 | 80.108 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 92.894 | 195.618 | 158.66 |  | 681.16 | 63.275 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 27.226 | 42.812 | 155.95 |  | 660.23 | 17.975 | preliminary | source:SRC-IECE-0005
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 11.418 | 40.81 | 244.84 |  | 1060.74 | 12.111 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 24 |  | 97.67 | 995.877 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 30.61 |  | 124.56 | 1270.158 | preliminary | source:SRC-IECE-0005
29 | HP attemperation spray water (BFP discharge) | water | BFP | HRSG | 1.516 | 195.618 | 158.66 |  | 681.16 | 1.033 | preliminary | source:SRC-IECE-0005
30 | Reheat attemperation spray water (BFP interstage) | water | BFP | HRSG | 0.681 | 42.812 | 155.95 |  | 660.23 | 0.45 | preliminary | source:SRC-IECE-0005

## Node balances
ALP-HMB-SUM-NG-100 - node balances
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 710.98 | 0 | 5.633 | 0 | -5.633 | 0
BFP | FALSE | 122.317 | 122.317 | 80.108 | 82.733 | 0 | -2.626 | 0
CEP | FALSE | 121.641 | 121.641 | 17.213 | 17.479 | 0 | -0.266 | 0
CMIX | FALSE | 133.059 | 133.059 | 21.1 | 21.103 | 0 | -0.002 | 0
COND | FALSE | 10318.445 | 10318.445 | 1287.373 | 1287.371 | 0 | 0.002 | 0
FGH | FALSE | 29.959 | 29.959 | 12.111 | 12.109 | 0 | 0.003 | 0
FGS | TRUE | 0 | 18.541 | 0 | 0 | 0 | 0 | 0
GT | FALSE | 729.521 | 729.521 | 894.446 | 513.704 | 380.74 | 0.001 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 1079.307 | 1079.306 | 913.917 | 912.005 | 0 | 1.912 | 1.879 | HRSG: gas-side duty 469.73 MW; residual = casing loss
OUT | TRUE | 10196.804 | 0 | 1270.158 | 0 | 0 | 1270.158 | 0
PIPE | FALSE | 310.46 | 310.46 | 1072.285 | 1071.964 | 0 | 0.321 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 995.877 | 0 | -995.877 | 0
ST | FALSE | 216.05 | 216.051 | 775.587 | 587.971 | 187.619 | -0.002 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 729.521 | 0 | 43.976 | 0 | 0 | 43.976 | 0

## Auxiliary loads
ALP-HMB-SUM-NG-100 - auxiliary loads
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-256 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-257 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-258 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-259 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-260 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-261 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-262 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-263 | GT GSU losses at this case load | IEC | fixed | 895 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-264 | ST GSU losses at this case load | IEC | fixed | 511 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-265 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 2720.7 | auxiliary | enthalpy rise 2,626 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-266 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 280.4 | auxiliary | enthalpy rise 266 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-267 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-268 | Closed cooling water pumps | IEPC | fixed | 320 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-269 | Electro-chlorination | IEPC | fixed | 260 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-270 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 450 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-271 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-272 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-273 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-274 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-275 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-276 | Fuel gas receiving station | IEPC | fixed | 60 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-277 | LDO system (standby on gas) | IEPC | fixed | 30 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-SUM-NG-100 - summary
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
Item | Value | Unit
GT output | 372.794 | MW
ST output | 184.533 | MW
Gross output | 557.327 | MW
Auxiliary loads | 9.9147 | MW
Transformer losses | 1.646 | MW
Net output | 545.7663 | MW
Heat input (LHV) | 880.3257 | MW
Gross heat rate | 5686.3791 | kJ/kWh
Net heat rate | 5806.8307 | kJ/kWh
Net efficiency | 61.996 | %
Auxiliary + transformer losses | 2.0743 | % of gross
Fuel LHV (ISO 6976) | 47.4799 | MJ/kg
Fuel LHV volumetric | 34.7797 | MJ/Sm3
Fuel flow | 18.541 | kg/s
Fuel flow | 91121.3218 | Sm3/h
HRSG gas-side duty | 469.7278 | MW
CW flow | 36168.8551 | m3/h
CW temperature rise | 6.61 | K
Condenser pressure | 52.71 | mbar(a)
Flue gas Ar (wet) | 0.874 | mol %
Flue gas CO2 (wet) | 4.366 | mol %
Flue gas H2O (wet) | 10.462 | mol %
Flue gas N2 (wet) | 73.16 | mol %
Flue gas O2 (wet) | 11.138 | mol %

## Checks
ALP-HMB-SUM-NG-100 - checks
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
Status | Check
OK | energy balance CMIX: residual -0.002 MW (tolerance 0.25 MW)
OK | energy balance COND: residual +0.002 MW (tolerance 1.29 MW)
OK | energy balance FGH: residual +0.003 MW (tolerance 0.25 MW)
OK | energy balance GT: residual +0.001 MW (tolerance 0.89 MW)
OK | energy balance HRSG: residual +1.912 MW vs stated casing loss 1.879 MW (tolerance 0.91 MW)
OK | energy balance PIPE: residual +0.321 MW (tolerance 1.07 MW)
OK | energy balance ST: residual -0.002 MW (tolerance 0.78 MW)
OK | gas flow 91,121 Sm3/h = 79.2 % of DP-OWNR-0033 (115,000 Sm3/h)