## Streams
ALP-HMB-WIN-NG-100 - streams
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 810.099 | 1.012 | -4.8 |  | -29.9 | -24.226 | preliminary | source:SRC-IECE-0005
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | fuel_gas | FGS | FGH | 22.357 | 38 | 25 |  | 0 | 0 | preliminary | source:SRC-IECE-0005
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 22.357 | 35.5 | 215 |  | 457.77 | 10.234 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 832.455 | 1.051 | 635.7 |  | 682.88 | 568.47 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 832.455 | 1.014 | 76.96 |  | 54.83 | 45.644 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 103.345 | 192.084 | 591.64 |  | 3523.2 | 364.105 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 103.345 | 186.382 | 590.14 |  | 3524.32 | 364.221 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 103.345 | 41.489 | 359.67 |  | 3114 | 321.817 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 103.345 | 40.767 | 358.67 |  | 3113.12 | 321.726 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 18.21 | 41.622 | 330.41 |  | 3039.19 | 55.344 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 121.556 | 38.796 | 594.97 |  | 3664.27 | 445.414 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 121.556 | 37.344 | 593.47 |  | 3662.01 | 445.139 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 12.389 | 5.599 | 251.78 |  | 2962.78 | 36.706 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 12.389 | 5.232 | 250.78 |  | 2961.95 | 36.696 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 121.556 | 5.124 | 305.9 |  | 3076.48 | 373.965 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 133.945 | 0.02174 | 18.82 | 0.91861 | 2335.41 | 312.816 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 133.945 | 0.02174 | 18.77 |  | 78.77 | 10.551 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 133.945 | 16 | 18.93 |  | 80.95 | 10.843 | preliminary | source:SRC-IECE-0005
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 13.385 | 44.94 | 75 |  | 317.57 | 4.251 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 147.33 | 15.5 | 24.09 |  | 102.47 | 15.097 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 134.941 | 6.121 | 159.57 |  | 673.71 | 90.911 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 103.345 | 215.283 | 163.41 |  | 702.66 | 72.616 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 31.595 | 47.94 | 160.37 |  | 679.62 | 21.473 | preliminary | source:SRC-IECE-0005
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 13.385 | 44.724 | 249.33 |  | 1082.42 | 14.488 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 8 |  | 32.56 | 331.959 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 15.28 |  | 62.18 | 634.042 | preliminary | source:SRC-IECE-0005

## Node balances
ALP-HMB-WIN-NG-100 - node balances
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 810.099 | 0 | -24.226 | 0 | 24.226 | 0
BFP | FALSE | 134.941 | 134.94 | 90.911 | 94.089 | 0 | -3.178 | 0
CEP | FALSE | 133.945 | 133.945 | 10.551 | 10.843 | 0 | -0.292 | 0
CMIX | FALSE | 147.33 | 147.33 | 15.093 | 15.097 | 0 | -0.003 | 0
COND | FALSE | 10330.749 | 10330.749 | 644.775 | 644.593 | 0 | 0.183 | 0
FGH | FALSE | 35.742 | 35.742 | 14.488 | 14.485 | 0 | 0.003 | 0
FGS | TRUE | 0 | 22.357 | 0 | 0 | 0 | 0 | 0
GT | FALSE | 832.456 | 832.455 | 1047.518 | 568.47 | 479.028 | 0.02 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 1218.07 | 1218.071 | 999.381 | 997.268 | 0 | 2.113 | 2.091 | HRSG: gas-side duty 522.83 MW; residual = casing loss
OUT | TRUE | 10196.804 | 0 | 634.042 | 0 | 0 | 634.042 | 0
PIPE | FALSE | 340.635 | 340.635 | 1168.042 | 1167.781 | 0 | 0.26 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 331.959 | 0 | -331.959 | 0
ST | FALSE | 237.29 | 237.29 | 846.055 | 634.633 | 211.422 | 0 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 832.455 | 0 | 45.644 | 0 | 0 | 45.644 | 0

## Auxiliary loads
ALP-HMB-WIN-NG-100 - auxiliary loads
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-212 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-213 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-214 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-215 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-216 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-217 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-218 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-219 | GT GSU losses at this case load | IEC | fixed | 1311 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-220 | ST GSU losses at this case load | IEC | fixed | 619 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-221 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 3293.7 | auxiliary | enthalpy rise 3,178 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-222 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 307.1 | auxiliary | enthalpy rise 292 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-223 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-224 | Closed cooling water pumps | IEPC | fixed | 320 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-225 | Electro-chlorination | IEPC | fixed | 260 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-226 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 450 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-227 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-228 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-229 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-230 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-231 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-232 | Fuel gas receiving station | IEPC | fixed | 60 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-233 | LDO system (standby on gas) | IEPC | fixed | 30 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-WIN-NG-100 - summary
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
Item | Value | Unit
GT output | 470 | MW
ST output | 207.945 | MW
Gross output | 677.945 | MW
Auxiliary loads | 10.5144 | MW
Transformer losses | 2.17 | MW
Net output | 665.2606 | MW
Heat input (LHV) | 1061.5092 | MW
Gross heat rate | 5636.7894 | kJ/kWh
Net heat rate | 5744.2646 | kJ/kWh
Net efficiency | 62.6712 | %
Auxiliary + transformer losses | 1.871 | % of gross
Fuel LHV (ISO 6976) | 47.4799 | MJ/kg
Fuel LHV volumetric | 34.7797 | MJ/Sm3
Fuel flow | 22.357 | kg/s
Fuel flow | 109875.3785 | Sm3/h
HRSG gas-side duty | 522.8255 | MW
CW flow | 36055.1746 | m3/h
CW temperature rise | 7.28 | K
Condenser pressure | 21.74 | mbar(a)
Flue gas Ar (wet) | 0.889 | mol %
Flue gas CO2 (wet) | 4.639 | mol %
Flue gas H2O (wet) | 9.175 | mol %
Flue gas N2 (wet) | 74.369 | mol %
Flue gas O2 (wet) | 10.929 | mol %

## Checks
ALP-HMB-WIN-NG-100 - checks
engine hmb v1.1.1 ¦ data 9f2d118f58330dd9 ¦ 2026-09-28T19:00:37Z
Status | Check
OK | energy balance CMIX: residual -0.003 MW (tolerance 0.25 MW)
OK | energy balance COND: residual +0.183 MW (tolerance 0.64 MW)
OK | energy balance FGH: residual +0.003 MW (tolerance 0.25 MW)
OK | energy balance GT: residual +0.020 MW (tolerance 1.05 MW)
OK | energy balance HRSG: residual +2.113 MW vs stated casing loss 2.091 MW (tolerance 1.00 MW)
OK | energy balance PIPE: residual +0.260 MW (tolerance 1.17 MW)
OK | energy balance ST: residual +0.000 MW (tolerance 0.85 MW)
OK | gas flow 109,875 Sm3/h = 95.5 % of DP-OWNR-0033 (115,000 Sm3/h)
INFO | net export 665.3 MW vs DP-OWNR-0051 connection capacity 640 MW (this case); capability above the capacity, export limited: 640 MW net at the 380 kV revenue meters (TQ-027, TP-E1)