## Summary
IEC-ALP-PER-001 Rev A - Summary
Item | Value | Unit
GT output at generator terminals | 425 | MW
GT heat rate (LHV) | 8314.1 | kJ/kWh
GT heat input (LHV) | 981.52 | MW
Fuel gas flow | 20.672 kg/s = 101,596 | Sm3/h
Compressor inlet air flow | 776.01 | kg/s
GT exhaust flow / temperature | 796.68 / 640.0 | kg/s / degC
GT generator efficiency | 98.9 | %
GT losses other than generator (lube oil, radiation) | 3.8 | MW
Performance gas heater duty | 9.46 | MW
HRSG heat transferred to water/steam | 500.83 | MW
HRSG heat loss (casing, % of gas-side duty) | 0.4 | %
Stack temperature | 80.5 | degC
ST output at generator terminals | 200.89 | MW
ST mechanical / generator efficiency | 99.55 / 98.80 | %
Condenser pressure | 34.44 | mbar(a)
Condenser duty | 290.03 | MW
Circulating water flow (7 K rise) | 10,181 kg/s = 36,058 | m3/h
Power island gross output | 625.89 | MW
Power island gross heat rate (LHV) | 5645.5 | kJ/kWh

## Streams SRC-NG-100
IEC-ALP-PER-001 Rev A - Streams SRC-NG-100
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | h kJ/kg
1 | Ambient air to GT compressor inlet | air | AMB | GT | 776.01 | 1.01 | 15 | -
2 | Fuel gas at performance gas heater inlet (IEC terminal point) | fuel_gas | FGS | FGH | 20.67 | 38 | 25 | -
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 20.67 | 35.5 | 215 | -
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 796.68 | 1.05 | 640 | -
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 796.68 | 1.01 | 80.5 | -
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 100.15 | 187 | 600 | -
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 100.15 | 181.5 | 598.5 | -
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 100.15 | 40.2 | 366.2 | -
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 100.15 | 39.5 | 365.2 | -
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 17.34 | 40.3 | 330 | -
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 117.49 | 37.6 | 600 | -
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 117.49 | 36.2 | 598.5 | -
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 11.39 | 5.4 | 300 | -
14 | LP steam at ST LP admission | steam | PIPE | ST | 11.39 | 5.05 | 299 | -
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 117.49 | 4.95 | 309.2 | -
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 128.88 | 0.0344 | 26.4 | 2361
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 128.88 | 0.0344 | 26.3 | -
18 | Condensate at CEP discharge | water | CEP | CMIX | 128.88 | 16 | 26.5 | -
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 12.48 | 43 | 75 | -
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 141.36 | 15.5 | 30.9 | -
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 129.97 | 5.9 | 158.1 | -
22 | HP feedwater at BFP discharge | water | BFP | HRSG | 100.15 | 209 | 161.8 | -
23 | IP feedwater at BFP interstage outlet | water | BFP | HRSG | 29.82 | 46 | 158.9 | -
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 12.48 | 43.3 | 248 | -
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10181.4 | 2.5 | 16 | -
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10181.4 | 1.7 | 23 | -

## Exhaust composition
IEC-ALP-PER-001 Rev A - Exhaust composition
N2 | O2 | Ar | CO2 | H2O
73.85 | 11.12 | 0.88 | 4.47 | 9.67

## HRSG profile
IEC-ALP-PER-001 Rev A - HRSG profile
HRSG section (gas flow order) | Gas in degC | Gas out degC | Duty MW
HPSH / RH | 640 | 450.6 | 176.83
HPEVAP | 450.6 | 371.6 | 71.38
HPECO2 | 371.6 | 299.9 | 63.71
IPSH | 299.9 | 295.1 | 4.19
IPEVAP | 295.1 | 261 | 29.89
HPECO1 / IPECO | 261 | 201.5 | 51.64
LPSH | 201.5 | 197.4 | 3.51
LPEVAP | 197.4 | 166.2 | 26.83
CPH | 166.2 | 80.5 | 72.85

## Ambient cases
IEC-ALP-PER-001 Rev A - Ambient cases
Ambient degC | RH % | Seawater degC | GT MW | GT HR kJ/kWh | Exhaust kg/s | Exhaust degC | ST MW | Gross MW | Gross HR kJ/kWh | Condenser mbar | Gas Sm3/h | Remark
-8 | 80 | 6.9 | 470 | 8089 | 823.5 | 634 | 211.2 | 681.2 | 5581 | 19.8 | 109310 | GT at output limit 470 MW
-4.8 | 80 | 8 | 470 | 8131 | 832.5 | 635.7 | 213.5 | 683.5 | 5590 | 21.2 | 109874 | GT at output limit 470 MW
5 | 75 | 11 | 452.8 | 8217 | 829.2 | 634.8 | 209.9 | 662.7 | 5615 | 25.5 | 106984
15 | 70 | 16 | 425 | 8314 | 796.7 | 640 | 200.9 | 625.9 | 5646 | 34.4 | 101596
25 | 55 | 22 | 397.2 | 8411 | 761.8 | 645.2 | 190.6 | 587.8 | 5684 | 48.7 | 96053
32.8 | 45 | 24 | 372.8 | 8501 | 729.5 | 649.3 | 183.4 | 556.2 | 5698 | 54.4 | 91121
40 | 35 | 27 | 348.2 | 8595 | 695.9 | 653 | 174.8 | 523 | 5722 | 64.2 | 86055

## Part load
IEC-ALP-PER-001 Rev A - Part load
GT load % | GT MW | GT HR kJ/kWh | Exhaust kg/s | Exhaust degC | ST MW | Gross MW | Gross HR kJ/kWh
100 | 425 | 8314 | 796.7 | 640 | 200.9 | 625.9 | 5646
80 | 340 | 8746 | 696.5 | 640 | 175.3 | 515.3 | 5771
60 | 255 | 9436 | 593.1 | 640 | 149 | 404 | 5957
50 | 212.5 | 9894 | 541 | 632 | 132.7 | 345.2 | 6090
40 | 170 | 10600 | 496.9 | 615 | 116 | 286 | 6300