## Register
Alpilla 600 MW Combined Cycle Power Plant - Tie-in / Terminal Point Register
engine tie_in_register v1.0.0 ¦ generated 2026-09-28T04:17:36Z by SETUP ¦ data d8600cf5aed7f9fd ¦ pressures barg, temperatures degC
ID | Contract | Category | Status | Agreed by | Agreed in | Service | Medium | Location | Size | Connection | Scope break (boundary) | Employer side (Owner / EPC) | Contractor side (EPC / IEC) | Isolation | Protection | Metering | Design p barg | Design T degC | Op p min barg | Op p max barg | Op T min degC | Op T max degC | Flow normal | Flow max | Flow unit | Density kg/m3 | Limited | U nom kV | U min kV | U max kV | Isc kA | Isc rating kA | pf | HMB stream | HMB check | HMB power | Upstream | Chain dp bar | Quality | Available by | Needed by | Scope | Related scope | Operating conditions (text) | Basis | Remarks
TP-A1 | ALP-EPC-001 | land_access | agreed | OWNER IEPC | TQ-030 | Temporary construction area (5 ha) | land | E 0-180, N 320-600 (5.04 ha), north of the plot, west of the access road |  | Fenced 5.04 ha field E 0-180, N 320-600 | Owner: lease of the field until Taking-Over, free of charge to the Contractor. Contractor: fencing, surfacing, drainage, temporary facilities and restoration to the original condition. | Lease of the 5 ha field until Taking-Over, free of charge to the Contractor | Laydown, pre-assembly, contractor facilities; restoration at the end | [26 empty] | 2027-02-01 | 2027-03-01 |  |  |  | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0010 | Lease starts 2027-02-01 (TQ-030).
TP-A2 | ALP-EPC-001 | land_access | agreed | OWNER IEPC | TQ-030 | Site (plot) handover | land | Plot E 0-400, N 0-300 (plant grid), levelled to +15.0 m |  | Plot boundary per land-use plan with boundary survey monuments | Owner: plot per land-use plan, levelled to +15.0 m with compaction records, boundary monuments, free of encumbrances except the buried 11 kV utility cable along the east boundary (E 390, N 0-300), which the Owner relocates outside the plot by 2027-06-30; the east strip E 370-400 is not available to the Contractor before then. Contractor: everything within the plot boundary from the access date, incl. demolition of the abandoned foundations (E 300-360, N 20-60) and the 10 m channel buffer. | Plot free of encumbrances, levelled to +15.0 m, boundary monuments; relocation of the buried 11 kV cable (E 390) by 2027-06-30 | All works within the plot from the access date | [26 empty] | 2026-11-02 | 2026-11-16 | SC-001 |  | East strip E 370-400 available 2027-06-30 (needed by the Contractor 2027-09-01 for the gas station civil works). | source:SRC-OWNR-0005 source:SRC-OWNR-0010
TP-CW1 | ALP-EPC-001 | marine | agreed | OWNER IEPC | TQ-030 | Seawater intake head | seawater | About 650 m offshore at -12 m | about 2 x DN2200 (Contractor to size) | Offshore intake head with velocity cap at -12 m | Owner: seabed survey and marine permit for the intake location. Contractor: intake head (velocity cap <= 0.15 m/s), pipelines, screens and pump house (SC-016, SC-042). | Seabed survey and marine permit | Intake head, pipelines, pump house | [7 empty] | 6.9 | 27 | 36050 | 40000 | m3/h | 1025 | [7 empty] | 25 | flow_temperature |  |  |  | source:SRC-OWNR-0002 requirement:ER-02.04 | 2027-04-30 | 2027-10-01 | SC-016 |  | 6.9-27.0 degC | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0010 | Capacity includes about 2,000 m3/h for SWRO and electro-chlorination in addition to the 38,000 m3/h CW design flow; pressure at the intake is hydrostatic (HMB pressure check not applicable).
TP-CW2 | ALP-EPC-001 | marine | agreed | OWNER IEPC | TQ-030 | Outfall diffuser | seawater | About 350 m offshore, at least 250 m from the intake |  | Outfall diffuser about 350 m offshore at -8 m | Owner: marine permit and discharge permit (EIA conditions). Contractor: outfall pipeline and diffuser; treated effluents (SC-020, SC-057) join the outfall upstream of the discharge monitoring. | Marine permit | Outfall pipeline and diffuser | [7 empty] | 12 | 34.5 | 36050 | 40000 | m3/h | 1025 | [7 empty] | 26 | flow_temperature |  |  |  | requirement:ER-08.04 requirement:ER-08.05 source:SRC-OWNR-0007 | 2027-04-30 | 2027-10-01 | SC-016 | SC-020 SC-057 |  | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0010 | Discharge limits: <= 3 K excess at the edge of the 100 m mixing zone, residual chlorine <= 0.1 mg/l; pressure at the diffuser is hydrostatic (HMB pressure check not applicable).
TP-D1 | ALP-EPC-001 | civil | agreed | OWNER IEPC | TQ-030 | Storm water discharge | storm water | Western stream channel (max 2 m3/s) or to sea |  | Contractor outlet structure with energy dissipation at the western stream channel | Owner: water authority consent for the discharge. Contractor: separate clean/oily drainage, oil interceptors (ER-09.06), outlet structure on the plot boundary and the channel protection within 5 m of the outlet. | Water authority consent | Site drainage, oil interceptors, outlet structure | [10 empty] | 2 | m3/s | 1000 | [12 empty] | requirement:ER-09.06 source:SRC-OWNR-0007 | 2026-11-02 | 2027-01-15 |  |  |  | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0010
TP-E1 | ALP-EPC-001 | electrical | agreed | OWNER IEPC | TQ-030 | Grid connection 380 kV | electricity | Line gantry at the north-west corner | 380 kV, 2 circuits | Line-side terminals of the Contractor's tension insulator strings on the gantry | Owner (line contractor): OHL, conductors and OPGW strung to the tension insulator strings on the Contractor's line gantry, incl. the line clamps. Contractor: gantry, insulator strings and hardware, jumpers and downleads to the GIS outdoor bushings, surge arresters, OPGW joint box on the gantry and fibre to the telecom room. | Double-circuit 380 kV OHL up to the dead-end tower, conductors to the gantry | Gantry, GIS switchyard, protection and metering | Contractor GIS line bay circuit breaker, line disconnector and line earthing switch; Owner/TSO breaker at the remote end (Kiyi substation). | Export limiter in the plant control system: 640 MW net at the 380 kV revenue meters (TQ-027); line differential 87L main 1 / main 2 with the remote end (plant end by the Contractor, remote end by the Owner), settings coordinated with the TSO (ER-18.02). | Revenue metering class 0.2S on both line bays (SC-035), TSO approved. | [7 empty] | 640 | MW |  | TRUE | 380 | 342 | 420 | 50 | 50 |  |  |  | net |  |  | source:SRC-OWNR-0006 requirement:ER-11.01 | 2028-07-15 | 2028-07-22 | SC-030 | SC-031 SC-048 | 380 kV nominal, 420 kV highest; 360-410 kV normal, 342-420 kV up to 30 min; 49.0-51.0 Hz; short-circuit 12-40 kA (2029), 50 kA (2035 planning); connection capacity 640 MW export / 40 MW import (ALP-OWN-ELE-001). | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0009 source:SRC-OWNR-0010 | Short-circuit values include the Alpilla generators' contribution (TSO, TQ-031). Reactive capability per ER-04.08 at the generator terminals (TQ-032).
TP-E2 | ALP-EPC-001 | electrical | agreed | OWNER IEPC | TQ-030 | Construction power | electricity | North gate | 34.5 kV / 5 MVA | 34.5 kV cable terminations at the outgoing side of the utility metering kiosk | Owner (distribution company): 34.5 kV line/cable to the metering kiosk at the north gate, incl. the utility meter and load-break switch. Contractor: cable from the kiosk outgoing terminals, 34.5 kV ring main unit and construction substations. | 34.5 kV connection, 5 MVA, metering | Construction substations and distribution | Utility load-break switch in the kiosk; Contractor RMU incoming switch with earthing switch. | Contractor RMU incoming circuit breaker (overcurrent / earth fault) graded with the utility. | Utility meter in the kiosk (construction energy paid by the Contractor, SC-045). | [7 empty] | 5 | MVA |  |  | 34.5 | 31.05 | 37.95 | 12.5 | 16 | [7 empty] | 2027-02-28 | 2027-03-15 | SC-045 | SC-045 | 34.5 kV +/- 10 %, 5 MVA, prospective short-circuit 12.5 kA (distribution company). | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0009 source:SRC-OWNR-0010
TP-G1 | ALP-EPC-001 | process | agreed | OWNER IEPC | TQ-030 | Natural gas supply | natural gas | North-east plot corner, flange at EL +14.0 | 16 in (DN400), CL600 | ASME B16.5 CL600 RF weld-neck flange, 16 in | Owner: spur line, tap valve station, remotely operable isolation valve and monolithic insulating joint; scope break at the downstream flange of the insulating joint. Contractor: counter-flange, gasket, stud bolts and everything downstream (gas receiving and metering station, SC-028). The Owner's cathodic protection ends at the insulating joint; plant earthing starts downstream. | 16-inch spur line (4.5 km), tap valve station, isolation valve and insulating joint | Gas receiving and metering station from the inlet flange | Owner boundary isolation valve (operated by the network operator); Contractor station inlet ESD valve. | Owner pipeline MAOP 75 barg; the Contractor's station is designed for 75 barg up to the regulators. | Fiscal metering by the Contractor in the station, approved by the network operator (ER-18.03). | 75 | 50 | 45 | 70 | 5 | 25 | 101600 | 115000 | Sm3/h | 0.7325 | [12 empty] | source:SRC-OWNR-0003 requirement:ER-03.06 | 2028-06-30 | 2028-08-15 | SC-028 | SC-027 SC-047 | Normal 55-65 barg; minimum 45 barg for full load; exceptional 40 barg up to 72 h/year (GT load limited, ER-03.03); MOP 70 / MAOP 75 barg; 5-25 degC; 115,000 Sm3/h firm (density 0.7325 kg/Sm3 at 15 degC, reference gas). | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0009 source:SRC-OWNR-0010
TP-L1 | ALP-EPC-001 | process | agreed | OWNER IEPC | TQ-030 | LDO supply | light diesel oil | North gate (road tankers) | 4 in tanker coupling (API RP 1004 bottom loading / dry-break) | Dry-break tanker coupling at the Contractor's unloading bays | Owner (LDO supplier): road tankers delivered to the unloading bays, tanker hoses and coupling halves on the tanker, first fill of the storage tanks (SC-055). Contractor: unloading bays, coupling halves on the plant side, pumps, metering, storage and treatment. | LDO supply contract (up to 25 trucks/day), first fill | Unloading station and storage | Tanker bottom valve (supplier); Contractor unloading valve and ESD at each bay. | Contractor unloading pumps relief; bay earthing and overfill interlock (tanker earthing permissive). | Contractor unloading flow meter per bay; tanker delivery notes (Owner supplier). | 10 | 50 | 0 | 3 | 0 | 40 | 100 | 150 | m3/h | 835 | [12 empty] | source:SRC-OWNR-0004 requirement:ER-03.07 | 2028-09-01 | 2028-11-01 | SC-052 | SC-055 SC-052 | Up to 25 trucks/day (about 30 m3 each); 4 bays at about 100 m3/h each unloading pump set; LDO per TS EN 590 based specification. | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0010
TP-M1 | ALP-EPC-001 | marine | agreed | OWNER IEPC | TQ-030 | Temporary barge landing | heavy transport | Public coastal strip south of the plot |  | Temporary ro-ro barge landing on the public coastal strip | Owner: coastal permit (application by 2027-04-30 based on the Contractor's design). Contractor: design, construction, operation, removal and reinstatement of the barge landing; heavy haul road to the site. | Coastal permit: application by 2027-04-30 if the Contractor's permit design is received by 2027-03-31; permit targeted by 2027-09-30 | Design, construction, operation and removal of the landing; marine works only 1 October - 30 April | [26 empty] | 2027-09-30 | 2027-11-01 |  |  | Heaviest pieces (IEC-ALP-REQ-001 section 10): GT core engine 405 t (13.2 x 5.9 x 5.6 m, about 480 t gross on SPMT), GT generator stator 340 t, GT GSU 268 t; landing and haul road designed for 480 t gross SPMT loads. | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0007 source:SRC-OWNR-0009 source:SRC-OWNR-0010
TP-R1 | ALP-EPC-001 | land_access | agreed | OWNER IEPC | TQ-030 | Road access | road | North gate |  | Existing 6 m asphalt road at the north gate (E 200, N 300) | Owner: existing road to the state road up to the north gate. Contractor: site roads from the gate, road condition survey before and after construction and repair of construction damage; abnormal loads via TP-M1. | Existing 6 m asphalt road to the state road | Site roads and gate | [26 empty] | 2026-11-02 | 2026-11-16 |  |  | 6 m asphalt, state road bridges limited to 120 t gross vehicle weight; components above about 90 t via the barge landing TP-M1 (ALP-OWN-GEN-001 section 3). | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0009 source:SRC-OWNR-0010
TP-S1 | ALP-EPC-001 | permit_service | agreed | OWNER IEPC | TQ-030 | Sanitary wastewater | sewage | None - no municipal sewer available |  |  | No physical connection (no municipal sewer). The Contractor's packaged sanitary treatment plant (SC-057) discharges treated effluent into the outfall (TP-CW2) within the Owner's discharge permit. | Nothing (no sewer) | Packaged sanitary treatment plant (SC-057); treated effluent to the outfall | [25 empty] | source:SRC-OWNR-0007 |  |  | SC-057 | SC-020 |  | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0010
TP-T1 | ALP-EPC-001 | control | agreed | OWNER IEPC | TQ-030 | Telecommunication | fibre | North gate |  | 2 x HDPE ducts with draw pits at the plot boundary (two operators) | Owner: operators' fibre in ducts up to the boundary draw pits. Contractor: ducts and fibre from the draw pits to the telecom room, telecom equipment. | Fibre ducts of two operators to the plot boundary | Site telecom network and SCADA links | - | [25 empty] | 2027-06-30 | 2028-05-01 | SC-035 | SC-044 |  | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0009 source:SRC-OWNR-0010
TP-T2 | ALP-EPC-001 | control | agreed | OWNER IEPC | TQ-030 | Emission data link to the environmental authority | data | CEMS data logger in the control building |  | Authority continuous emission monitoring protocol over the public network (VPN), per the Ministry's data-link rules | Owner: registration with the Ministry of Environment continuous emission monitoring centre, the operator credentials and the data-link agreement. Contractor: CEMS (SC-038), data acquisition system, firewall and VPN router in the control building; scope break at the router's public network port. | Registration of the plant with the Ministry's continuous emission monitoring centre, credentials, connection agreement | CEMS, data acquisition and the data link (SC-038) up to the Ministry server interface | - | [25 empty] | 2028-08-01 | 2028-10-02 | SC-038 |  |  | source:SRC-OWNR-0005 source:SRC-OWNR-0010
TP-T3 | ALP-EPC-001 | control | agreed | OWNER IEPC | TQ-030 | TSO SCADA and revenue metering link | data | TSO RTU and metering cubicle in the control building |  | IEC 60870-5-104 over OPGW fibre (TP-E1) and a second path via the operator fibre (TP-T1) | Owner/TSO: signal list, IEC 60870-5-104 profile, TSO end equipment and the OPGW up to the joint box on the Contractor's gantry. Contractor: joint box, fibre to the telecom room, RTU, revenue meters and SCADA tests with the TSO. | TSO signal list and protocol, TSO end of the link, OPGW on the Owner's line | RTU, revenue meters, fibre from the gantry joint box, telecom equipment (SC-035) | - | [25 empty] | 2028-05-01 | 2028-06-01 | SC-035 |  |  | source:SRC-OWNR-0005 source:SRC-OWNR-0010
TP-W1 | ALP-EPC-001 | utility | agreed | OWNER IEPC | TQ-030 | Potable water | water | North gate | DN150 | DN150 PN16 EN 1092-1 flange at the outlet of the Owner's meter pit valve | Owner: municipal main, connection, meter, backflow preventer and outlet valve in the meter pit at the north gate. Contractor: from the outlet flange (counter-flange, gasket, bolts) to storage and distribution. | DN150 municipal main connection and meter, 3 barg, 20 m3/h | Potable water storage and distribution | Owner valves before and after the meter; Contractor isolation valve downstream. | Owner backflow preventer (TS EN 1717). | Municipal meter in the pit. | 10 | 30 | 2.5 | 6 | 5 | 25 | 10 | 20 | m3/h | 1000 | [12 empty] | source:SRC-OWNR-0005 | 2027-02-28 | 2027-03-15 | SC-043 | SC-045 | 2.5-6.0 barg at the meter outlet, 20 m3/h (municipal supply), potable quality per the Turkish drinking water regulation. | decision:DEC-EPCE-0004 source:SRC-OWNR-0005 source:SRC-OWNR-0009 source:SRC-OWNR-0010
IF-01 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Natural gas to GT | natural gas | performance gas heater inlet flange | 12 in (DN300) CL600 | ASME B16.5 CL600 RF weld-neck flange | IEC supplies the performance gas heater inlet flange; EPC supplies the counter-flange, gasket (spiral wound, 316L/graphite), stud bolts and the pipe support nearest the flange, and makes the joint. Hydrotest up to the flange by each party; joint leak test with gas-in by EPC. | EPC: gas from EPC gas receiving/metering station | IEC: performance gas heater inlet flange | EPC: gas station outlet ESD valve (fail-closed, SIL 2, closed by the TCS gas trip) and manual valve with spectacle blind upstream of IF-01. IEC: gas skid stop and control valves. | EPC gas station pressure control: monitor + active regulator, slam-shut set 46 barg, token relief 44 barg; downstream design 63 barg (EN 12186 / ASME B31.8). | Fiscal metering (ultrasonic 2 x 100 % + gas chromatograph) in the EPC gas station; IEC skid flow meter for control only. | 63 | 80 | 36.5 | 41 | 5 | 40 | 20.67 | 23 | kg/s | [8 empty] | 2 |  |  | TP-G1 | 4.7 | requirement:ER-03.06 source:SRC-OWNR-0003 source:SRC-EPCE-0010 | 2028-08-31 | 2028-09-18 |  | SC-029 | Pressure rate of change <= 0.7 bar/s; >= 28 K superheat above hydrocarbon and water dew points; filtration 3 um absolute; below 36.5 barg the TCS load limiter applies (DEC-EPCE-0003). | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-02 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | LDO to GT | LDO | liquid fuel skid inlet flange | 6 in (DN150) CL150 | ASME B16.5 CL150 RF flange | IEC supplies the liquid fuel skid inlet flange; EPC supplies counter-flange, gasket, bolts, the last pipe support and the joint. | EPC: LDO forwarding/treatment system | IEC: liquid fuel skid inlet flange | EPC: LDO ESD valve (fail-closed) and manual valve with spectacle blind at the skid boundary. IEC: skid stop valve. | EPC forwarding pumps: discharge relief to tank set 12 barg (< 16 barg design). | EPC Coriolis meter on the forwarding skid (consumption and performance tests). | 16 | 60 | 3 | 6 | 10 | 45 | 22.41 | 24 | kg/s | [8 empty] | 27 |  |  |  |  | requirement:ER-03.07 source:SRC-OWNR-0004 source:SRC-EPCE-0010 | 2028-11-15 | 2028-12-01 |  | SC-053 SC-054 | LDO treated by the EPC to the GT inlet limits (ER-03.07); filtration 5 um. | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-03 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Demin water for water injection | demin water | water injection skid inlet | 4 in (DN100) CL150 | ASME B16.5 CL150 RF flange | IEC supplies the water injection skid inlet flange (skid with high-pressure pumps by IEC); EPC supplies counter-flange, gasket, bolts and the demin water forwarding pumps. | EPC: demin water storage/pumps | IEC: water injection skid inlet | EPC manual isolation valve and spectacle blind; IEC skid inlet valve. | EPC demin forwarding pumps shut-off head <= 12 barg (< 16 barg design). |  | 16 | 50 | 3 | 6 | 10 | 40 | 13.44 | 15 | kg/s | [8 empty] | 28 | flow_temperature |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-11-15 | 2028-12-01 |  | SC-054 | Water/fuel ratio 0.60 on LDO (TQ-IEC-018). HMB stream 28 is at the IEC skid discharge (60 bar(a)); pressure at IF-03 is 3.0-6.0 barg. | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008 | HMB pressure check not applicable: PER-003 stream 28 is downstream of the IEC injection pumps (TQ-IEC-021 item 3); the injection pump power is part of the IEC GT auxiliaries.
IF-04 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Compressor wash water | demin water | wash skid inlet | 2 in (DN50) CL150 | ASME B16.5 CL150 RF flange | IEC wash skid inlet flange; EPC demin water line, counter-flange, gasket and bolts. | EPC: demin water | IEC: wash skid inlet | EPC manual valve; IEC skid inlet valve. | EPC demin pumps shut-off <= 8 barg. |  | 10 | 50 | 3 | 6 | 10 | 40 | 5 | 10 | m3/h | 1000 | [12 empty] | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-15 | 2028-12-15 |  |  | 5 m3 per wash (off-line), tank filling at up to 10 m3/h. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-05 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | HP steam | steam | HRSG HP SH outlet stop valve, weld end | 12 in P91 (SA-335 P91) | butt-weld end ASME B16.25, IEC pup piece 300 mm | IEC supplies the HP SH outlet stop valve with a 300 mm pup piece (matching material and wall); the field weld, its PWHT and 100 % RT/UT are by EPC, witnessed by IEC. | EPC: main steam piping (EPC) | IEC: HRSG HP SH outlet stop valve, weld end | IEC HP SH outlet motor-operated stop valve and non-return valve. | IEC HRSG HP SH safety valves set <= 196 bar(a), electromatic relief 194 bar(a). |  | 209 | 610 | 59 | 192 | 560 | 600 | 100.16 | 105 | kg/s | [8 empty] | 6 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  | Sliding pressure 60-193 bar(a); attemperation to 600 degC. | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-06 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | HP steam | steam | ST main stop valve inlet, weld end | 12 in P91 (SA-335 P91) | butt-weld end ASME B16.25, IEC pup piece 300 mm | IEC supplies the ST main stop valve with pup piece; field weld, PWHT and NDT by EPC. | EPC: main steam piping (EPC) | IEC: ST main stop valve inlet, weld end | IEC main stop valve (ST trip). | Upstream HRSG HP SH safety valves (IF-05) <= 196 bar(a); MSV casing design 215 bar(a) / 610 degC (TQ-IEC-021 item 1). |  | 214 | 610 | 52 | 186 | 560 | 600 | 100.16 | 105 | kg/s | [8 empty] | 7 |  |  | IF-05 | 6 | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  | ST rated inlet 180 bar(a) / 598 degC per IEC 60045-1; main steam line pressure drop <= 6.0 bar at 105 kg/s. | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-07 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Cold reheat | steam | HP turbine exhaust, weld end | 24 in SA-335 P22 | butt-weld end, IEC pup piece | IEC supplies the HP turbine exhaust nozzle with pup piece and the CRH non-return valve; field weld by EPC. | EPC: cold reheat piping (EPC) | IEC: HP turbine exhaust, weld end | IEC CRH non-return valve (power assisted). | Reheater safety valves on the HRSG (IEC). |  | 51 | 420 | 18 | 41 | 340 | 395 | 100.16 | 105 | kg/s | [8 empty] | 8 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-08 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Cold reheat | steam | HRSG reheater inlet, weld end | 24 in SA-335 P22 | butt-weld end, IEC pup piece | IEC supplies the HRSG reheater inlet with pup piece and the CRH safety valves; field weld by EPC. | EPC: cold reheat piping (EPC) | IEC: HRSG reheater inlet, weld end | None at the HRSG inlet (CRH non-return valve at IF-07). | IEC cold reheat safety valves set 50 bar(a). |  | 51 | 420 | 17 | 41 | 340 | 395 | 100.16 | 105 | kg/s | [8 empty] | 9 |  |  | IF-07 | 1 | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-09 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Hot reheat | steam | HRSG reheater outlet stop valve, weld end | 28 in P91 (SA-335 P91) | butt-weld end, IEC pup piece | IEC supplies the HRSG reheater outlet stop valve with pup piece; field weld, PWHT, NDT by EPC. | EPC: hot reheat piping (EPC) | IEC: HRSG reheater outlet stop valve, weld end | IEC HRH outlet stop valve. | IEC hot reheat safety valves set <= 48 bar(a). |  | 49 | 610 | 17 | 38.5 | 550 | 600 | 117.5 | 125 | kg/s | [8 empty] | 11 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-10 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Hot reheat | steam | ST IP stop-control valve inlet | 28 in P91 (SA-335 P91) | butt-weld end, IEC pup piece | IEC supplies the ST IP stop/control valve with pup piece; field weld, PWHT, NDT by EPC. | EPC: hot reheat piping (EPC) | IEC: ST IP stop-control valve inlet | IEC IP stop valve (ST trip). | Upstream HRH safety valves (IF-09) <= 48 bar(a); IP valve casing design 52 bar(a) / 610 degC (TQ-IEC-021 item 1). |  | 51 | 610 | 15.5 | 38.5 | 550 | 600 | 117.5 | 125 | kg/s | [8 empty] | 12 |  |  | IF-09 | 1.5 | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-11 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | LP steam | steam | HRSG LP SH outlet stop valve | 20 in SA-106 C | butt-weld end | IEC supplies the LP SH outlet stop valve with pup piece; field weld by EPC. | EPC: LP steam piping (EPC) | IEC: HRSG LP SH outlet stop valve | IEC LP SH outlet stop valve and non-return valve. | IEC LP SH safety valve set 8.0 bar(a). |  | 9 | 330 | 1.5 | 5 | 210 | 260 | 11.39 | 16.5 | kg/s | [8 empty] | 13 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-12 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | LP steam | steam | ST LP admission valve inlet | 20 in SA-106 C | butt-weld end | IEC supplies the ST LP admission valve with pup piece; field weld by EPC. | EPC: LP steam piping (EPC) | IEC: ST LP admission valve inlet | IEC LP admission stop valve. | Upstream LP SH safety valve (IF-11) 8.0 bar(a); admission valve casing design 10 bar(a) / 330 degC (TQ-IEC-021 item 1). |  | 9 | 330 | 1.1 | 5 | 210 | 260 | 11.39 | 16.5 | kg/s | [8 empty] | 14 |  |  | IF-11 | 0.4 | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-13 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | HP / IP / LP bypass valves | steam / water | valves supplied loose by IEC (incl. desuperheating) | HP 12 in / IP 28 in / LP 20 in (per valve datasheets) | butt-weld ends; spray water flanges CL2500 (HP) / CL600 (IP, LP) | Loose supply: IEC supplies HP, IP and LP bypass valves with desuperheaters (free issue to site); EPC installs them in its piping, supplies the spray water lines from the BFP discharge/interstage and CEP discharge and all welds. | EPC: installation in EPC piping, spray water from BFP/CEP (EPC) | IEC: valves supplied loose by IEC (incl. desuperheating) | EPC isolation on the spray water lines; bypass valves close on loss of spray water (IEC logic). | HP bypass downstream design 52 bar(a) (CRH); IP/LP bypass downstream 16 bar(a) (IF-14). |  | 214 | 610 | 1 | 192 | 150 | 600 |  | 125 | kg/s | [13 empty] | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-02-01 | 2028-03-01 |  |  | Inlet side most onerous (HP bypass inlet); delivery of the loose valves by 2028-02-01 for piping erection. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-14 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Bypass steam to condenser | steam | condenser neck dump devices (IEC) | 2 x 36 in + 1 x 28 in | butt-weld end at the condenser neck dump devices | IEC supplies the dump devices in the condenser neck with weld ends; EPC supplies the IP/LP bypass downstream piping and the welds. | EPC: IP/LP bypass downstream piping (EPC) | IEC: condenser neck dump devices (IEC) | Bypass valves (IF-13). | Condenser rupture discs (IEC) and bypass trip on high condenser pressure. |  | 15 | 250 | -1 | 12 | 40 | 250 |  | 141.5 | kg/s | [13 empty] | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-05-01 | 2028-06-01 |  |  | Start-up and trip only; 100 % HRH + LP flow. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-15 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Condensate from hotwell | condensate | hotwell outlet nozzle | 20 in (DN500) CL150 | ASME B16.5 CL150 RF flange, vacuum-tight | IEC hotwell outlet nozzle flange; EPC counter-flange, spiral-wound gasket, bolts and CEP suction piping. | EPC: CEP suction piping (EPC) | IEC: hotwell outlet nozzle | EPC motor-operated suction valve per CEP. | Full vacuum design both sides. |  | 2.5 | 80 | -0.995 | -0.9 | 15 | 40 | 128 | 140 | kg/s | [8 empty] | 17 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  | Full vacuum to 3.5 bar(a). | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-16 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Condensate to CPH | condensate | HRSG CPH inlet | 12 in (DN300) CL300 | ASME B16.5 CL300 RF flange | IEC HRSG condensate preheater inlet flange; EPC condensate line, counter-flange, gasket, bolts. | EPC: condensate line (EPC) | IEC: HRSG CPH inlet | EPC motor-operated isolation valve. | EPC CEP shut-off head <= 22 bar(a) at maximum speed (< 25 bar(a) design), verified at pump FAT. |  | 24 | 180 | 12 | 21 | 15 | 45 | 141.37 | 150 | kg/s | [8 empty] | 20 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-17 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | BFP suction | feedwater | HRSG LP drum downcomer outlet nozzle | 16 in (DN400) CL150 | ASME B16.5 CL150 RF flange | IEC LP drum downcomer outlet nozzle flange; EPC BFP suction piping, counter-flange, gasket, bolts. | EPC: BFP suction piping (EPC) | IEC: HRSG LP drum downcomer outlet nozzle | EPC suction isolation valve per BFP. | IEC LP drum safety valves. |  | 9 | 185 | 1.5 | 6 | 130 | 165 | 129.98 | 140 | kg/s | [8 empty] | 21 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  | LP drum normal water level EL +31.5 m; the EPC confirms BFP NPSH with the drum level and suction losses. | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-18 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | HP feedwater | feedwater | HRSG HP ECO1 inlet | 10 in (DN250) CL2500 | butt-weld end (SA-106 C / SA-335 P11) | IEC HRSG HP economiser 1 inlet with pup piece; field weld by EPC. | EPC: HP feedwater piping (EPC) | IEC: HRSG HP ECO1 inlet | EPC HP feedwater motor-operated isolation valve and non-return valve. | EPC BFP shut-off head at maximum speed <= 234 barg (VFD speed limit), verified at pump FAT; minimum-flow recirculation valve. |  | 234 | 200 | 95 | 215 | 130 | 170 | 100.16 | 110 | kg/s | [8 empty] | 22 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-19 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | IP feedwater | feedwater | HRSG IP ECO inlet | 6 in (DN150) CL600 | butt-weld end | IEC HRSG IP economiser inlet with pup piece; field weld by EPC. | EPC: IP feedwater piping (EPC) | IEC: HRSG IP ECO inlet | EPC IP feedwater isolation and non-return valve. | EPC BFP interstage pressure at shut-off <= 58 bar(a), verified at FAT. |  | 59 | 200 | 20 | 48 | 130 | 165 | 29.82 | 33 | kg/s | [8 empty] | 23 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-20 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | FGH water return | feedwater | performance gas heater water outlet | 4 in (DN100) CL600 | ASME B16.5 CL600 RF flange | IEC performance gas heater water outlet flange; EPC return line to the condensate system. | EPC: return line to condensate (EPC) | IEC: performance gas heater water outlet | EPC isolation valve; IEC FGH outlet control valve. | EPC return line designed 60 bar(a) / 260 degC up to and including its pressure-reducing valve at the condensate connection; condensate system relief valve downstream (EPC). |  | 59 | 260 | 18 | 46 | 60 | 90 | 12.48 | 14.5 | kg/s | [8 empty] | 19 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-21 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | HRSG blowdown | water | continuous / intermittent blowdown valves outlet | 2 in / 3 in | socket-weld / butt-weld ends | IEC supplies the continuous and intermittent blowdown valves (two in series); scope break at the outlet weld of the second valve; EPC blowdown piping, flash tanks and silencers. | EPC: blowdown tanks (EPC) | IEC: continuous / intermittent blowdown valves outlet | IEC two valves in series (ASME I PG-58.3.6). | EPC blowdown piping designed for the drum design pressure up to the flash tank inlet. |  | 209 | 370 | 0 | 5 | 100 | 370 | 1 | 5 | kg/s | [13 empty] | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  | Continuous blowdown up to 1 % of HP flow; intermittent 5 kg/s for 30 s. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-22 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | HRSG drains and vents | water/steam | drain/vent valves outlet (IEC) | various (1 in - 3 in) | socket-weld / butt-weld ends | Scope break at the outlet weld of the IEC drain/vent valve (second isolation); EPC drain collection, atmospheric flash tanks and vent silencers. | EPC: drain collection, flash tanks, silencers (EPC) | IEC: drain/vent valves outlet (IEC) | IEC two valves in series on all pressure part drains. | EPC drain headers designed for the highest upstream design up to the first flash tank. |  | 209 | 610 | 0 | 1 | 40 | 610 |  | 10 | kg/s | [13 empty] | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  | Start-up drains. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-23 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Chemical dosing | chemicals | dosing nozzles on drums/condensate | 1 in | socket-weld, IEC root valve | IEC dosing nozzles with root valves on the drums; EPC dosing skids and lines. | EPC: dosing skids and lines (EPC) | IEC: dosing nozzles on drums/condensate | IEC root valve + EPC isolation and check valve. | EPC dosing pump relief set below the line design. |  | 234 | 100 | 3 | 215 | 5 | 40 |  | 0.1 | m3/h | 1000 | [12 empty] | source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  | Lay-up and optional drum dosing; AVT(O) ammonia dosing into the condensate by EPC. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-24 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Sampling | water/steam | sample nozzles with root valves (IEC) | 1/2 in | socket-weld, IEC root valve | IEC sample nozzles with root valves; EPC sample lines, coolers and the SWAS. | EPC: sample lines, coolers, SWAS (EPC) | IEC: sample nozzles with root valves (IEC) | IEC root valve; EPC isolation at the SWAS. | EPC sample line design = upstream design. |  | 234 | 610 | -1 | 215 | 20 | 600 |  | 0.5 | kg/s | [13 empty] | source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  | Sample points per IEC-ALP-REQ-001 section 4. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-25 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Aqueous ammonia | NH4OH 24.5 % | ammonia injection skid inlet (IEC) | 1 in | ASME B16.5 CL150 RF flange (316L) | IEC ammonia injection skid inlet flange; EPC storage, unloading and forwarding pumps. | EPC: storage, unloading, forwarding pumps (EPC) | IEC: ammonia injection skid inlet (IEC) | EPC ESD valve (fail-closed) and manual valve. | EPC forwarding pump relief 9 barg. |  | 10 | 40 | 3 | 7 | 5 | 40 | 0.125 | 0.5 | t/h | [13 empty] | requirement:ER-06.03 source:SRC-EPCE-0010 | 2028-11-01 | 2028-11-15 |  |  | Aqueous ammonia 24.5 %: 125 kg/h on gas, 480 kg/h on LDO (TQ-IEC-018). | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-26 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Flue gas to stack | flue gas | HRSG outlet transition flange | D 9.2 m | bolted flange with EPC fabric expansion joint | IEC HRSG outlet transition duct flange (drilled); EPC fabric expansion joint, stack, silencer, CEMS and damper (if any). | EPC: stack (EPC), CEMS (EPC) | IEC: HRSG outlet transition flange | None (no stack damper). | HRSG casing design +/- 50 mbar. |  | 0.05 | 200 | 0 | 0.03 | 60 | 120 | 796.7 | 850 | kg/s | [8 empty] | 5 |  |  |  |  | requirement:ER-14.02 | 2028-06-30 | 2028-09-15 |  | SC-010 SC-011 |  | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-27 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Circulating water | seawater | condenser water box flanges (2 inlets, 2 outlets) | 4 x DN1800 | EN 1092-1 PN6 flanges, rubber-lined water boxes | IEC condenser water box inlet/outlet flanges; EPC CW piping (GRP), expansion joints, counter-flanges and bolts. | EPC: CW pipes (EPC) | IEC: condenser water box flanges (2 inlets, 2 outlets) | EPC butterfly valves per inlet and outlet half (condenser half-side operation). | EPC CW pump shut-off head <= 3.5 barg at the condenser; surge analysis for pump trip <= 4 barg; vacuum breaker at the outlet high point. |  | 4 | 40 | 0.5 | 3 | 5 | 35 | 36050 | 38000 | m3/h | 1025 | [7 empty] | 25 |  |  |  |  | source:SRC-OWNR-0002 requirement:ER-02.04 | 2028-09-01 | 2028-09-15 |  | SC-012 | Design flow 38,000 m3/h (DEC-EPCE-0002); condenser pressure drop 0.62 bar clean. | decision:DEC-EPCE-0004 source:SRC-IECE-0005 source:SRC-IECE-0008
IF-28 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Closed cooling water | demin water + inhibitor | IEC coolers inlet/outlet flanges | various (DN50 - DN400) | ASME B16.5 CL150 RF flanges | IEC cooler inlet/outlet flanges; EPC CCW system. | EPC: CCW system (EPC) | IEC: IEC coolers inlet/outlet flanges | EPC valves per consumer. | EPC CCW pump shut-off <= 8 barg. |  | 10 | 60 | 3 | 6 | 20 | 36 | 1055 | 1160 | m3/h | 1000 | [12 empty] | source:SRC-EPCE-0010 | 2028-08-09 | 2028-08-16 |  |  | 9,400 kW; supply <= 36 degC (ST TEWAC) / 38 degC (others). | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-29 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Instrument and service air | air | IEC skids | 1 in - 2 in | ASME B16.5 CL150 RF flanges | IEC skid inlet flanges; EPC compressed air system. | EPC: compressed air system (EPC) | IEC: IEC skids | EPC valve per skid. | EPC air receivers relief 10 barg. |  | 10 | 50 | 6 | 8 | 5 | 45 | 350 | 500 | Nm3/h | 1.293 | [12 empty] | source:SRC-EPCE-0010 | 2028-08-09 | 2028-08-16 |  |  | Instrument air dew point -40 degC at 7 barg (ISO 8573-1 class 1.2.1). | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-30 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Nitrogen | N2 | HRSG lay-up / generator purge connections | 1 in | ASME B16.5 CL150 RF flange | IEC lay-up / purge connections; EPC nitrogen supply. | EPC: N2 supply (EPC) | IEC: HRSG lay-up / generator purge connections | EPC valve + IEC valve. | EPC pressure regulator + relief 9 barg. |  | 10 | 50 | 5 | 8 | 5 | 40 |  | 1000 | Nm3/h | 1.25 | [12 empty] | source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  | 99.9 % N2; 3,000 Nm3 per lay-up event. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-31 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Hydrogen / CO2 | H2 / CO2 | GT generator gas control panel inlet | 1/2 in | compression fitting (316L) | IEC generator gas control panel inlet; EPC bottle racks, regulators and piping. | EPC: bottle racks and piping (EPC) | IEC: GT generator gas control panel inlet | EPC valves at the racks. | EPC regulator + relief 14 barg. |  | 16 | 50 | 8 | 12 | 5 | 40 |  | 60 | Nm3/h | [13 empty] | source:SRC-EPCE-0010 | 2028-08-25 | 2028-09-01 |  |  | H2 99.9 %, 12 Nm3/day; CO2 150 Nm3 per purge. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-32 | ALP-CA-001 | utility | agreed | IEPC IEC | TQ-IEC-021 | Auxiliary steam | steam | gland steam header inlet (IEC) | 4 in (DN100) CL300 | butt-weld end | IEC gland steam header inlet; EPC auxiliary steam line from the auxiliary boiler. | EPC: auxiliary boiler steam (EPC) | IEC: gland steam header inlet (IEC) | EPC isolation valve. | EPC auxiliary steam header relief set 15 barg. |  | 15 | 320 | 8 | 9.5 | 250 | 300 | 4.5 | 7.5 | t/h | [13 empty] | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-30 | 2028-10-16 |  |  | 4.5 t/h gland sealing, 3 t/h HRSG sparging (optional). | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-33 | ALP-CA-001 | control | agreed | IEPC IEC | TQ-IEC-021 | Fire protection | - | GT enclosure CO2 system (IEC) | - | hardwired volt-free contacts + Modbus TCP summary | IEC GT enclosure CO2 fire protection panel terminals; EPC fire alarm panel (NFPA 72), cables, transformer deluge, hydrants. | EPC: fire detection/alarm, transformer deluge, hydrants (EPC) | IEC: GT enclosure CO2 system (IEC) | - | [25 empty] | 2028-08-17 | 2028-08-24 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-34 | ALP-CA-001 | electrical | agreed | IEPC IEC | TQ-IEC-021 | GT GSU HV | electrical | GT GSU HV bushings | 560 MVA | GSU HV air bushings, EPC 420 kV connection to the GIS | IEC GSU HV bushing terminals; EPC conductors/cable, clamps, surge arresters at the bushings and the GIS bay. | EPC: 380 kV connection to GIS (EPC) | IEC: GT GSU HV bushings | EPC GIS generator transformer bay circuit breaker, disconnector and earthing switch; IEC GCB on the LV side. | GSU differential (87T) and overall differential (87G-T) by IEC; GIS bay protection by EPC; trip matrix per IF-41. | [8 empty] | 560 | MVA |  |  | 380 | 342 | 420 | 50 | 50 | 0.85 |  |  | gt_output | TP-E1 |  |  | 2028-07-29 | 2028-08-02 |  | SC-014 | OLTC 400 +/- 8 x 1.25 % (360-440 kV) with generator 21 kV +/- 5 % covers 342-420 kV. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-35 | ALP-CA-001 | electrical | agreed | IEPC IEC | TQ-IEC-021 | ST GSU HV | electrical | ST GSU HV bushings | 270 MVA | GSU HV air bushings, EPC 420 kV connection to the GIS | As IF-34 for the ST GSU. | EPC: 380 kV connection to GIS (EPC) | IEC: ST GSU HV bushings | As IF-34. | As IF-34. | [8 empty] | 270 | MVA |  |  | 380 | 342 | 420 | 50 | 50 | 0.85 |  |  | st_output | TP-E1 |  |  | 2028-07-29 | 2028-08-02 |  | SC-014 | OLTC 400 +/- 8 x 1.25 % with generator 15.75 kV +/- 5 %. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-36 | ALP-CA-001 | electrical | agreed | IEPC IEC | TQ-IEC-021 | UAT supply | electrical | IPB tap-off flange (GT and ST IPB) | 21 kV (GT) / 15.75 kV (ST) | IPB tap-off flange (IEC), EPC MV busduct | IEC IPB tap-off flange between GCB and GSU; EPC UAT, UAT busduct and flexible links. | EPC: UAT and MV busduct (EPC) | IEC: IPB tap-off flange (GT and ST IPB) | IEC tap-off disconnector link; EPC UAT MV circuit breaker. | UAT differential and overcurrent by EPC, integrated in the IEC unit trip matrix. | [8 empty] | 31.5 | MVA |  |  | 21 | 19.95 | 22.05 | 169 | 200 | [7 empty] | 2028-08-09 | 2028-08-16 |  |  | Prospective 169 kA at the GT generator bus (96 kA via GSU + 73 kA generator); ST bus 125 kA. IPB tap-off rated 200 kA sym / 550 kA peak (TQ-IEC-021 item 4). | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-37 | ALP-CA-001 | electrical | agreed | IEPC IEC | TQ-IEC-021 | MV supplies | electrical | SFC isolation transformer, IEC MV consumers | 10.5 kV feeders | cable terminations at the IEC equipment (lugs by EPC) | EPC 10.5 kV feeders and cables up to and including the terminations at the IEC equipment. | EPC: 10.5 kV switchgear feeders (EPC) | IEC: SFC isolation transformer, IEC MV consumers | EPC feeder circuit breaker with earthing switch. | EPC feeder protection. | [8 empty] | 10 | MVA |  |  | 10.5 | 9.45 | 11.55 | 35 | 40 | [7 empty] | 2028-08-09 | 2028-08-16 |  |  | SFC 8.5 MW for 30 min at start-up. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-38 | ALP-CA-001 | electrical | agreed | IEPC IEC | TQ-IEC-021 | LV supplies | electrical | IEC MCCs incoming | 0.4 kV feeders | IEC MCC incoming terminals | EPC 0.4 kV feeders and cables up to the IEC MCC incoming terminals. | EPC: 0.4 kV switchgear feeders (EPC) | IEC: IEC MCCs incoming | EPC feeder breaker; IEC MCC incomer. | EPC feeder protection selective with IEC MCC. | [12 empty] | 0.4 | 0.36 | 0.44 | 50 | 50 | [7 empty] | 2028-08-09 | 2028-08-16 |  |  | Loads per IEC-ALP-REQ-001 section 7.1. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-39 | ALP-CA-001 | electrical | agreed | IEPC IEC | TQ-IEC-021 | DC and UPS | electrical | TCS, protection, emergency oil pumps | 220 V DC / 230 V AC UPS | IEC panel incoming terminals | EPC DC and UPS distribution feeders up to the IEC panel terminals. | EPC: 220 V DC and 230 V AC UPS (EPC) | IEC: TCS, protection, emergency oil pumps | EPC feeder MCB/fuse. | EPC selective fusing. | [12 empty] | 0.22 | 0.187 | 0.242 | [9 empty] | 2028-08-09 | 2028-08-16 |  |  | GT 37 kW / ST 45 kW DC emergency oil pumps, 3 h autonomy; 45 kVA UPS for the TCS. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-40 | ALP-CA-001 | control | agreed | IEPC IEC | TQ-IEC-021 | Control system interface | data | IEC turbine control system (TCS) gateway | OPC UA + Modbus TCP, redundant; hardwired trips | OPC UA + Modbus TCP, redundant fibre; hardwired trips | IEC TCS gateway ports and fibre patch panel in the IEC electronic room; EPC fibre cables, DCS and the firewall between the zones (IEC 62443 zone/conduit). | EPC: plant DCS (EPC) | IEC: IEC turbine control system (TCS) gateway | - | [25 empty] | 2028-06-01 | 2028-06-15 |  | SC-013 | About 2,500 signals. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-41 | ALP-CA-001 | control | agreed | IEPC IEC | TQ-IEC-021 | Protection interface | signals | generator/GSU protection panels | IEC 61850 + hardwired | IEC 61850 (GOOSE/MMS) + hardwired trips | IEC generator/GSU protection panel terminals; EPC switchyard protection, substation automation and TSO SCADA. | EPC: switchyard protection and TSO SCADA (EPC) | IEC: generator/GSU protection panels | - | [25 empty] | 2028-07-29 | 2028-08-02 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-42 | ALP-CA-001 | civil | agreed | IEPC IEC | TQ-IEC-021 | Earthing | electrical | equipment earthing bosses | - | bolted earthing pads (IEC), EPC 240 mm2 Cu risers | IEC equipment earthing pads and internal earthing; EPC earthing grid (IEEE 80) and risers. | EPC: earthing grid (EPC) | IEC: equipment earthing bosses | - | [25 empty] | 2027-10-15 | 2027-11-15 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-43 | ALP-CA-001 | civil | agreed | IEPC IEC | TQ-IEC-021 | Foundations | civil | anchor bolts, sole plates, load data (IEC) | - | anchor bolts / sole plates (IEC supply), grout by EPC to IEC specification | IEC load data, anchor bolts, sole plates and grouting specification; EPC foundation design, construction, cast-in of anchor bolts and grouting. | EPC: foundation design and construction (EPC) | IEC: anchor bolts, sole plates, load data (IEC) | - | [25 empty] | 2027-11-01 | 2027-11-15 |  |  | Loads per IEC-ALP-REQ-001 section 9. | decision:DEC-EPCE-0004 source:SRC-IECE-0008
IF-44 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Condenser tube cleaning balls | seawater + sponge balls | condenser inlet water boxes (injection) and outlet water box flanges (strainers) | 2 x DN150 per inlet half | EN 1092-1 PN10 flanges | IEC ball injection nozzles on the condenser inlet water boxes; EPC tube cleaning system (ball strainers in the outlet lines, recirculation pumps, collectors). | EPC: ball recirculation units, strainers, debris filters, controls | IEC: injection nozzles and outlet flanges on the water boxes | EPC valves at the nozzles. | As IF-27. |  | 4 | 40 | 0.5 | 3.5 | 5 | 35 |  | 200 | m3/h | 1025 | [12 empty] | source:SRC-OWNR-0002 requirement:ER-02.04 | 2028-09-01 | 2028-09-15 |  |  |  | decision:DEC-EPCE-0004 source:SRC-IECE-0008 | added by TQ-IEC-005
IF-45 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | HP attemperation spray water | feedwater | HRSG HP attemperator spray control station inlet | 3 in (DN80) CL2500 | butt-weld end | IEC HP attemperator spray control station inlet (station with control and block valves by IEC); EPC spray water line from the BFP discharge and the weld. | EPC: spray water line from the BFP discharge | IEC: HP attemperator spray control station | EPC isolation valve at the BFP discharge header; IEC block valve. | As IF-18 (BFP shut-off <= 234 barg). |  | 234 | 200 | 95 | 215 | 130 | 170 |  | 5 | kg/s | [8 empty] | 29 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  |  | source:SRC-IECE-0008 source:SRC-IECE-0005 decision:DEC-EPCE-0004
IF-46 | ALP-CA-001 | process | agreed | IEPC IEC | TQ-IEC-021 | Reheat attemperation spray water | feedwater | HRSG reheat attemperator spray control station inlet | 2 in (DN50) CL600 | butt-weld end | IEC reheat attemperator spray control station inlet; EPC spray water line from the BFP interstage. | EPC: spray water line from the BFP interstage | IEC: reheat attemperator spray control station | EPC isolation valve at the interstage header; IEC block valve. | As IF-19 (interstage <= 58 bar(a)). |  | 59 | 200 | 20 | 48 | 130 | 170 |  | 3 | kg/s | [8 empty] | 30 |  |  |  |  | requirement:ER-09.03 source:SRC-EPCE-0010 | 2028-09-01 | 2028-09-15 |  |  |  | source:SRC-IECE-0008 source:SRC-IECE-0005 decision:DEC-EPCE-0004

## Checks
Alpilla 600 MW Combined Cycle Power Plant - Tie-in checks
engine tie_in_register v1.0.0 ¦ generated 2026-09-28T04:17:36Z by SETUP ¦ data d8600cf5aed7f9fd ¦ pressures barg, temperatures degC
Point | Check | Result | Detail
IF-01 | completeness | OK | process: complete
IF-01 | HMB flow | OK | stream 2 max 22.36 kg/s (WIN-NG-100) <= capacity 23.00 kg/s (margin +2.8 %), 8 cases
IF-01 | HMB pressure | OK | stream 2: 36.987 - 36.987 barg within 36.5 - 41.0 barg (design 63.0)
IF-01 | HMB temperature | OK | stream 2: 25.0 - 25.0 degC within 5.0 - 40.0 degC (design 80.0)
IF-01 | chain pressure | OK | TP-G1 min 45.0 barg - 4.7 bar = 40.30 barg >= required 36.5 barg
IF-01 | chain design | OK | TP-G1 design 75 barg > 63.0 barg here: protected - EPC gas station pressure control: monitor + active regulator, slam-shut set 46 barg, token relief 44 barg; downstream de
IF-01 | chain flow | OK | capacity here 23.00 kg/s <= TP-G1 23.40 kg/s
IF-01 | dates | OK | available 2028-08-31, needed 2028-09-18: float 18 d
IF-01 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-02 | completeness | OK | process: complete
IF-02 | HMB flow | OK | stream 27 max 22.41 kg/s (SRC-LDO-100) <= capacity 24.00 kg/s (margin +6.6 %), 1 cases
IF-02 | HMB pressure | OK | stream 27: 3.987 - 3.987 barg within 3.0 - 6.0 barg (design 16.0)
IF-02 | HMB temperature | OK | stream 27: 30.0 - 30.0 degC within 10.0 - 45.0 degC (design 60.0)
IF-02 | dates | OK | available 2028-11-15, needed 2028-12-01: float 16 d
IF-02 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-03 | completeness | OK | process: complete
IF-03 | HMB flow | OK | stream 28 max 13.44 kg/s (SRC-LDO-100) <= capacity 15.00 kg/s (margin +10.4 %), 1 cases
IF-03 | HMB temperature | OK | stream 28: 30.0 - 30.0 degC within 10.0 - 40.0 degC (design 50.0)
IF-03 | HMB scope | INFO | stream 28: flow + temperature checked only - see remarks
IF-03 | dates | OK | available 2028-11-15, needed 2028-12-01: float 16 d
IF-03 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-04 | completeness | OK | utility: complete
IF-04 | dates | OK | available 2028-09-15, needed 2028-12-15: float 91 d
IF-04 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-05 | completeness | OK | process: complete
IF-05 | HMB flow | OK | stream 6 max 103.34 kg/s (WIN-NG-100) <= capacity 105.00 kg/s (margin +1.6 %), 9 cases
IF-05 | HMB pressure | OK | stream 6: 92.706 - 191.071 barg within 59.0 - 192.0 barg (design 209.0)
IF-05 | HMB temperature | OK | stream 6: 577.4 - 600.0 degC within 560.0 - 600.0 degC (design 610.0)
IF-05 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-05 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-06 | completeness | OK | process: complete
IF-06 | HMB flow | OK | stream 7 max 103.34 kg/s (WIN-NG-100) <= capacity 105.00 kg/s (margin +1.6 %), 9 cases
IF-06 | HMB pressure | OK | stream 7: 89.936 - 185.369 barg within 52.0 - 186.0 barg (design 214.0)
IF-06 | HMB temperature | OK | stream 7: 575.9 - 598.5 degC within 560.0 - 600.0 degC (design 610.0)
IF-06 | chain pressure | OK | IF-05 min 59.0 barg - 6.0 bar = 53.00 barg >= required 52.0 barg
IF-06 | chain flow | OK | capacity here 105.00 kg/s <= IF-05 105.00 kg/s
IF-06 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-06 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-07 | completeness | OK | process: complete
IF-07 | HMB flow | OK | stream 8 max 103.34 kg/s (WIN-NG-100) <= capacity 105.00 kg/s (margin +1.6 %), 9 cases
IF-07 | HMB pressure | OK | stream 8: 19.633 - 40.476 barg within 18.0 - 41.0 barg (design 51.0)
IF-07 | HMB temperature | OK | stream 8: 357.1 - 387.6 degC within 340.0 - 395.0 degC (design 420.0)
IF-07 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-07 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-08 | completeness | OK | process: complete
IF-08 | HMB flow | OK | stream 9 max 103.34 kg/s (WIN-NG-100) <= capacity 105.00 kg/s (margin +1.6 %), 9 cases
IF-08 | HMB pressure | OK | stream 9: 19.289 - 39.754 barg within 17.0 - 41.0 barg (design 51.0)
IF-08 | HMB temperature | OK | stream 9: 356.1 - 386.6 degC within 340.0 - 395.0 degC (design 420.0)
IF-08 | chain pressure | OK | IF-07 min 18.0 barg - 1.0 bar = 17.00 barg >= required 17.0 barg
IF-08 | chain flow | OK | capacity here 105.00 kg/s <= IF-07 105.00 kg/s
IF-08 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-08 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-09 | completeness | OK | process: complete
IF-09 | HMB flow | OK | stream 11 max 121.56 kg/s (WIN-NG-100) <= capacity 125.00 kg/s (margin +2.8 %), 9 cases
IF-09 | HMB pressure | OK | stream 11: 18.294 - 37.783 barg within 17.0 - 38.5 barg (design 49.0)
IF-09 | HMB temperature | OK | stream 11: 566.0 - 600.0 degC within 550.0 - 600.0 degC (design 610.0)
IF-09 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-09 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-10 | completeness | OK | process: complete
IF-10 | HMB flow | OK | stream 12 max 121.56 kg/s (WIN-NG-100) <= capacity 125.00 kg/s (margin +2.8 %), 9 cases
IF-10 | HMB pressure | OK | stream 12: 17.561 - 36.331 barg within 15.5 - 38.5 barg (design 51.0)
IF-10 | HMB temperature | OK | stream 12: 564.5 - 598.5 degC within 550.0 - 600.0 degC (design 610.0)
IF-10 | chain pressure | OK | IF-09 min 17.0 barg - 1.5 bar = 15.50 barg >= required 15.5 barg
IF-10 | chain flow | OK | capacity here 125.00 kg/s <= IF-09 125.00 kg/s
IF-10 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-10 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-11 | completeness | OK | process: complete
IF-11 | HMB flow | OK | stream 13 max 15.27 kg/s (SRC-LDO-100) <= capacity 16.50 kg/s (margin +7.5 %), 9 cases
IF-11 | HMB pressure | OK | stream 13: 1.783 - 4.586 barg within 1.5 - 5.0 barg (design 9.0)
IF-11 | HMB temperature | OK | stream 13: 218.7 - 251.8 degC within 210.0 - 260.0 degC (design 330.0)
IF-11 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-11 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-12 | completeness | OK | process: complete
IF-12 | HMB flow | OK | stream 14 max 15.27 kg/s (SRC-LDO-100) <= capacity 16.50 kg/s (margin +7.5 %), 9 cases
IF-12 | HMB pressure | OK | stream 14: 1.589 - 4.219 barg within 1.1 - 5.0 barg (design 9.0)
IF-12 | HMB temperature | OK | stream 14: 217.7 - 250.8 degC within 210.0 - 260.0 degC (design 330.0)
IF-12 | chain pressure | OK | IF-11 min 1.5 barg - 0.4 bar = 1.10 barg >= required 1.1 barg
IF-12 | chain flow | OK | capacity here 16.50 kg/s <= IF-11 16.50 kg/s
IF-12 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-12 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-13 | completeness | OK | process: complete
IF-13 | dates | OK | available 2028-02-01, needed 2028-03-01: float 29 d
IF-13 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-14 | completeness | OK | process: complete
IF-14 | dates | OK | available 2028-05-01, needed 2028-06-01: float 31 d
IF-14 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-15 | completeness | OK | process: complete
IF-15 | HMB flow | OK | stream 17 max 133.94 kg/s (WIN-NG-100) <= capacity 140.00 kg/s (margin +4.3 %), 9 cases
IF-15 | HMB pressure | OK | stream 17: -0.993 - -0.952 barg within -0.995 - -0.9 barg (design 2.5)
IF-15 | HMB temperature | OK | stream 17: 17.5 - 36.5 degC within 15.0 - 40.0 degC (design 80.0)
IF-15 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-15 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-16 | completeness | OK | process: complete
IF-16 | HMB flow | OK | stream 20 max 147.33 kg/s (WIN-NG-100) <= capacity 150.00 kg/s (margin +1.8 %), 9 cases
IF-16 | HMB pressure | OK | stream 20: 14.487 - 14.487 barg within 12.0 - 21.0 barg (design 24.0)
IF-16 | HMB temperature | OK | stream 20: 23.0 - 40.0 degC within 15.0 - 45.0 degC (design 180.0)
IF-16 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-16 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-17 | completeness | OK | process: complete
IF-17 | HMB flow | OK | stream 21 max 134.94 kg/s (WIN-NG-100) <= capacity 140.00 kg/s (margin +3.6 %), 9 cases
IF-17 | HMB pressure | OK | stream 21: 2.059 - 5.294 barg within 1.5 - 6.0 barg (design 9.0)
IF-17 | HMB temperature | OK | stream 21: 134.3 - 160.7 degC within 130.0 - 165.0 degC (design 185.0)
IF-17 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-17 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-18 | completeness | OK | process: complete
IF-18 | HMB flow | OK | stream 22 max 103.34 kg/s (WIN-NG-100) <= capacity 110.00 kg/s (margin +6.1 %), 9 cases
IF-18 | HMB pressure | OK | stream 22: 100.266 - 214.270 barg within 95.0 - 215.0 barg (design 234.0)
IF-18 | HMB temperature | OK | stream 22: 135.9 - 163.9 degC within 130.0 - 170.0 degC (design 200.0)
IF-18 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-18 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-19 | completeness | OK | process: complete
IF-19 | HMB flow | OK | stream 23 max 31.59 kg/s (WIN-NG-100) <= capacity 33.00 kg/s (margin +4.3 %), 9 cases
IF-19 | HMB pressure | OK | stream 23: 22.358 - 46.927 barg within 20.0 - 48.0 barg (design 59.0)
IF-19 | HMB temperature | OK | stream 23: 134.6 - 161.4 degC within 130.0 - 165.0 degC (design 200.0)
IF-19 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-19 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-20 | completeness | OK | process: complete
IF-20 | HMB flow | OK | stream 19 max 13.40 kg/s (MIN-NG-100) <= capacity 14.50 kg/s (margin +7.6 %), 8 cases
IF-20 | HMB pressure | OK | stream 19: 19.358 - 43.927 barg within 18.0 - 46.0 barg (design 59.0)
IF-20 | HMB temperature | OK | stream 19: 75.0 - 75.0 degC within 60.0 - 90.0 degC (design 260.0)
IF-20 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-20 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-21 | completeness | OK | process: complete
IF-21 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-21 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-22 | completeness | OK | process: complete
IF-22 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-22 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-23 | completeness | OK | utility: complete
IF-23 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-23 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-24 | completeness | OK | utility: complete
IF-24 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-24 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-25 | completeness | OK | utility: complete
IF-25 | dates | OK | available 2028-11-01, needed 2028-11-15: float 14 d
IF-25 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-26 | completeness | OK | process: complete
IF-26 | HMB flow | OK | stream 5 max 832.46 kg/s (WIN-NG-100) <= capacity 850.00 kg/s (margin +2.1 %), 9 cases
IF-26 | HMB pressure | OK | stream 5: 0.001 - 0.001 barg within 0.0 - 0.03 barg (design 0.05)
IF-26 | HMB temperature | OK | stream 5: 68.2 - 89.7 degC within 60.0 - 120.0 degC (design 200.0)
IF-26 | dates | OK | available 2028-06-30, needed 2028-09-15: float 77 d
IF-26 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-27 | completeness | OK | process: complete
IF-27 | HMB flow | OK | stream 25 max 10196.80 kg/s (WIN-NG-100) <= capacity 10819.44 kg/s (margin +5.8 %), 9 cases
IF-27 | HMB pressure | OK | stream 25: 1.487 - 1.487 barg within 0.5 - 3.0 barg (design 4.0)
IF-27 | HMB temperature | OK | stream 25: 6.9 - 27.0 degC within 5.0 - 35.0 degC (design 40.0)
IF-27 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-27 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-28 | completeness | OK | utility: complete
IF-28 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight)
IF-28 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-29 | completeness | OK | utility: complete
IF-29 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight)
IF-29 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-30 | completeness | OK | utility: complete
IF-30 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-30 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-31 | completeness | OK | utility: complete
IF-31 | dates | INFO | available 2028-08-25, needed 2028-09-01: float 7 d (tight)
IF-31 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-32 | completeness | OK | utility: complete
IF-32 | dates | OK | available 2028-09-30, needed 2028-10-16: float 16 d
IF-32 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-33 | completeness | OK | control: complete
IF-33 | dates | INFO | available 2028-08-17, needed 2028-08-24: float 7 d (tight)
IF-33 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-34 | completeness | OK | electrical: complete
IF-34 | short circuit | OK | prospective 50.0 kA <= rating 50.0 kA
IF-34 | HMB power | OK | max gt_output 470.0 MW (WIN-NG-100) / pf 0.85 = 552.9 MVA <= 560 MVA (margin +1.3 %)
IF-34 | chain voltage | OK | TP-E1 342.0-420.0 kV within 342.0-420.0 kV here
IF-34 | chain short circuit | OK | TP-E1 50.0 kA <= rating 50.0 kA here
IF-34 | dates | INFO | available 2028-07-29, needed 2028-08-02: float 4 d (tight)
IF-34 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-35 | completeness | OK | electrical: complete
IF-35 | short circuit | OK | prospective 50.0 kA <= rating 50.0 kA
IF-35 | HMB power | OK | max st_output 207.9 MW (WIN-NG-100) / pf 0.85 = 244.6 MVA <= 270 MVA (margin +9.4 %)
IF-35 | chain voltage | OK | TP-E1 342.0-420.0 kV within 342.0-420.0 kV here
IF-35 | chain short circuit | OK | TP-E1 50.0 kA <= rating 50.0 kA here
IF-35 | dates | INFO | available 2028-07-29, needed 2028-08-02: float 4 d (tight)
IF-35 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-36 | completeness | OK | electrical: complete
IF-36 | short circuit | OK | prospective 169.0 kA <= rating 200.0 kA
IF-36 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight)
IF-36 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-37 | completeness | OK | electrical: complete
IF-37 | short circuit | OK | prospective 35.0 kA <= rating 40.0 kA
IF-37 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight)
IF-37 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-38 | completeness | OK | electrical: complete
IF-38 | short circuit | OK | prospective 50.0 kA <= rating 50.0 kA
IF-38 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight)
IF-38 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-39 | completeness | OK | electrical: complete
IF-39 | dates | INFO | available 2028-08-09, needed 2028-08-16: float 7 d (tight)
IF-39 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-40 | completeness | OK | control: complete
IF-40 | dates | OK | available 2028-06-01, needed 2028-06-15: float 14 d
IF-40 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-41 | completeness | OK | control: complete
IF-41 | dates | INFO | available 2028-07-29, needed 2028-08-02: float 4 d (tight)
IF-41 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-42 | completeness | OK | civil: complete
IF-42 | dates | OK | available 2027-10-15, needed 2027-11-15: float 31 d
IF-42 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-43 | completeness | OK | civil: complete
IF-43 | dates | OK | available 2027-11-01, needed 2027-11-15: float 14 d
IF-43 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-44 | completeness | OK | process: complete
IF-44 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-44 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-45 | completeness | OK | process: complete
IF-45 | HMB flow | OK | stream 29 max 2.06 kg/s (MAX-NG-100) <= capacity 5.00 kg/s (margin +58.8 %), 4 cases
IF-45 | HMB pressure | OK | stream 29: 143.744 - 194.605 barg within 95.0 - 215.0 barg (design 234.0)
IF-45 | HMB temperature | OK | stream 29: 147.6 - 158.7 degC within 130.0 - 170.0 degC (design 200.0)
IF-45 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-45 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
IF-46 | completeness | OK | process: complete
IF-46 | HMB flow | OK | stream 30 max 0.95 kg/s (MAX-NG-100) <= capacity 3.00 kg/s (margin +68.4 %), 4 cases
IF-46 | HMB pressure | OK | stream 30: 31.811 - 41.799 barg within 20.0 - 48.0 barg (design 59.0)
IF-46 | HMB temperature | OK | stream 30: 145.7 - 155.9 degC within 130.0 - 170.0 degC (design 200.0)
IF-46 | dates | OK | available 2028-09-01, needed 2028-09-15: float 14 d
IF-46 | agreement | OK | agreed by IEPC, IEC (TQ-IEC-021)
TP-A1 | completeness | OK | land_access: complete
TP-A1 | dates | OK | available 2027-02-01, needed 2027-03-01: float 28 d
TP-A1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-A2 | completeness | OK | land_access: complete
TP-A2 | dates | OK | available 2026-11-02, needed 2026-11-16: float 14 d
TP-A2 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-CW1 | completeness | OK | marine: complete
TP-CW1 | HMB flow | OK | stream 25 max 10196.80 kg/s (WIN-NG-100) <= capacity 11388.89 kg/s (margin +10.5 %), 9 cases
TP-CW1 | HMB temperature | OK | stream 25: 6.9 - 27.0 degC within 6.9 - 27.0 degC (design None)
TP-CW1 | HMB scope | INFO | stream 25: flow + temperature checked only - see remarks
TP-CW1 | dates | OK | available 2027-04-30, needed 2027-10-01: float 154 d
TP-CW1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-CW2 | completeness | OK | marine: complete
TP-CW2 | HMB flow | OK | stream 26 max 10196.80 kg/s (WIN-NG-100) <= capacity 11388.89 kg/s (margin +10.5 %), 9 cases
TP-CW2 | HMB temperature | OK | stream 26: 14.1 - 33.4 degC within 12.0 - 34.5 degC (design None)
TP-CW2 | HMB scope | INFO | stream 26: flow + temperature checked only - see remarks
TP-CW2 | dates | OK | available 2027-04-30, needed 2027-10-01: float 154 d
TP-CW2 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-D1 | completeness | OK | civil: complete
TP-D1 | dates | OK | available 2026-11-02, needed 2027-01-15: float 74 d
TP-D1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-E1 | completeness | OK | electrical: complete
TP-E1 | short circuit | OK | prospective 50.0 kA <= rating 50.0 kA
TP-E1 | HMB power | INFO | max net 665.3 MW (WIN-NG-100) > 640 MW (margin -3.9 %); limited to 640 MW at this point: Export limiter in the plant control system: 640 MW net at the 380 kV revenue meters (TQ-027); line differential 87L main 1 / main 2 with the remote end (plant end by the Contractor, remote end by the Owner), settings coordinated with the TSO (ER-18.02).
TP-E1 | dates | INFO | available 2028-07-15, needed 2028-07-22: float 7 d (tight)
TP-E1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-E2 | completeness | OK | electrical: complete
TP-E2 | short circuit | OK | prospective 12.5 kA <= rating 16.0 kA
TP-E2 | dates | OK | available 2027-02-28, needed 2027-03-15: float 15 d
TP-E2 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-G1 | completeness | OK | process: complete
TP-G1 | dates | OK | available 2028-06-30, needed 2028-08-15: float 46 d
TP-G1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-L1 | completeness | OK | process: complete
TP-L1 | dates | OK | available 2028-09-01, needed 2028-11-01: float 61 d
TP-L1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-M1 | completeness | OK | marine: complete
TP-M1 | dates | OK | available 2027-09-30, needed 2027-11-01: float 32 d
TP-M1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-R1 | completeness | OK | land_access: complete
TP-R1 | dates | OK | available 2026-11-02, needed 2026-11-16: float 14 d
TP-R1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-S1 | completeness | OK | permit_service: complete
TP-S1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-T1 | completeness | OK | control: complete
TP-T1 | dates | OK | available 2027-06-30, needed 2028-05-01: float 306 d
TP-T1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-T2 | completeness | OK | control: complete
TP-T2 | dates | OK | available 2028-08-01, needed 2028-10-02: float 62 d
TP-T2 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-T3 | completeness | OK | control: complete
TP-T3 | dates | OK | available 2028-05-01, needed 2028-06-01: float 31 d
TP-T3 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
TP-W1 | completeness | OK | utility: complete
TP-W1 | dates | OK | available 2027-02-28, needed 2027-03-15: float 15 d
TP-W1 | agreement | OK | agreed by OWNER, IEPC (TQ-030)
- | HMB coverage | INFO | streams not mapped to a tie-in (internal to one scope, else an interface is missing): 1 Ambient air to GT compressor inlet; 3 Heated fuel gas to GT combustion system; 4 GT exhaust gas to HRSG inlet; 10 IP superheated steam (joins cold reheat inside the HRSG); 15 IP turbine exhaust (crossover, internal); 16 LP turbine exhaust to condenser (UEEP); 18 Condensate at CEP discharge; 24 IP economiser water to performance fuel gas heater
- | coverage | OK | SC-001 (Site boundary per land-use plan): TP-A2
- | coverage | INFO | SC-006 terminal point 'GT exhaust flange to HRSG inlet duct' not referenced by a tie-in
- | coverage | INFO | SC-007 terminal point 'Generator terminals (IPB connection)' not referenced by a tie-in
- | coverage | INFO | SC-009 terminal point 'Generator terminals' not referenced by a tie-in
- | coverage | OK | SC-010 (HRSG outlet to stack): IF-26
- | coverage | OK | SC-012 (Cooling water flanges at condenser water boxes): IF-27
- | coverage | OK | SC-013 (DCS interface (redundant fibre)): IF-40
- | coverage | OK | SC-014 (GSU HV bushings): IF-34, IF-35
- | coverage | OK | SC-016 (Offshore intake head / outfall diffuser): TP-CW1, TP-CW2
- | coverage | OK | SC-020 (Discharge point to outfall): TP-CW2, TP-S1
- | coverage | OK | SC-027 (Owner valve at plant boundary (inlet flange of gas): TP-G1
- | coverage | OK | SC-028 (Inlet flange at plant boundary): TP-G1
- | coverage | OK | SC-030 (380 kV line gantry / cable sealing ends): TP-E1
- | coverage | OK | SC-031 (Line gantry at switchyard): TP-E1
- | coverage | OK | SC-035 (TSO RTU interface in control building): TP-T1, TP-T3
- | coverage | OK | SC-038 (Data link to environmental authority): TP-T2
- | coverage | OK | SC-043 (Site boundary): TP-W1
- | coverage | OK | SC-044 (Site boundary): TP-T1
- | coverage | OK | SC-047 (Gas receiving station inlet): TP-G1
- | coverage | INFO | SC-051 terminal point 'Owner's warehouse' not referenced by a tie-in
- | coverage | OK | SC-052 (Tanker coupling at unloading bays): TP-L1, TP-L1
- | coverage | OK | SC-053 (GT liquid fuel skid inlet flange): IF-02
- | coverage | OK | SC-055 (Tanker coupling at unloading bays): TP-L1
- | coverage | OK | SC-057 (Discharge into the outfall): TP-CW2, TP-S1

## HMB envelope
Alpilla 600 MW Combined Cycle Power Plant - HMB envelope at the tie-ins over 9 cases: MAX-NG-100, MIN-NG-100, SRC-LDO-100, SRC-NG-060, SRC-NG-100, SRC-NG-GT80, SRC-NG-MEL, SUM-NG-100, WIN-NG-100
engine tie_in_register v1.0.0 ¦ generated 2026-09-28T04:17:36Z by SETUP ¦ data d8600cf5aed7f9fd ¦ pressures barg, temperatures degC
Point | Stream | Check | Flow min kg/s | Flow max kg/s | at case | Capacity kg/s | p min barg | p max barg | Range barg | Design barg | T min degC | T max degC | Range degC | Design degC
TP-CW1 | 25 | flow_temperature | 10196.804 | 10196.804 | WIN-NG-100 | 11388.89 | 1.4868 | 1.4868 | - - - |  | 6.9 | 27 | 7 - 27
TP-CW2 | 26 | flow_temperature | 10196.804 | 10196.804 | WIN-NG-100 | 11388.89 | 0.6867 | 0.6867 | - - - |  | 14.1 | 33.4 | 12 - 34
IF-01 | 2 | full | 8.682 | 22.357 | WIN-NG-100 | 23 | 36.9868 | 36.9868 | 36.50 - 41.00 | 63 | 25 | 25 | 5 - 40 | 80
IF-02 | 27 | full | 22.406 | 22.406 | SRC-LDO-100 | 24 | 3.9867 | 3.9867 | 3.00 - 6.00 | 16 | 30 | 30 | 10 - 45 | 60
IF-03 | 28 | flow_temperature | 13.443 | 13.443 | SRC-LDO-100 | 15 | 58.9868 | 58.9868 | 3.00 - 6.00 | 16 | 30 | 30 | 10 - 40 | 50
IF-05 | 6 | full | 50.31 | 103.345 | WIN-NG-100 | 105 | 92.7057 | 191.0708 | 59.00 - 192.00 | 209 | 577.4 | 600 | 560 - 600 | 610
IF-06 | 7 | full | 50.31 | 103.345 | WIN-NG-100 | 105 | 89.9357 | 185.3688 | 52.00 - 186.00 | 214 | 575.9 | 598.5 | 560 - 600 | 610
IF-07 | 8 | full | 50.31 | 103.345 | WIN-NG-100 | 105 | 19.6328 | 40.4757 | 18.00 - 41.00 | 51 | 357.1 | 387.6 | 340 - 395 | 420
IF-08 | 9 | full | 50.31 | 103.345 | WIN-NG-100 | 105 | 19.2888 | 39.7538 | 17.00 - 41.00 | 51 | 356.1 | 386.6 | 340 - 395 | 420
IF-09 | 11 | full | 60.92 | 121.556 | WIN-NG-100 | 125 | 18.2937 | 37.7828 | 17.00 - 38.50 | 49 | 566 | 600 | 550 - 600 | 610
IF-10 | 12 | full | 60.92 | 121.556 | WIN-NG-100 | 125 | 17.5608 | 36.3308 | 15.50 - 38.50 | 51 | 564.5 | 598.5 | 550 - 600 | 610
IF-11 | 13 | full | 6.357 | 15.266 | SRC-LDO-100 | 16.5 | 1.7827 | 4.5857 | 1.50 - 5.00 | 9 | 218.7 | 251.8 | 210 - 260 | 330
IF-12 | 14 | full | 6.357 | 15.266 | SRC-LDO-100 | 16.5 | 1.5887 | 4.2188 | 1.10 - 5.00 | 9 | 217.7 | 250.8 | 210 - 260 | 330
IF-15 | 17 | full | 67.277 | 133.945 | WIN-NG-100 | 140 | -0.9931 | -0.9521 | -0.99 - -0.90 | 2.5 | 17.5 | 36.5 | 15 - 40 | 80
IF-16 | 20 | full | 73.895 | 147.33 | WIN-NG-100 | 150 | 14.4868 | 14.4868 | 12.00 - 21.00 | 24 | 23 | 40 | 15 - 45 | 180
IF-17 | 21 | full | 67.538 | 134.941 | WIN-NG-100 | 140 | 2.0587 | 5.2938 | 1.50 - 6.00 | 9 | 134.3 | 160.7 | 130 - 165 | 185
IF-18 | 22 | full | 50.31 | 103.345 | WIN-NG-100 | 110 | 100.2657 | 214.2697 | 95.00 - 215.00 | 234 | 135.9 | 163.9 | 130 - 170 | 200
IF-19 | 23 | full | 17.228 | 31.595 | WIN-NG-100 | 33 | 22.3577 | 46.9267 | 20.00 - 48.00 | 59 | 134.6 | 161.4 | 130 - 165 | 200
IF-20 | 19 | full | 6.618 | 13.398 | MIN-NG-100 | 14.5 | 19.3577 | 43.9267 | 18.00 - 46.00 | 59 | 75 | 75 | 60 - 90 | 260
IF-26 | 5 | full | 441.951 | 832.455 | WIN-NG-100 | 850 | 0.0008 | 0.0008 | 0.00 - 0.03 | 0.05 | 68.2 | 89.7 | 60 - 120 | 200
IF-27 | 25 | full | 10196.804 | 10196.804 | WIN-NG-100 | 10819.44 | 1.4868 | 1.4868 | 0.50 - 3.00 | 4 | 6.9 | 27 | 5 - 35 | 40
IF-45 | 29 | full | 1.386 | 2.058 | MAX-NG-100 | 5 | 143.7438 | 194.6047 | 95.00 - 215.00 | 234 | 147.6 | 158.7 | 130 - 170 | 200
IF-46 | 30 | full | 0.305 | 0.948 | MAX-NG-100 | 3 | 31.8107 | 41.7987 | 20.00 - 48.00 | 59 | 145.7 | 155.9 | 130 - 170 | 200

## Summary
Category | Points | Agreed / frozen | Draft | Checks WARN | Checks INFO
process | 28 | 28 | 0 | 0 | 1
utility | 10 | 10 | 0 | 0 | 3
electrical | 8 | 8 | 0 | 0 | 8
control | 6 | 6 | 0 | 0 | 2
civil | 3 | 3 | 0 | 0 | 0
marine | 3 | 3 | 0 | 0 | 2
land_access | 3 | 3 | 0 | 0 | 0
permit_service | 1 | 1 | 0 | 0 | 0
Total | 62 | 62 | 0 | 0 | 21