## Register
Alpilla 600 MW Combined Cycle Power Plant - Technical Query Register - ALP-EPC-001 Engineering, Procurement and Construction Contract for the Alpilla 600 MW Combined Cycle Power Plant
engine clarification_register v1.1.0 ¦ generated 2026-09-28T18:13:10Z by SETUP ¦ data ae00813907e24242
TQ | Round | Follows | Raised by | Raised | Discipline | Subject | Question | Proposal | References | Answer | Answered | Status | Outcome | Impact | Price effect (EUR) | Records changed
TQ-001 | 1 |  | Imaginary Electric | 2026-09-18 | process | Site Reference seawater temperature 16.0 degC vs measured 15.4 degC | ER-02.03 and ER-07.08 fix the Site Reference seawater temperature at 16.0 degC. ALP-OWN-MAR-001 section 3 gives a measured annual mean of 15.4 degC at the intake depth. Which value is the contractual reference for PG-01/PG-02 and the condenser design? | Keep 16.0 degC as the contractual reference (our guarantees are priced on it); the measured data is used for the condenser/CW design range only. | requirement:ER-02.03 requirement:ER-07.08 source:SRC-OWNR-0002 design_parameter:DP-CASE-0014 | Confirmed: 16.0 degC remains the contractual Site Reference seawater temperature for all guarantees. The measured data in ALP-OWN-MAR-001 (annual mean 15.4 degC, range 6.9-27.0 degC) is the design range for the condenser and CW system. ER-02.03 is annotated accordingly. | 2026-09-22 | closed | confirmed as is | none |  | requirement/ER-02.03
TQ-002 | 1 |  | Imaginary Electric | 2026-09-18 | process | Gas LHV range: 45.0 MJ/kg (contract) vs 44.2 MJ/kg (network data) | ER-03.02 requires operation for LHV 45.0-50.0 MJ/kg; ALP-OWN-FUL-001 shows 44.2 MJ/kg for 3 % of hours (high N2/CO2 gas). Must the plant operate, and meet guarantees and emissions, below 45.0 MJ/kg? | Plant to operate and meet emission limits over 44.2-50.0 MJ/kg (the Wobbe range 47.2-51.8 is within the combustion system capability); performance guarantees remain at the reference gas. | requirement:ER-03.02 source:SRC-OWNR-0003 design_parameter:DP-CASE-0019 | Accepted. The plant shall operate and meet the emission limits for LHV 44.2-50.0 MJ/kg; performance guarantees apply at the reference gas with corrections per the agreed curves. | 2026-09-22 | closed | requirement changed | technical_only |  | requirement/ER-03.02 design_parameter/DP-CASE-0019
TQ-003 | 1 |  | Imaginary Electric | 2026-09-18 | process | Exceptional minimum gas pressure 40 barg is below the gas turbine requirement | The GT requires at least 43.5 barg at the fuel skid inlet at base load; with about 1.5 bar loss in the gas receiving station we need 45 barg at TP-G1. ALP-OWN-FUL-001 allows 40 barg for up to 72 h/year. Is a gas booster compressor expected, or may the plant transfer to LDO / reduce load during these periods? | No compressor. Below 45 barg the control system transfers automatically to LDO (ER-03.10); availability loss is limited to the transfer. Option price for a booster compressor on request. | requirement:ER-03.03 source:SRC-OWNR-0003 tie_in:TP-G1 | Superseded by TQ-017: load limitation between 40 and 45 barg, no compressor. | 2026-09-22 | closed | contractor proposal accepted | cost
TQ-004 | 1 |  | Imaginary Electric | 2026-09-18 | mechanical | Hydrogen admixture up to 10 vol % | The offered DLN combustion system is released for 5 vol % hydrogen. 10 vol % requires an upgraded combustor set that will be available as a retrofit. ALP-OWN-FUL-001 says 10 % is not firm before 2035. Please confirm the requirement. | 5 vol % without modification and with full guarantees; 10 vol % by future OEM retrofit, with provisions now (fuel system materials, gas detection, control system capacity). | requirement:ER-03.02 source:SRC-OWNR-0003 design_parameter:DP-CASE-0021 | Accepted: 5 vol % hydrogen without modification and with all guarantees; 10 vol % by future OEM retrofit (not in the Contract Price) with provisions now as proposed. | 2026-09-22 | closed | contractor proposal accepted | technical_only |  | requirement/ER-03.02 design_parameter/DP-CASE-0021
TQ-005 | 1 |  | Istanbul EPC | 2026-09-18 | mechanical | LDO alkali metals: delivered 1.0 mg/kg (history 1.8) vs 0.5 mg/kg at GT inlet | ER-03.07 requires Na+K <= 0.5 mg/kg at the GT inlet; ALP-OWN-FUL-002 says delivered LDO may contain up to 1.0 mg/kg and has reached 1.8 mg/kg. ER-03.09 asks for treatment 'if needed'. Is the Owner's intent that treatment is always included? | Treatment is needed: 2 x 100 % centrifugal separators with water washing. Not in our price (the tender was based on on-spec fuel): EUR 1,900,000. | requirement:ER-03.07 requirement:ER-03.09 source:SRC-OWNR-0004 scope_item:SC-053 | Rejected in round 1; resolved by the compromise in TQ-018. | 2026-09-22 | closed | price adjustment | none
TQ-006 | 1 |  | Istanbul EPC | 2026-09-18 | mechanical | LDO storage volume and resupply rate | 72 h at base load on LDO is about 6,900 m3 (two tanks of about 3,500 m3 net). The supplier's maximum of 25 trucks/day (about 825 m3/day) covers only about 36 % of base-load consumption. Please confirm that the plant is not required to run beyond the storage autonomy, and that 'net working volume' excludes heel and fire-fighting reserves. | Two tanks of 3,500 m3 net working volume each (about 4,000 m3 gross); no requirement to sustain operation beyond 72 h. | requirement:ER-03.08 source:SRC-OWNR-0004 tie_in:TP-L1 | Confirmed: two tanks of 3,500 m3 net working volume each (heel and fire-fighting reserves in addition); the plant is not required to operate beyond the storage autonomy. | 2026-09-22 | closed | requirement changed | technical_only |  | requirement/ER-03.08
TQ-007 | 1 |  | Istanbul EPC | 2026-09-18 | structural | Stack height 60 m (contract) vs 65 m (EIA decision) | ER-06.06 and Appendix E state 60 m; ALP-OWN-ENV-001 requires 65 m based on the approved dispersion study. Please confirm 65 m. | 65 m stack; additional cost EUR 180,000 (steel, foundation, platforms). | requirement:ER-06.06 design_parameter:DP-CASE-0043 source:SRC-OWNR-0007 | Accepted: stack height 65 m as required by the EIA decision; price adjustment EUR 180,000 accepted. | 2026-09-22 | closed | price adjustment | cost | 180000 | requirement/ER-06.06 design_parameter/DP-CASE-0043
TQ-008 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Sanitary wastewater: no municipal sewer at the Site | SC-043 assigns 'potable water and sewage connections at site boundary' to the Owner, but ALP-OWN-GEN-001 states that no sewer is available (TP-S1). Who provides sanitary wastewater treatment and discharge? | Contractor provides a packaged sanitary treatment plant (biological + UV), discharge through the outfall within EIA limits; EUR 350,000. | scope_item:SC-043 tie_in:TP-S1 source:SRC-OWNR-0005 source:SRC-OWNR-0007 | Accepted: the Owner provides potable water only. The Contractor provides a packaged sanitary wastewater treatment plant with discharge through the outfall within the EIA limits; EUR 350,000 accepted. | 2026-09-22 | closed | price adjustment | cost | 350000 | scope_item/SC-043 scope_item/SC-057 tie_in/TP-S1 requirement/ER-09.05
TQ-009 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Heavy transport: no jetty, 120 t bridges | The GT (about 460 t), generators (about 330 t) and GSU transformers (about 280 t) cannot use the state road. We plan a temporary barge landing on the 60 m public coastal strip. ALP-OWN-GEN-001 says the Owner can apply for the coastal permit (about 6 months). Please confirm the Owner obtains the permit and the dates. | Contractor designs, builds and removes the landing at its cost (within ER-02.14); Owner applies for the coastal permit within 30 days of receiving the design and obtains it by 2027-09-30, so the landing is built in the Oct 2027 - Apr 2028 window. | requirement:ER-02.14 source:SRC-OWNR-0005 source:SRC-OWNR-0007 | Confirmed: the Contractor designs, builds, operates and removes the temporary barge landing at its cost (ER-02.14). The Owner applies for the coastal permit within 30 days of receiving the Contractor's permit design and will use reasonable endeavours to obtain it by 2027-09-30. Please state when the permit design will be submitted. | 2026-09-22 | closed | owner to provide | time |  | requirement/ER-02.14 tie_in/TP-M1
TQ-010 | 1 |  | Istanbul EPC | 2026-09-18 | electrical | 380 kV line readiness 2028-09-30 is after the back-feed key date 2028-08-02 | Key date KD-010 (back-feed, 2028-08-02) and first fire KD-020 (2028-10-02) need the 380 kV line, which ALP-OWN-ELE-001 and TP-E1 give as ready on 2028-09-30. Please advance the line or move the key dates. | Owner to make TP-E1 available by 2028-07-15, or the key dates KD-010 to KD-040 move by about 2.5 months. | tie_in:TP-E1 source:SRC-OWNR-0006 contract_clause:ALP-EPC-001_9.4 | The Owner will accelerate its 380 kV line contract: TP-E1 will be available by 2028-07-15. The key dates remain unchanged. | 2026-09-22 | closed | owner to provide | none |  | tie_in/TP-E1
TQ-011 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Marine works window and marine permit date | Marine works are prohibited 1 May - 30 September (ALP-OWN-ENV-001). With the marine permit by 2027-04-30 (TP-CW1/CW2) the first usable window is October 2027 - April 2028, which must also carry the barge landing. Can the permit be obtained by 2027-02-28 to use part of the spring 2027 window? | Owner targets 2027-02-28; our programme will not depend on it. | tie_in:TP-CW1 tie_in:TP-CW2 source:SRC-OWNR-0007 | The contractual marine permit date remains 2027-04-30. The Owner will target 2027-02-28 without commitment. | 2026-09-22 | closed | confirmed as is | none
TQ-012 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Construction laydown area | The usable plot area is about 10.6 ha after setbacks, which is not enough for the power block, laydown, pre-assembly and contractor facilities. Will the Owner exercise its option on the 5 ha field north of the plot? | Owner exercises the option and makes the 5 ha available free of charge from 2027-03-01 until Taking-Over; the Contractor restores it. | requirement:ER-02.01 source:SRC-OWNR-0005 | Accepted: the Owner will exercise the option; the 5 ha field north of the plot is available free of charge from 2027-03-01 until Taking-Over; the Contractor restores it to its original condition. | 2026-09-22 | closed | owner to provide | none |  | tie_in/TP-A1 requirement/ER-02.01
TQ-013 | 1 |  | Imaginary Electric | 2026-09-18 | mechanical | Verification of salt removal at the GT air inlet | ER-02.10 requires Na+K at the compressor inlet within the OEM limit at the storm maximum (165 ug/m3). This cannot be tested on demand. Please accept verification by analysis plus monitoring. | Filter design report with OEM confirmation, plus an Na+K air sampler downstream of the filters with 12 months of data reported during the Defects Notification Period. | requirement:ER-02.10 source:SRC-OWNR-0001 | Accepted as proposed: verification by filter design report with OEM confirmation plus 12 months of Na+K air sampling downstream of the filters, reported during the Defects Notification Period. | 2026-09-22 | closed | contractor proposal accepted | technical_only |  | requirement/ER-02.10
TQ-014 | 1 |  | Imaginary Electric | 2026-09-18 | process | Status of the 36 mbar(a) condenser pressure | ER-07.08 sets 36 mbar(a) at SRC and names an ASME PTC 12.2 test, but there is no guarantee or LD for it. Is the condenser pressure a separate guarantee, or is compliance demonstrated through the plant heat rate guarantee? | Design requirement only; compliance through PG-02; PTC 12.2 test for information. | requirement:ER-07.08 guarantee:PG-02 | Accepted: the condenser pressure is a design requirement; contractual compliance is through PG-02. The ASME PTC 12.2 test is carried out for information. | 2026-09-22 | closed | contractor proposal accepted | technical_only |  | requirement/ER-07.08
TQ-015 | 1 |  | Istanbul EPC | 2026-09-18 | electrical | 380 kV switchgear in a C5 salt atmosphere | ER-11.01 asks for a GIS switchyard and ER-02.10 for very-heavy-pollution creepage outdoors. Is an indoor GIS in a building acceptable to the Owner? | Indoor GIS in a ventilated building; only line gantry bushings outdoors. No change to the price. | requirement:ER-11.01 requirement:ER-02.10 | Accepted: indoor GIS in a ventilated building, only the line gantry bushings outdoors; no price change. | 2026-09-22 | closed | contractor proposal accepted | technical_only |  | requirement/ER-11.01
TQ-016 | 1 |  | Istanbul EPC | 2026-09-18 | civil | Relocation of the buried 11 kV cable | The 11 kV cable along the east boundary is relocated only by 2027-06-30 (ALP-OWN-GEN-001). Our layout places the LDO tank farm and warehouse in the east. Can the relocation be completed by 2027-02-28? | Owner to relocate by 2027-02-28; otherwise we re-sequence the east area works. | requirement:ER-02.13 source:SRC-OWNR-0005 | Not possible: the relocation is carried out by the regional utility and 2027-06-30 is its committed date. The Contractor shall sequence the east-area works accordingly. | 2026-09-22 | closed | rejected | none
TQ-017 | 2 | TQ-003 | Imaginary Electric | 2026-09-24 | process | Low gas pressure: booster compressor option vs load limitation | As requested: (a) booster compressor option, 2 x 100 % electric reciprocating units, 115,000 Sm3/h from 40 to 47 barg, about 1.3 MW each: EUR 6,800,000, 14 months delivery, no key-date impact if ordered by 2027-03-31. (b) Estimated operation below 45 barg: about 40 h/year based on the network data. (c) Zero-cost alternative: between 40 and 45 barg the GT reduces load to the pressure-limited load (about 60 % GT load at 40 barg) and stays on gas; transfer to LDO only below 40 barg. Which does the Owner choose? | Alternative (c): load limitation on gas between 40 and 45 barg, no compressor, no price change. | requirement:ER-03.03 requirement:ER-03.10 tie_in:TP-G1 source:SRC-OWNR-0003 | The Owner chooses alternative (c): no booster compressor. Between 40 and 45 barg the plant operates on gas at the pressure-limited load; automatic transfer to LDO only below 40 barg. ER-03.03 is revised. TQ-003 is closed by this answer. | 2026-09-26 | closed | contractor proposal accepted | technical_only |  | requirement/ER-03.03 clarification/TQ-003
TQ-018 | 2 | TQ-005 | Istanbul EPC | 2026-09-24 | commercial | LDO treatment - request to reconsider | ALP-OWN-FUL-002 lists Na+K <= 1.0 mg/kg 'as delivered, not guaranteed by supplier' in the specification table; our tender assumed the tabulated value, which the forwarding filters and water draining handle for most deliveries. The 1.8 mg/kg history is a note on other plants. The requirement 'if needed' is ambiguous for a lump-sum price. We propose a compromise. | Treatment (2 x 100 % centrifugal separators with water washing) included as mandatory scope; cost shared 50/50: EUR 950,000. The Owner adds to its LDO supply contract Na+K <= 1.0 mg/kg with sampling of each delivery. | requirement:ER-03.09 source:SRC-OWNR-0004 contract_clause:ALP-EPC-001_1.3 | Accepted as a compromise: fuel treatment (2 x 100 % centrifugal separators with water washing) becomes mandatory scope; cost shared, price adjustment EUR 950,000. The Owner will require Na+K <= 1.0 mg/kg with sampling of each delivery in its LDO supply contract (decision recorded). TQ-005 is closed by this answer. | 2026-09-26 | closed | price adjustment | cost | 950000 | requirement/ER-03.09 scope_item/SC-053 clarification/TQ-005 decision (LDO supply contract)
TQ-019 | 2 | TQ-009 | Istanbul EPC | 2026-09-24 | civil | Barge landing permit: submission and application dates | We will submit the barge landing permit design by 2027-03-31. Please confirm the Owner's application by 2027-04-30 and that the crossing of the public coastal strip by the intake and outfall pipelines is covered by the marine permit. | Dates as stated; crossing covered by the marine permit (TP-CW1/CW2). | tie_in:TP-M1 tie_in:TP-CW1 tie_in:TP-CW2 | Confirmed: the Owner applies for the coastal permit by 2027-04-30 provided the design is received by 2027-03-31; the crossing of the coastal strip by the intake and outfall pipelines is covered by the marine permit. TQ-009 is closed. | 2026-09-26 | closed | owner to provide | none |  | tie_in/TP-M1 clarification/TQ-009
TQ-020 | 2 | TQ-010 | Istanbul EPC | 2026-09-24 | electrical | Contractual status of the 380 kV line date 2028-07-15 | Please confirm that TP-E1 availability by 2028-07-15 is an Owner obligation under Sub-Clause 2.4 (so that a late line entitles the Contractor to an extension of time under Sub-Clause 9.4), and who coordinates the line energisation with the TSO. | Owner obligation; Owner energises the line with the TSO; Contractor coordinates the plant-side tests. | tie_in:TP-E1 contract_clause:ALP-EPC-001_2.4 contract_clause:ALP-EPC-001_9.4 requirement:ER-18.02 | Confirmed: availability of TP-E1 by 2028-07-15 is an Owner-furnished item under Sub-Clause 2.4; late availability entitles the Contractor to relief under Sub-Clause 9.4. The Owner energises the line with the TSO; the Contractor coordinates the plant-side protection settings and tests. TQ-010 is closed. | 2026-09-26 | closed | owner to provide | none |  | requirement/ER-18.02 clarification/TQ-010
TQ-021 | 2 |  | Imaginary Electric | 2026-09-24 | process | Demineralised water for LDO water injection | Water injection needs about 80 t/h of demineralised water at base load on LDO. ER-09.02 requires storage for 72 h of LDO operation (about 5,800 m3) on top of 3 days of cycle make-up: a very large tank for a fuel used less than 500 h/year. | Demin storage 2 x 1,250 m3 (cycle make-up plus about 24 h of water injection), demin plant sized for continuous water injection at 50 % LDO load, plus a connection for mobile demin trailers. No price change. | requirement:ER-09.02 requirement:ER-03.11 source:SRC-OWNR-0004 | Accepted as proposed: demin storage 2 x 1,250 m3, demin plant sized for continuous water injection at 50 % LDO load, and a connection for mobile demin trailers; no price change. | 2026-09-26 | closed | contractor proposal accepted | technical_only |  | requirement/ER-09.02
TQ-022 | 2 | TQ-001 | Imaginary Electric | 2026-09-24 | process | Seawater temperature correction in the performance test | Following TQ-001, please confirm that the performance test corrects from the measured seawater temperature during the test to the 16.0 degC reference using the agreed correction curves. | Confirmed as stated. | requirement:ER-16.04 requirement:ER-02.03 guarantee:PG-01 guarantee:PG-02 | Confirmed: corrections from the measured test seawater temperature to 16.0 degC with the agreed correction curves. | 2026-09-26 | closed | confirmed as is | none
TQ-023 | 3 |  | Imaginary Electric | 2026-09-26 | process | Reference LDO for the LDO performance guarantees | ALP-OWN-FUL-002 allows FAME (biodiesel) up to 7 % v/v and LHV 42.6-43.2 MJ/kg. PG-15/PG-16 refer to LHV 42.9 MJ/kg but not to FAME or water content, which affect output, heat rate and water injection. Please define the reference LDO for the guarantees. | Reference LDO: LHV 42.9 MJ/kg, FAME 0 %, water 100 mg/kg, H/C per the test fuel analysis; corrections for the actual test fuel by agreed curves. | guarantee:PG-15 guarantee:PG-16 source:SRC-OWNR-0004 requirement:ER-03.07 | Accepted as proposed; PG-15 and PG-16 conditions revised. | 2026-09-27 | closed | contractor proposal accepted | technical_only |  | guarantee/PG-15 guarantee/PG-16
TQ-024 | 3 |  | Istanbul EPC | 2026-09-26 | commercial | Consolidated price and incorporation of the clarifications | All technical queries TQ-001 to TQ-023 are closed or answered. Agreed price adjustments: TQ-007 EUR 180,000, TQ-008 EUR 350,000, TQ-018 EUR 950,000; total EUR 1,480,000 (onshore portion). No time impacts. We propose the Contract Price of EUR 532,480,000 and that the clarification register becomes Appendix I of the Contract, prevailing over Appendix A where it modifies it. Please confirm readiness for signature on 2026-10-15. | Contract Price EUR 532,480,000 (offshore 327,000,000; onshore 205,480,000); Appendix H Owner documents and Appendix I agreed clarifications added to the contract documents. | contract_clause:ALP-EPC-001_A3 contract_clause:ALP-EPC-001_A4 | Confirmed. Contract Price EUR 532,480,000 (offshore EUR 327,000,000; onshore EUR 205,480,000); Appendix H (Owner-provided documents) and Appendix I (agreed clarifications) are added to the contract documents in Article A3. The Contract is agreed and ready for signature on 2026-10-15. | 2026-09-27 | closed | price adjustment | cost | 0 | contract/ALP-EPC-001 contract_clause/ALP-EPC-001_A3 contract_clause/ALP-EPC-001_A4
TQ-025 | 4 |  | Istanbul EPC | 2026-09-27 | process | Reference fuel LHV inconsistent with the reference composition | ER-03.02 and DP-CASE-0018 give LHV 48.4 MJ/kg for the reference composition. ISO 6976 gives 47.48 MJ/kg (34.78 MJ/Sm3, relative density 0.598) for that composition; ALP-OWN-FUL-001 section 3 itself gives 34.4 MJ/Sm3 and relative density 0.600, which also mean about 47 MJ/kg. Guarantees are on heat input, so the error does not change them, but fuel flow, the gas booking check and the metering design use the mass LHV. | Correct ER-03.02 and DP-CASE-0018 to 47.48 MJ/kg (ISO 6976, 25 degC combustion reference). | requirement:ER-03.02 design_parameter:DP-CASE-0018 source:SRC-OWNR-0003 | Agreed. The 48.4 MJ/kg was a rounded network operator figure on another reference basis. ER-03.02 and DP-CASE-0018 are corrected to 47.48 MJ/kg (ISO 6976, 25 degC combustion reference); guarantees remain on heat input at the reference composition. | 2026-09-28 | closed | requirement changed | technical_only |  | requirement/ER-03.02 design_parameter/DP-CASE-0018
TQ-026 | 4 |  | Istanbul EPC | 2026-09-27 | i_and_c | Power island control system: integration solution for SC-013 | IEC's turbine control system keeps its own controllers (turbine protection) with the HMI integration package: graphics and alarms native on the plant DCS operator stations, one KKS tag database, common time sync, own IEC 62443 zone (TQ-IEC-004). Does the Owner accept this as 'integrated in the DCS' under SC-013? | Accept as compliant with SC-013. | scope_item:SC-013 requirement:ER-12.01 | Accepted as compliant with SC-013 and ER-12.01 on condition that (1) all power island operation, alarms and trends are available on the DCS operator stations with the DCS look and feel (no separate operator HMI needed in normal operation), (2) alarm management follows the plant alarm philosophy (EEMUA 191 / IEC 62682), (3) all TCS signals are archived in the plant historian. SC-013 is reworded accordingly. | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | scope_item/SC-013
TQ-027 | 4 |  | Istanbul EPC | 2026-09-27 | electrical | Export above the 640 MW connection capacity in winter | Below about 5 degC the plant can export more than 640 MW (about 670 MW net at -4.8 degC). The TCS provides an export limiter at the HV metering point. Please confirm the export limit to be set (640 MW net at the 380 kV meters?) and whether the Owner intends to increase the connection capacity. | Limiter set to 640 MW net. | design_parameter:DP-OWNR-0051 requirement:ER-18.02 | The export limiter shall be set to 640 MW net at the 380 kV revenue meters. The Owner has applied to the TSO for a connection capacity of 680 MW; if granted, the Owner will instruct the new set point as a variation. | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | tie_in/TP-E1
TQ-028 | 4 |  | Istanbul EPC | 2026-09-27 | mechanical | Hot gas path interval: EOH basis and calendar interval | ER-05.07 requires a hot gas path interval of at least 25,000 EOH. With the OEM start factors (hot 10, warm 15, cold 20 EOH) and the ER-01.03 regime this is about 2.3 calendar years. Please confirm that ER-05.07 is EOH-based as written. | Confirm the EOH basis; OEM start factors per TQ-IEC-010. | requirement:ER-05.07 requirement:ER-01.03 | Confirmed: ER-05.07 is EOH-based with the OEM start factors (hot 10, warm 15, cold 20 EOH, trips per TQ-IEC-010). The Owner accepts about 2.3 calendar years at the ER-01.03 regime; ER-05.07 is clarified. | 2026-09-28 | closed | confirmed as is | none |  | requirement/ER-05.07
TQ-029 | 4 |  | Istanbul EPC | 2026-09-27 | general | Scope item SC-011 still states a 60 m stack | TQ-007 agreed a 65 m stack and ER-06.06 was revised, but the scope split item SC-011 (Appendix D) still reads "Stack 60 m with CEMS platform and silencer". Please confirm the editorial correction before signature. | SC-011: Stack 65 m with CEMS platform and silencer (per TQ-007 / ER-06.06). | scope_item:SC-011 requirement:ER-06.06 | Confirmed: SC-011 corrected to a 65 m stack (TQ-007, ER-06.06). | 2026-09-28 | closed | requirement changed | none |  | scope_item/SC-011
TQ-030 | 5 |  | Istanbul EPC | 2026-09-28 | general | Tie-in register: confirmation of the terminal point conditions | The Consortium's tie-in register (draft) states for each terminal point the exact scope break, connection, isolation, protection, operating envelope, capacity and the dates needed from the Contractor's commissioning sequence. Please confirm, and provide the missing data: (a) TP-W1 maximum supply pressure; (b) TP-E2 prospective short-circuit current of the 34.5 kV supply; (c) SC-001 (site boundary) has no terminal point - propose TP-A2 plot handover incl. the 11 kV cable relocation by 2027-06-30; (d) SC-035 and SC-038 need Owner/TSO/authority input - propose TP-T3 (TSO SCADA and metering link) and TP-T2 (emission data link to the Ministry); (e) TP-A1 is available on 2027-03-01, the day it is needed (no float): earlier access requested. | Confirm the draft; TP-W1 6 barg max; add TP-A2, TP-T2, TP-T3; TP-A1 from 2027-02-01. | tie_in:TP-W1 tie_in:TP-E2 tie_in:TP-A1 scope_item:SC-001 scope_item:SC-035 scope_item:SC-038 source:SRC-OWNR-0005 | Register confirmed with: (a) TP-W1 2.5-6.0 barg; (b) TP-E2 12.5 kA; (c) TP-A2 added (plot, 11 kV cable relocated by 2027-06-30, east strip E 370-400 until then not available); (d) TP-T2 and TP-T3 added; (e) TP-A1 lease from 2027-02-01. The conditions of all terminal points TP-A1..TP-W1 are agreed. | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | tie_in/TP-A1 tie_in/TP-A2 tie_in/TP-CW1 tie_in/TP-CW2 tie_in/TP-D1 tie_in/TP-E1 tie_in/TP-E2 tie_in/TP-G1 tie_in/TP-L1 tie_in/TP-M1 tie_in/TP-R1 tie_in/TP-S1 tie_in/TP-T1 tie_in/TP-T2 tie_in/TP-T3 tie_in/TP-W1
TQ-031 | 5 |  | Istanbul EPC | 2026-09-28 | electrical | Short-circuit level at TP-E1: plant contribution | ALP-OWN-ELE-001 gives 40 kA (2029) and 50 kA (2035 planning) at the plant 380 kV busbar; the GIS is specified for 50 kA (ER-11.01). The Alpilla generators add about 3.7 kA (GT 2.4 kA, ST 1.3 kA). Please confirm whether the TSO values include the Alpilla contribution; if not, 50 kA would be exceeded in 2035. | TSO to confirm that 50 kA includes the Alpilla units. | tie_in:TP-E1 requirement:ER-11.01 source:SRC-OWNR-0006 | The TSO confirms (letter of 2026-09-25) that 40 kA (2029) and 50 kA (2035) include the contribution of the Alpilla units. The GIS rating of 50 kA stands. | 2026-09-28 | closed | confirmed as is | none |  | tie_in/TP-E1
TQ-032 | 5 |  | Istanbul EPC | 2026-09-28 | electrical | Reactive capability: generator terminals (ER-04.08) or connection point (ELE-001) | ER-04.08 requires 0.85 lagging / 0.95 leading at rated active power at the generator terminals; ALP-OWN-ELE-001 section 3 states the same at the connection point. At the connection point, at the winter GT output of 470 MW, the GT generator and GSU would need about 600 MVA instead of 560 MVA (GSU reactive losses). Please confirm that ER-04.08 governs. | ER-04.08 governs (generator terminals); the connection agreement requirement is met with the plant's reactive capability less the GSU losses. | requirement:ER-04.08 tie_in:TP-E1 tie_in:IF-34 source:SRC-OWNR-0006 | ER-04.08 governs: 0.85 lagging / 0.95 leading at rated active power at the generator terminals. The TSO accepts the Grid Code compliance demonstration on that basis; ALP-OWN-ELE-001 will be corrected in its next revision. | 2026-09-28 | closed | confirmed as is | none
TQ-033 | 5 |  | Istanbul EPC | 2026-09-28 | general | Appendix A.19 (codes and standards) and the permits register | ER-01.07 sets the order of precedence and refers to 'the codes and standards listed in Appendix A.19', but the Contract has no Appendix A.19. The Consortium proposes the attached register (Turkish laws and regulations, Grid Code, codes and standards, each with edition, responsible party and the ER it serves) as Appendix A.19, and the permits register with applicant, supporting deliverables, lead times and need dates. Please confirm: (a) the register as Appendix A.19, editions at the Base Date; (b) the EIA limits (ER-14.02) govern over the Large Combustion Plants Regulation where stricter; (c) the permit split: the Owner applies for and holds the development, permanent-works and operating permits (SC-003), the Contractor for its construction permits; (d) permits PMT-005, PMT-007, PMT-014 have less than 14 days float between approval and need - earlier applications requested; (e) dates of PMT-001 and PMT-002. | (a)-(c) as proposed; (d) Owner applications 30 days earlier; PMT-007: Contractor's barge landing design by 2027-03-31. | requirement:ER-01.07 requirement:ER-14.02 scope_item:SC-003 permit:PMT-005 permit:PMT-007 permit:PMT-014 | (a) Agreed: the register (with ISO 14001 added by the Owner) is Appendix A.19; editions at the Base Date. (b) Confirmed: the stricter EIA limits of ER-14.02 govern. (c) Confirmed. (d) The Owner applies for PMT-005 on 2026-11-16, PMT-007 on 2027-04-01 (Contractor's design by 2027-03-31) and PMT-014 on 2028-03-15; the Contractor advances its own applications likewise. (e) PMT-001 granted 2026-03-12, PMT-002 granted 2026-05-28. | 2026-09-28 | closed | contractor proposal accepted | none |  | permit/PMT-001 permit/PMT-002 permit/PMT-005 permit/PMT-007 permit/PMT-014
TQ-034 | 6 |  | Istanbul EPC | 2026-09-28 | process | Aqueous ammonia storage basis (ER-06.04) | ER-06.04 requires aqueous ammonia storage for 2 x 7 days at base load. SCR consumption is 125 kg/h on gas and 480 kg/h on LDO (TQ-IEC-018). 7 days on gas is 21 t per tank; 72 h on LDO (the LDO storage autonomy, ER-03.08) needs 34.6 t. Please confirm the basis: 2 x 7 days on gas, and the total also covering 72 h of LDO operation. | 2 tanks of 30 m3 (27 t of 24.5 % solution each): 7 days on gas per tank, 72 h on LDO from one full and one half-full tank; unloading from 25 t road tankers. | requirement:ER-06.04 requirement:ER-03.08 tie_in:IF-25 | Accepted: 2 x 30 m3 as proposed; ER-06.04 clarified. The ammonia inventory (about 54 t) is added to the major accident notification (PMT-015). | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | requirement/ER-06.04
TQ-035 | 7 |  | Istanbul EPC | 2026-09-28 | general | Engineering start-up: KKS key list, document numbering, MDL, review classes and AWP definitions | (1) ER-17.01 requires the Owner's document numbering, which has not been provided. The consortium proposes ALP-<ORG>-<KKS system or 00000>-<DISC>-<TYPE>-<NNNN> (procedure ALP-EPC-00000-GE-PRC-0002), with the IEC 61355 document class on every document type. Does the Owner accept it as the project numbering? (2) Please approve the project KKS key list (125 function, equipment-unit and component keys, 0 = common / 1 = GT+HRSG / 2 = ST unit numbering) for use in engineering. (3) Please accept the MDL (623 documents incl. the IEC VDRL) as the document baseline, the review classes per document type (approval / review / information / internal) and the Basic Design Package flag (21-day review). (4) Please accept the AWP definitions: 12 CWAs in path-of-construction order, one CWP per CWA and discipline, one EWP per CWP needed 20 working days before the CWP starts, MRs as PWPs (ROS at the first CWP start); IWPs are prepared by the construction contractors from the CWPs. | Adopt the consortium numbering as the Owner's numbering under ER-17.01; approve the key list with verification by the Owner's Engineer; accept the MDL, review classes and AWP definitions. | requirement:ER-01.06 requirement:ER-17.01 requirement:ER-17.02 | (1) Accepted: the consortium numbering is the project numbering under ER-17.01; the Owner's EDMS will use it unchanged. (2) The KKS key list is approved for engineering. The Owner's Engineer verifies each key title against the VGB-S-811 key catalogue with the KKS manual review; until then keys stay flagged 'not verified'. (3) MDL accepted as baseline for the Basic Design Package. Review classes accepted with one change: logic diagrams (LOG) incl. cause and effect are safety relevant and are for approval. The MDL is updated monthly with the progress report. (4) AWP definitions accepted. The Owner requires every CWP to be released for construction only when its EWP is complete (all IFC) and its PWP materials are on site or have a confirmed delivery before the planned installation. | 2026-09-28 | closed | requirement changed | technical_only |  | doc_type/LOG
TQ-036 | 8 |  | Istanbul EPC | 2026-09-28 | general | MDL Rev B baseline: document quantities, new document types, structures and packages | The consortium re-issues the MDL as Rev B: 2205 documents (1455 EPC, 120 IEC, 630 other suppliers), 21,362 sheets. Rev A (623 documents) missed the per-tag deliverables, the supplier documents of the BOP packages, factory and site tests, system-based commissioning and O&M documents and several permit dossiers. Document quantities now follow rules per system / structure / area / package with estimated quantities until the registers exist. Please accept (1) the MDL Rev B as the document baseline, (2) the new document types TST, TRP, WIR, HUP, SUP, RBR, EFD, MOS, MDB, CEM, HMI with their review classes, (3) the structure keys UZD (pipe racks), UZE (cable trenches), UZF (temporary barge landing), (4) the 14 added procurement packages, (5) the review of supplier documents: EPC reviews all; transmitted to the Owner for approval: supplier P&IDs, ITPs and FAT procedures; for review: GA, datasheets, calculations, schematics, manuals; for information: manufacturing record books. |  | requirement:ER-17.01 requirement:ER-01.06 requirement:ER-16.01 | (1)-(5) accepted with one change and one condition. Change: fire fighting, escape route and safety signage drawings are submitted to the fire brigade (occupancy permit PMT-020) and are for Owner approval. Condition: the Owner's Engineer review load must be planned; the consortium issues a monthly document issue forecast (from the engineering plan) and transmits in batches of at most 150 documents per week. The new structure keys are approved for engineering (verification with the KKS key list). | 2026-09-28 | closed | requirement changed | technical_only |  | mdl_rule/DL-HS-ESC
TQ-037 | 8 |  | Istanbul EPC | 2026-09-28 | general | AWP release rule: progressive EWP release to the IWPs of a CWP | TQ-035 requires a CWP to be released only when its EWP is complete (all documents IFC). With the Rev B MDL a piping CWP carries up to 2,800 isometric sheets and a civil CWP the reinforcement of every pour; requiring all of them IFC before the first IWP would delay construction by 3-9 months or require engineering staff far above a realistic peak. The consortium proposes: (a) a CWP is released when the documents of its first IWPs are IFC (layouts, GA, foundations, plans: 100 % at release) and its materials for those IWPs are on site or confirmed; (b) progressive documents (isometrics, supports, schematics, loop diagrams, reinforcement, equipment foundations) are released per IWP, planned at CWP start - lead + share x CWP duration per document type; (c) no IWP is issued to the field unless all its documents are IFC and its constraints removed; (d) the EWP completeness per CWP is reported monthly. |  | requirement:ER-17.02 | Accepted as proposed, with the condition that the monthly report shows per CWP the IFC status of the documents needed for the next 8 weeks of IWPs, and that a CWP whose first-IWP documents are not IFC is not started. TQ-035 item (4) is amended accordingly. | 2026-09-28 | closed | contractor proposal accepted | none
TQ-038 | 9 |  | Istanbul EPC | 2026-09-28 | general | Payment milestone MS-02 (Basic Design Package approved, month 3) cannot be met | Release gate G-OWN-BDP: The Basic Design Package (25 documents, of them 10 P&IDs) must be approved for MS-02 at month 3 (2027-02-02). With the Owner review period for the BDP (21 days, ER-17.01) and the input chain design basis -> system design specification -> P&ID, the earliest possible approval is 2027-03-08 even with unlimited staff; with the planned process team (12 FTE, 9,000 h of P&IDs needed before May 2027 for the long-lead requisitions and the first EWPs) the BDP is approved on 2027-07-21. Please confirm one of: (a) MS-02 split into MS-02a 'BDP batch 1 approved' (design bases, PFDs, HMB, plot plan, SLD, power island P&IDs; month 5) and MS-02b 'BDP batch 2 approved' (BOP P&IDs; month 9), same total percentage; (b) MS-02 at month 9; (c) approval on the tender-stage P&IDs at IFR with the IFC review later. The consortium recommends (a). |  | contract_clause:ALP-EPC-001_15.3 requirement:ER-17.01 |  |  | open

## Summary
By round | Raised | Closed | Open | Price effect (EUR)
Round 1 | 16 | 16 | 0 | 530000
Round 2 | 6 | 6 | 0 | 950000
Round 3 | 2 | 2 | 0 | 0
Round 4 | 5 | 5 | 0 | 0
Round 5 | 4 | 4 | 0 | 0
Round 6 | 1 | 1 | 0 | 0
Round 7 | 1 | 1 | 0 | 0
Round 8 | 2 | 2 | 0 | 0
Round 9 | 1 | 0 | 1 | 0
Total | 38 | 37 | 1 | 1480000
By outcome | Count
confirmed as is | 6
contractor proposal accepted | 14
none | 1
owner to provide | 5
price adjustment | 5
rejected | 1
requirement changed | 6