# Alpilla 600 MW Combined Cycle Power Plant
Codes, Standards and Regulations (Appendix A.19), Permits and Authorities

100 register entries (100 agreed), 24 permits (24 agreed), 15 authorities. Agreed in TQ-033, TQ-IEC-022. Checks: 0 warning(s), 2 note(s).

# 1. Order of precedence (ER-01.07)

Turkish laws and regulations

Grid Code

Contract

Codes and standards (Appendix A.19) - where codes conflict the more stringent requirement applies

Good industry practice / project libraries

Edition: 'edition at Base Date' = the edition in force 28 days before the tender submission date; later editions apply only by variation. Responsible = parties whose design or work must comply (IEPC = Istanbul EPC, IEC = Imaginary Electric).

# 2. Laws, regulations and Grid Code

| Code | Title | Edition | Authority | Applies to / obligations | Responsible | Status |
| --- | --- | --- | --- | --- | --- | --- |
| Law 167 | Groundwater Law (Yeralti Sulari Hakkinda Kanun) | 1960, as amended | DSI | construction dewatering and groundwater wells | Istanbul EPC | agreed |
| Law 2863 | Law on the Protection of Cultural and Natural Assets | 1983, as amended | Museum Dir. | archaeological chance-find procedure during excavation | Istanbul EPC | agreed |
| Law 2872 | Environmental Law (Cevre Kanunu) | 1983, as amended | Ministry Env. | all environmental obligations; EIA conditions | Istanbul EPC, Imaginary Electric | agreed |
| Law 2918 | Highway Traffic Law (Karayollari Trafik Kanunu) | 1983, as amended | KGM | abnormal load transport permits | Istanbul EPC | agreed |
| Law 3194 | Zoning Law (Imar Kanunu) | 1985, as amended | Municipality | building permit and occupancy permit | Istanbul EPC, Imaginary Electric | agreed |
| Law 3621 | Coastal Law (Kiyi Kanunu) | 1990, as amended | Ministry Env. | intake and outfall pipelines and the temporary barge landing on the coastal strip | Istanbul EPC | agreed |
| Law 4646 | Natural Gas Market Law (Dogal Gaz Piyasasi Kanunu) | 2001, as amended | Gas network operator | gas connection, metering and station approval by the network operator | Istanbul EPC | agreed |
| Law 6331 | Occupational Health and Safety Law (Is Sagligi ve Guvenligi Kanunu) | 2012 | MoLSS | design and construction safety, risk assessment | Istanbul EPC, Imaginary Electric | agreed |
| Law 6446 | Electricity Market Law (Elektrik Piyasasi Kanunu) | 2013 | EMRA | generation licence, connection and system use | Owner | agreed |
| Law 7381 | Nuclear Regulatory Law (Nukleer Duzenleme Kanunu) | 2022 | NDK | licensing of radiation sources for radiographic testing | Istanbul EPC, Imaginary Electric | agreed |
| Construction OHS Regulation | Regulation on OHS in Construction Works (Yapi Islerinde ISG Yonetmeligi) | 2013 | MoLSS | site safety plan, coordination between contractors | Istanbul EPC, Imaginary Electric | agreed |
| EIA Regulation | Environmental Impact Assessment Regulation (CED Yonetmeligi) | 2022 | Ministry Env. | conditions of the positive EIA decision (ALP-OWN-ENV-001); changes to the project need an EIA review | Istanbul EPC, Imaginary Electric | agreed |
| Earthing Regulation | Regulation on Earthing in Electrical Installations (Elektrik Tesislerinde Topraklamalar Yonetmeligi) | 2001 | MENR | earthing system design and verification | Istanbul EPC, Imaginary Electric | agreed |
| Env. Permit Regulation | Environmental Permit and Licence Regulation (Cevre Izin ve Lisans Yonetmeligi) | 2014 | Ministry Env. | temporary activity certificate and environmental permit (air emissions, discharges) | Istanbul EPC, Imaginary Electric | agreed |
| Explosive Atmospheres Regulation | Regulation on Protection of Workers from Explosive Atmospheres | 2013 | MoLSS | explosion protection document for the gas station, GT package, LDO, H2 | Istanbul EPC, Imaginary Electric | agreed |
| Fire Regulation | Regulation on Fire Protection of Buildings (Binalarin Yangindan Korunmasi Hakkinda Yonetmelik) | 2007, as amended | Municipality | fire protection design approval of buildings | Istanbul EPC, Imaginary Electric | agreed |
| Heavy Current Regulation | Regulation on Electrical Heavy Current Installations (Elektrik Kuvvetli Akim Tesisleri Yonetmeligi) | 2000 | MENR | HV/MV installations, clearances | Istanbul EPC, Imaginary Electric | agreed |
| LCP Regulation | Large Combustion Plants Regulation (Buyuk Yakma Tesisleri Yonetmeligi) | 2010 | Ministry Env. | emission limit values of gas turbines > 50 MWth; the stricter EIA limits (ER-14.02) govern | Istanbul EPC, Imaginary Electric | agreed |
| Major Accident Regulation | Regulation on Prevention and Mitigation of Major Industrial Accidents (Seveso III) | 2019 | Ministry Env. | LDO storage about 5,850 t (2 x 3,500 m3) exceeds the 2,500 t lower-tier threshold for petroleum products: notification and Major Accident Prevention Policy; aqueous ammonia and hydrogen inventories added by the aggregation rule | Istanbul EPC, Imaginary Electric | agreed |
| Noise Regulation | Environmental Noise Control Regulation (Cevresel Gurultunun Kontrolu Yonetmeligi) | edition at Base Date | Ministry Env. | noise at the receptors (45/55 dB(A)), construction noise assessment | Istanbul EPC, Imaginary Electric | agreed |
| SKHKKY | Industrial Air Pollution Control Regulation (Sanayi Kaynakli Hava Kirliliginin Kontrolu Yonetmeligi) | 2009 | Ministry Env. | stack height and dispersion, emission measurement | Istanbul EPC, Imaginary Electric | agreed |
| Soil Regulation | Soil Pollution Control and Point-Source Contaminated Sites Regulation | 2010 | Ministry Env. | baseline and closure soil condition, spill prevention | Istanbul EPC | agreed |
| TBDY 2018 | Turkish Building Earthquake Code (Turkiye Bina Deprem Yonetmeligi) | 2018 | Municipality | seismic design of buildings and structures; equipment anchorage | Istanbul EPC, Imaginary Electric | agreed |
| WPCR | Water Pollution Control Regulation (Su Kirliligi Kontrolu Yonetmeligi) | 2004 | Ministry Env. | sea discharge limits of process, sanitary and cooling water effluents | Istanbul EPC | agreed |
| Waste Regulation | Waste Management Regulation (Atik Yonetimi Yonetmeligi) | 2015 | Ministry Env. | construction and operation waste, hazardous waste | Istanbul EPC | agreed |
| Work Equipment Regulation | Regulation on Health and Safety in the Use of Work Equipment | 2013 | MoLSS | first and periodic inspection of lifting and pressure equipment before use | Istanbul EPC, Imaginary Electric | agreed |
| ATEX 2014/34/EU | ATEX Equipment Directive, transposed as the regulation on equipment for potentially explosive atmospheres | 2014/34/EU | MoIT | equipment in hazardous areas | Istanbul EPC, Imaginary Electric | agreed |
| Machinery Directive 2006/42/EC | Machinery Directive, transposed as the Machinery Safety Regulation (Makine Emniyeti Yonetmeligi) | 2006/42/EC | MoIT | CE marking and declarations of conformity of machinery packages (GT, ST, pumps, cranes) | Istanbul EPC, Imaginary Electric | agreed |
| PED 2014/68/EU | Pressure Equipment Directive, transposed as the Pressure Equipment Regulation (Basincli Ekipmanlar Yonetmeligi) | 2014/68/EU | MoIT | conformity assessment of pressure equipment by a notified body (HRSG, vessels, piping) | Istanbul EPC, Imaginary Electric | agreed |
| Grid Code | Electricity Grid Regulation (Elektrik Sebeke Yonetmeligi) - TSO Grid Code | edition at Base Date | TSO | generator performance, protection, frequency and voltage control, compliance tests | Istanbul EPC, Imaginary Electric | agreed |

# 3. Codes and standards

| Code | Title | Edition | Applies to | ER | Responsible | Deviation / clarification | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TS 500 | Requirements for design and construction of reinforced concrete structures | edition at Base Date | reinforced concrete (with EN 1992) | ER-13.04 | Istanbul EPC | - | agreed |
| TS EN 590 | Automotive fuels - Diesel - Requirements and test methods (basis of the LDO specification) | edition at Base Date | LDO delivered by the Owner's supplier (TP-L1) | ER-03.07 | Owner | - | agreed |
| ACI 351.3R | Report on Foundations for Dynamic Equipment | edition at Base Date | turbine-generator foundations (IEC load data, IF-43) | ER-13.01 | Istanbul EPC | - | agreed |
| API 650 | Welded Tanks for Oil Storage | edition at Base Date | LDO and water storage tanks | ER-03.08 | Istanbul EPC | - | agreed |
| ASME B16.25 | Buttwelding Ends | edition at Base Date | weld-end terminal points | - | Istanbul EPC, Imaginary Electric | - | agreed |
| ASME B16.34 | Valves - Flanged, Threaded, and Welding End | edition at Base Date | valves | - | Istanbul EPC, Imaginary Electric | - | agreed |
| ASME B16.5 | Pipe Flanges and Flanged Fittings NPS 1/2 through NPS 24 | edition at Base Date | flanged terminal points | - | Istanbul EPC, Imaginary Electric | - | agreed |
| ASME B31.1 | Power Piping | edition at Base Date | steam, feedwater, condensate and utility piping | - | Istanbul EPC | - | agreed |
| ASME B31.3 | Process Piping | edition at Base Date | chemical, ammonia and LDO piping | - | Istanbul EPC | - | agreed |
| ASME B31.8 | Gas Transmission and Distribution Piping Systems | edition at Base Date | gas receiving station and plant gas piping | ER-18.03 | Istanbul EPC | - | agreed |
| ASME B36.10M | Welded and Seamless Wrought Steel Pipe | - | pipe dimensions and wall thicknesses (pipe_size records) | - | Istanbul EPC, Imaginary Electric | - | agreed |
| ASME PTC 12.2 | Performance Test Code on Steam Surface Condensers | edition at Base Date | condenser performance test | ER-07.08 | Imaginary Electric | - | agreed |
| ASME PTC 22 | Performance Test Code on Gas Turbines | edition at Base Date | GT performance tests | - | Imaginary Electric | - | agreed |
| ASME PTC 4.4 | Performance Test Code on Gas Turbine Heat Recovery Steam Generators | edition at Base Date | HRSG performance tests | - | Imaginary Electric | - | agreed |
| ASME PTC 46 | Performance Test Code on Overall Plant Performance | edition at Base Date | plant performance tests and correction curves | ER-16.04, ER-12.05 | Istanbul EPC, Imaginary Electric | - | agreed |
| ASME PTC 6 | Performance Test Code on Steam Turbines | edition at Base Date | ST performance tests (flow section in the main steam line) | - | Istanbul EPC, Imaginary Electric | - | agreed |
| ASME Section I | ASME BPVC Section I - Rules for Construction of Power Boilers | edition at Base Date | HRSG pressure parts, boiler external piping | ER-06.02 | Istanbul EPC, Imaginary Electric | Selected for the HRSG (IEC); PED module G by a notified body; boiler external piping by the EPC to ASME Section I / B31.1. | agreed |
| ASME Section IX | ASME BPVC Section IX - Welding, Brazing and Fusing Qualifications | edition at Base Date | welding procedure and welder qualification (alternative EN ISO 15614) | ER-15.05 | Istanbul EPC, Imaginary Electric | - | agreed |
| ASME Section VIII Div. 1 | ASME BPVC Section VIII Division 1 - Pressure Vessels | edition at Base Date | BOP pressure vessels (flash tanks, air receivers, deaeration) | - | Istanbul EPC | - | agreed |
| EN 10204 | Metallic products - Types of inspection documents | 2004 | material certificates 3.1 / 3.2 | ER-15.04 | Istanbul EPC, Imaginary Electric | - | agreed |
| EN 12186 | Gas infrastructure - Gas pressure regulating stations for transmission and distribution | edition at Base Date | gas pressure regulation and safety devices (slam-shut, relief) | ER-03.04 | Istanbul EPC | - | agreed |
| EN 12952 | Water-tube boilers and auxiliary installations (all parts) | edition at Base Date | HRSG - alternative to ASME Section I (ER-06.02); EN 12952-3 fatigue assessment for cyclic operation (ER-06.05) | ER-06.02, ER-06.05 | Imaginary Electric | HRSG designed to ASME Section I with PED conformity by a notified body (module G); EN 12952-3 applied only for the low-cycle fatigue assessment of the thick-walled parts (HP drum, SH/RH outlet headers) per ER-06.05. | agreed |
| EN 13001 | Cranes - General design (all parts) | edition at Base Date | turbine hall EOT crane and hoists | ER-10.07 | Istanbul EPC | - | agreed |
| EN 14181 | Stationary source emissions - Quality assurance of automated measuring systems | edition at Base Date | CEMS QAL1/QAL2/QAL3/AST | ER-12.04 | Istanbul EPC | - | agreed |
| EN 15259 | Air quality - Measurement of stationary source emissions - Measurement sections and sites | edition at Base Date | stack measurement ports and platforms | ER-06.06 | Istanbul EPC | - | agreed |
| EN 15267-3 | Air quality - Certification of automated measuring systems - Part 3 | edition at Base Date | certified CEMS analysers | ER-12.04 | Istanbul EPC | - | agreed |
| EN 1822 | High efficiency air filters (EPA, HEPA and ULPA) | edition at Base Date | GT inlet air final filter class | ER-05.02 | Imaginary Electric | - | agreed |
| EN 1990 | Eurocode - Basis of structural design (with EN 1991 actions) | edition at Base Date | structural design basis and actions (wind, snow, thermal) | - | Istanbul EPC | - | agreed |
| EN 1992 | Eurocode 2 - Design of concrete structures | edition at Base Date | concrete structures and foundations | ER-13.04 | Istanbul EPC | - | agreed |
| EN 1993 | Eurocode 3 - Design of steel structures | edition at Base Date | steel structures | ER-13.03 | Istanbul EPC | - | agreed |
| EN ISO 1461 | Hot dip galvanized coatings on fabricated iron and steel articles | edition at Base Date | galvanizing of structural steel | ER-13.03 | Istanbul EPC | - | agreed |
| EN ISO 15614 | Specification and qualification of welding procedures for metallic materials - Welding procedure test | edition at Base Date | welding procedure qualification (alternative ASME IX) | ER-15.05 | Istanbul EPC, Imaginary Electric | - | agreed |
| HEI 2629 | HEI Standards for Steam Surface Condensers | 12th edition | condenser thermal and mechanical design | ER-07.07, ER-07.08, ER-07.09, ER-07.10 | Imaginary Electric | - | agreed |
| IAPWS TGD | IAPWS Technical Guidance Documents on cycle chemistry (HRSG, AVT, instrumentation) | edition at Base Date | water/steam chemistry of the HRSG plant | ER-09.03 | Istanbul EPC, Imaginary Electric | - | agreed |
| IAPWS-IF97 | Industrial Formulation 1997 for the Thermodynamic Properties of Water and Steam | 1997 | water/steam properties in heat balances and tests | - | Istanbul EPC, Imaginary Electric | - | agreed |
| IEC 60034-1 | Rotating electrical machines - Part 1: Rating and performance | edition at Base Date | generators; also -3 for turbine-type generators | ER-11.02, ER-04.08 | Imaginary Electric | - | agreed |
| IEC 60045-1 | Steam turbines - Part 1: Specifications | edition at Base Date | steam turbine; rated and design conditions | - | Imaginary Electric | - | agreed |
| IEC 60076 | Power transformers (all parts) | edition at Base Date | GSU, UAT and auxiliary transformers | ER-11.03 | Istanbul EPC, Imaginary Electric | - | agreed |
| IEC 60079-10-1 | Explosive atmospheres - Classification of areas - Explosive gas atmospheres | edition at Base Date | hazardous area classification | ER-14.06 | Istanbul EPC, Imaginary Electric | - | agreed |
| IEC 60364 | Low-voltage electrical installations (all parts) | edition at Base Date | LV installations | - | Istanbul EPC | - | agreed |
| IEC 60815 | Selection and dimensioning of high-voltage insulators for polluted conditions | edition at Base Date | creepage distances of outdoor insulation (salt air) | ER-02.10 | Istanbul EPC, Imaginary Electric | - | agreed |
| IEC 60909 | Short-circuit currents in three-phase AC systems | edition at Base Date | short-circuit studies (TP-E1, IF-34..IF-38) | - | Istanbul EPC, Imaginary Electric | - | agreed |
| IEC 61511 | Functional safety - Safety instrumented systems for the process industry sector | edition at Base Date | SIS incl. burner management and HRSG protection | ER-12.03 | Istanbul EPC, Imaginary Electric | - | agreed |
| IEC 61850 | Communication networks and systems for power utility automation | edition at Base Date | substation automation and protection interface (IF-41) | - | Istanbul EPC, Imaginary Electric | - | agreed |
| IEC 61936-1 | Power installations exceeding 1 kV AC - Part 1: Common rules | edition at Base Date | HV/MV installations, transformer fire separation | - | Istanbul EPC | - | agreed |
| IEC 62271-203 | High-voltage switchgear - Gas-insulated metal-enclosed switchgear for rated voltages above 52 kV | edition at Base Date | 380 kV GIS | ER-11.01 | Istanbul EPC | - | agreed |
| IEC 62305 | Protection against lightning (all parts) | edition at Base Date | lightning protection and risk assessment | ER-02.12, ER-11.07 | Istanbul EPC | - | agreed |
| IEC 62443 | Security for industrial automation and control systems (all parts) | edition at Base Date | OT cybersecurity SL2 (DCS, TCS, zone/conduit at IF-40) | ER-05.06, ER-12.07 | Istanbul EPC, Imaginary Electric | IEC TCS certified to IEC 62443-4-1 / -4-2 components, system SL2 per IEC 62443-3-3; zone/conduit boundary and firewall at IF-40 by the EPC. | agreed |
| IEC 62770 | Fluids for electrotechnical applications - Unused natural esters for transformers | edition at Base Date | GSU insulating liquid (natural ester) | - | Imaginary Electric | - | agreed |
| IEC/IEEE 62271-37-013 | High-voltage switchgear - Alternating-current generator circuit-breakers | edition at Base Date | generator circuit breakers | ER-11.02 | Imaginary Electric | - | agreed |
| IEEE 80 | Guide for Safety in AC Substation Grounding | edition at Base Date | earthing grid | ER-11.07 | Istanbul EPC | - | agreed |
| IEEE C37.102 | Guide for AC generator protection | edition at Base Date | generator protection functions | - | Imaginary Electric | - | agreed |
| ISO 10494 | Gas turbines and gas turbine sets - Measurement of emitted airborne noise | edition at Base Date | GT noise data and tests | ER-14.03 | Imaginary Electric | - | agreed |
| ISO 12944-2 | Paints and varnishes - Corrosion protection of steel structures by protective paint systems - Part 2: Classification of environments | edition at Base Date | corrosivity category of outdoor equipment (coastal) | ER-02.08 | Istanbul EPC, Imaginary Electric | - | agreed |
| ISO 14001 | Environmental management systems - Requirements | 2015 | environmental management during construction and commissioning (ESMP) | - | Istanbul EPC, Imaginary Electric | - | agreed |
| ISO 20816-2 | Mechanical vibration - Measurement and evaluation of machine vibration - Part 2: Land-based gas turbines, steam turbines and generators above 40 MW with fluid-film bearings | edition at Base Date | vibration limits of the GT, ST and generators (IEC) | - | Imaginary Electric | - | agreed |
| ISO 21789 | Gas turbine applications - Safety | edition at Base Date | GT package | - | Imaginary Electric | - | agreed |
| ISO 3977-3 | Gas turbines - Procurement - Part 3: Design requirements | edition at Base Date | GT package | - | Imaginary Electric | - | agreed |
| ISO 45001 | Occupational health and safety management systems | 2018 | HSE management system | ER-14.05 | Istanbul EPC, Imaginary Electric | - | agreed |
| ISO 6976 | Natural gas - Calculation of calorific values, density, relative density and Wobbe indices | 2016 | fuel LHV in heat balances and performance tests | - | Istanbul EPC, Imaginary Electric | - | agreed |
| ISO 9001 | Quality management systems - Requirements | 2015 | quality management of the Contractor and major suppliers | ER-15.01 | Istanbul EPC, Imaginary Electric | - | agreed |
| NFPA 11 | Standard for Low-, Medium-, and High-Expansion Foam | edition at Base Date | LDO tank foam protection | ER-03.08 | Istanbul EPC | - | agreed |
| NFPA 12 | Standard on Carbon Dioxide Extinguishing Systems | edition at Base Date | GT enclosure CO2 system | ER-10.05 | Imaginary Electric | CO2 total flooding for the GT enclosure (ER-10.05 allows water mist or CO2); no water mist. | agreed |
| NFPA 20 | Standard for the Installation of Stationary Pumps for Fire Protection | edition at Base Date | fire pumps | ER-10.05 | Istanbul EPC | - | agreed |
| NFPA 30 | Flammable and Combustible Liquids Code | edition at Base Date | LDO unloading, storage and bunds | ER-03.08 | Istanbul EPC | - | agreed |
| NFPA 72 | National Fire Alarm and Signaling Code | edition at Base Date | fire detection and alarm (IF-33) | ER-10.05 | Istanbul EPC | - | agreed |
| NFPA 85 | Boiler and Combustion Systems Hazards Code | edition at Base Date | HRSG purge and combustion turbine exhaust systems | - | Imaginary Electric | - | agreed |
| NFPA 850 | Recommended Practice for Fire Protection for Electric Generating Plants and HVDC Converter Stations | edition at Base Date | plant fire protection concept | ER-10.05 | Istanbul EPC, Imaginary Electric | - | agreed |
| VGB-S-010 | Feed water, boiler water and steam quality for power plants | edition at Base Date | cycle chemistry limits | ER-09.03 | Istanbul EPC, Imaginary Electric | - | agreed |
| AVEVA class library 1.0.1 | AVEVA engineering class library (classes, attributes, units, value lists) - project tag classification standard | modelUpdatedAtVersion 4.0.0.0 | engineering classes and attributes of the project database | - | Istanbul EPC | - | agreed |

# 4. Permits, licences and approvals

| ID | Permit | Authority | Legal basis | Applicant | Deliverables (who provides) | Apply by / lead | Needed by / gates | Permit status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PMT-001 | Positive EIA decision | Ministry Env. | Law 2872, EIA Regulation | Owner | - | - / - d | 2026-11-02 all works | granted |
| PMT-002 | Generation licence | EMRA | Law 6446 | Owner | - | - / - d | 2026-11-02 Contract effectiveness | granted |
| PMT-003 | Grid connection agreement | TSO | Law 6446, Grid Code | Owner | - | - / - d | 2026-11-02 grid design | granted |
| PMT-010 | Workplace registration and construction site notification | SGK | Law 6331, Construction OHS Regulation | Istanbul EPC | EPC: site safety plan, OHS professionals | 2026-11-02 / 10 d | 2026-11-16 mobilisation | in preparation |
| PMT-025 | Archaeological chance-find notifications | Museum Dir. | Law 2863 | Istanbul EPC | EPC: chance-find procedure in the construction ESMP | - / - d | 2026-11-16 excavations | planned |
| PMT-011 | Construction noise assessment report | Ministry Env. | Noise Regulation, EIA Regulation | Istanbul EPC | EPC: acoustic report, working hours plan | 2026-12-01 / 30 d | 2027-01-15 piling | planned |
| PMT-022 | Storm water discharge consent | DSI | WPCR | Owner | EPC: drainage design, oil interceptors | - / - d | 2027-01-15 site drainage | granted |
| PMT-005 | Building permit (yapi ruhsati) | Municipality | Law 3194, TBDY 2018, Fire Regulation | Owner | EPC: architectural, structural (TBDY 2018), mechanical and electrical projects signed by licensed Turkish engineers, geotechnical report, fire approval; IEC: equipment loads and foundation drawings | 2026-11-16 / 60 d | 2027-02-15 start of permanent foundations (piling) | in preparation |
| PMT-012 | Construction dewatering permit | DSI | Law 167 | Istanbul EPC | EPC: dewatering design and discharge plan | 2026-11-16 / 60 d | 2027-02-15 deep excavations | planned |
| PMT-023 | Construction power connection | DISCO | Law 6446 | Owner | EPC: load list, RMU design | 2026-12-15 / 60 d | 2027-03-15 construction power | applied |
| PMT-006 | Coastal permit for intake and outfall pipelines | Ministry Env. | Law 3621, EIA Regulation | Owner | EPC: marine design, route survey, construction method statement | 2026-11-02 / 180 d | 2027-10-01 marine works (window 1 October - 30 April) | applied |
| PMT-007 | Coastal permit for the temporary barge landing | Ministry Env. | Law 3621 | Owner | EPC: landing design and removal plan by 2027-03-31 | 2027-04-01 / 180 d | 2027-11-01 first heavy delivery by barge | planned |
| PMT-008 | Harbour master approval for barge operations | MoTI / Harbour Master | Law 3621 | Istanbul EPC | EPC: marine operations plan; IEC: heavy piece list (weights, dimensions) | 2027-09-15 / 30 d | 2027-11-01 first heavy delivery by barge | planned |
| PMT-009 | Abnormal load road transport permits | KGM | Law 2918 | Istanbul EPC | EPC: route survey; IEC: transport drawings | 2027-09-01 / 30 d | 2027-11-01 heavy haul to site | planned |
| PMT-013 | Radiation source licence for radiographic testing | NDK | Law 7381 | Istanbul EPC | NDT subcontractor licence, radiation protection plan | 2027-09-15 / 60 d | 2027-12-01 first site radiography | planned |
| PMT-004 | System use agreement and energisation approval | TSO | Law 6446, Grid Code | Owner | EPC: protection settings, SCADA test report, single-line diagram; IEC: generator and GSU data, excitation and governor models | 2028-03-15 / 90 d | 2028-07-15 KD-010 back-feed | planned |
| PMT-016 | First inspection of lifting and pressure equipment | MoLSS | Work Equipment Regulation, PED 2014/68/EU | Istanbul EPC | EPC and IEC: declarations of conformity, notified body certificates, load tests | 2028-06-15 / 14 d | 2028-08-01 use of equipment in commissioning | planned |
| PMT-014 | Gas connection and receiving station approval | Gas network operator | Law 4646 | Owner | EPC: station design (EN 12186 / ASME B31.8), metering, pressure protection, test records; IEC: GT gas demand and pressure requirements | 2028-03-15 / 120 d | 2028-08-15 gas-in (TP-G1) | planned |
| PMT-017 | Emission data link registration (continuous emission monitoring centre) | Ministry Env. | Env. Permit Regulation, SKHKKY | Owner | EPC: CEMS certificates (EN 15267), QAL1, data link test | 2028-07-15 / 45 d | 2028-10-02 first fire (KD-020) | planned |
| PMT-018 | Temporary activity certificate (environmental) | Ministry Env. | Env. Permit Regulation, LCP Regulation, WPCR | Owner | EPC: emission and discharge measurement plan, CEMS; IEC: GT emission data | 2028-08-15 / 30 d | 2028-10-02 first fire (KD-020) | planned |
| PMT-015 | Major accident notification and Major Accident Prevention Policy | Ministry Env. | Major Accident Regulation | Owner | EPC: hazardous substance inventory, QRA inputs, MAPP draft; IEC: inventories in the power island (lube oil, H2, ammonia skid) | 2028-08-15 / 60 d | 2028-11-01 LDO first fill (TP-L1) | planned |
| PMT-019 | Environmental permit (air emissions and discharges) | Ministry Env. | Env. Permit Regulation, LCP Regulation, WPCR | Owner | EPC: QAL2 report, accredited emission and discharge test reports (ER-16.05) | 2029-03-01 / 90 d | 2029-07-04 Taking-Over (KD-040) | planned |
| PMT-020 | Occupancy permit (yapi kullanma izin belgesi) | Municipality | Law 3194, Fire Regulation | Owner | EPC: as-built drawings, fire system test certificates | 2029-05-15 / 30 d | 2029-07-04 Taking-Over (KD-040) | planned |
| PMT-021 | Grid Code compliance approval (provisional and final) | TSO | Grid Code | Owner | EPC and IEC: test programme, validated models, test reports (ER-16.03) | 2029-01-02 / 60 d | 2029-07-04 commercial operation | planned |

# 5. Authorities

| ID | Authority | Regulations enforced | Permits |
| --- | --- | --- | --- |
| DISCO | Regional electricity distribution company (construction power) | - | PMT-023 |
| DSI | General Directorate of State Hydraulic Works (surface and groundwater) | Law 167 | PMT-012, PMT-022 |
| EMRA | Energy Market Regulatory Authority (EPDK) | Law 6446 | PMT-002 |
| GASNO | Natural gas transmission network operator (connection and station approval) | Law 4646 | PMT-014 |
| KGM | General Directorate of Highways (abnormal load permits) | Law 2918 | PMT-009 |
| MENR | Ministry of Energy and Natural Resources | Heavy Current Regulation, Earthing Regulation | - |
| MOCT | Ministry of Culture and Tourism (regional museum directorate) | Law 2863 | PMT-025 |
| MOEUCC | Ministry of Environment, Urbanisation and Climate Change (and its Provincial Directorate) | Law 2872, EIA Regulation, Env. Permit Regulation, SKHKKY, LCP Regulation, WPCR, Noise Regulation, Waste Regulation, Soil Regulation, Major Accident Regulation, Law 3621 | PMT-001, PMT-006, PMT-007, PMT-011, PMT-015, PMT-017, PMT-018, PMT-019 |
| MOIT | Ministry of Industry and Technology (market surveillance of products) | PED 2014/68/EU, Machinery Directive 2006/42/EC, ATEX 2014/34/EU | - |
| MOLSS | Ministry of Labour and Social Security (OHS inspection) | Law 6331, Construction OHS Regulation, Work Equipment Regulation, Explosive Atmospheres Regulation | PMT-016 |
| MOTI | Ministry of Transport and Infrastructure (Harbour Master, coastal structures) | - | PMT-008 |
| MUNI | District municipality / provincial special administration (building, occupancy, fire approval, water) | Law 3194, Fire Regulation, TBDY 2018 | PMT-005, PMT-020 |
| NDK | Nuclear Regulatory Authority (radiation sources for NDT) | Law 7381 | PMT-013 |
| SGK | Social Security Institution (workplace registration) | - | PMT-010 |
| TSO | National Transmission System Operator | Grid Code | PMT-003, PMT-004, PMT-021 |

# 6. Check results

| Item | Check | Result | Detail |
| --- | --- | --- | --- |
| PMT-010 | timing | INFO | apply 2026-11-02 + 10 d = 2026-11-12; needed 2026-11-16: float 4 d |
| PMT-025 | timing | INFO | no lead time: procedural, needed from 2026-11-16 |