## Streams
ALP-HMB-MIN-NG-100 - streams
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 801.288 | 1.012 | -8 |  | -33.1 | -26.52 | preliminary | source:SRC-IECE-0005
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | fuel_gas | FGS | FGH | 22.242 | 38 | 25 |  | 0 | 0 | preliminary | source:SRC-IECE-0005
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 22.242 | 35.5 | 215 |  | 457.77 | 10.182 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 823.529 | 1.05 | 634.04 |  | 680.82 | 560.676 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 823.529 | 1.014 | 76.13 |  | 53.94 | 44.425 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 101.645 | 189.11 | 593.44 |  | 3530.91 | 358.899 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 101.645 | 183.507 | 591.94 |  | 3531.91 | 359.001 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 101.645 | 40.872 | 361.39 |  | 3119.62 | 317.093 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 101.645 | 40.163 | 360.39 |  | 3118.7 | 317 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 18.132 | 41.023 | 329.42 |  | 3038.22 | 55.089 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 119.777 | 38.22 | 594.57 |  | 3663.82 | 438.841 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 119.777 | 36.789 | 593.07 |  | 3661.55 | 438.569 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 12.266 | 5.522 | 251.11 |  | 2961.64 | 36.327 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 12.266 | 5.158 | 250.11 |  | 2960.81 | 36.317 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 119.777 | 5.051 | 305.66 |  | 3076.16 | 368.454 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 132.044 | 0.02013 | 17.59 | 0.91985 | 2335.98 | 308.452 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 132.044 | 0.02013 | 17.54 |  | 73.62 | 9.721 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 132.044 | 16 | 17.7 |  | 75.81 | 10.01 | preliminary | source:SRC-IECE-0005
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 13.398 | 44.331 | 75 |  | 317.52 | 4.254 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 145.442 | 15.5 | 23.04 |  | 98.08 | 14.265 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 133.176 | 6.041 | 159.05 |  | 671.45 | 89.421 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 101.645 | 211.677 | 162.82 |  | 699.92 | 71.143 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 31.53 | 47.331 | 159.84 |  | 677.3 | 21.355 | preliminary | source:SRC-IECE-0005
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 13.398 | 44.135 | 248.35 |  | 1077.67 | 14.439 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 6.9 |  | 28.08 | 286.315 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 14.1 |  | 57.38 | 585.078 | preliminary | source:SRC-IECE-0005
31 | Fuel gas to the station preheater burners (water-bath heaters) | fuel_gas | FGS | PHB | 0.0476 | 2.5 | 5 |  | -41.94 | -0.002 | preliminary | decision:DEC-EPCE-0014

## Node balances
ALP-HMB-MIN-NG-100 - node balances
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 801.288 | 0 | -26.52 | 0 | 26.52 | 0
BFP | FALSE | 133.176 | 133.175 | 89.421 | 92.498 | 0 | -3.078 | 0
CEP | FALSE | 132.044 | 132.044 | 9.721 | 10.01 | 0 | -0.288 | 0
CMIX | FALSE | 145.442 | 145.442 | 14.264 | 14.265 | 0 | -0.001 | 0
COND | FALSE | 10328.848 | 10328.848 | 594.767 | 594.799 | 0 | -0.032 | 0
FGH | FALSE | 35.64 | 35.64 | 14.439 | 14.436 | 0 | 0.003 | 0
FGS | TRUE | 0 | 22.29 | 0 | -0.002 | 0 | 0.002 | 0
GT | FALSE | 823.53 | 823.529 | 1039.711 | 560.676 | 479.028 | 0.007 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 1203.791 | 1203.791 | 984.44 | 982.352 | 0 | 2.088 | 2.065 | HRSG: gas-side duty 516.25 MW; residual = casing loss
OUT | TRUE | 10196.804 | 0 | 585.078 | 0 | 0 | 585.078 | 0
PHB | TRUE | 0.048 | 0 | -0.002 | 0 | 0 | -0.002 | 0
PIPE | FALSE | 335.333 | 335.333 | 1151.161 | 1150.888 | 0 | 0.274 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 286.315 | 0 | -286.315 | 0
ST | FALSE | 233.688 | 233.689 | 833.887 | 625.546 | 208.344 | -0.003 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 823.529 | 0 | 44.425 | 0 | 0 | 44.425 | 0

## Auxiliary loads
ALP-HMB-MIN-NG-100 - auxiliary loads
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-234 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-235 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-236 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-237 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-238 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-239 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-240 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-241 | GT GSU losses at this case load | IEC | fixed | 1311 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-242 | ST GSU losses at this case load | IEC | fixed | 604 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-243 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 3189.3 | auxiliary | enthalpy rise 3,078 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-244 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 303.6 | auxiliary | enthalpy rise 288 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-245 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-246 | Closed cooling water pumps | IEPC | fixed | 160 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-247 | Electro-chlorination | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-248 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 250 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-249 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-250 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-251 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-252 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-253 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-254 | Fuel gas receiving station | IEPC | fixed | 60 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-255 | LDO system (standby on gas) | IEPC | fixed | 30 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-MIN-NG-100 - summary
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Item | Value | Unit
GT output | 470 | MW
ST output | 204.918 | MW
Gross output | 674.918 | MW
Auxiliary loads | 9.9665 | MW
Transformer losses | 2.155 | MW
Net output | 662.7965 | MW
Heat input (LHV) | 1058.3091 | MW
Gross heat rate | 5632.9457 | kJ/kWh
Net heat rate | 5748.2393 | kJ/kWh
Net efficiency | 62.6279 | %
Auxiliary + transformer losses | 1.796 | % of gross
Fuel LHV (ISO 6976) | 47.4799 | MJ/kg
Fuel LHV volumetric | 34.7797 | MJ/Sm3
Fuel flow | 22.2896 | kg/s
Fuel flow | 109544.1354 | Sm3/h
HRSG gas-side duty | 516.2518 | MW
CW flow | 36047.3854 | m3/h
CW temperature rise | 7.2 | K
Condenser pressure | 20.13 | mbar(a)
Flue gas Ar (wet) | 0.889 | mol %
Flue gas CO2 (wet) | 4.666 | mol %
Flue gas H2O (wet) | 9.152 | mol %
Flue gas N2 (wet) | 74.407 | mol %
Flue gas O2 (wet) | 10.886 | mol %

## Checks
ALP-HMB-MIN-NG-100 - checks
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Status | Check
OK | energy balance CMIX: residual -0.001 MW (tolerance 0.25 MW)
OK | energy balance COND: residual -0.032 MW (tolerance 0.59 MW)
OK | energy balance FGH: residual +0.003 MW (tolerance 0.25 MW)
OK | energy balance GT: residual +0.007 MW (tolerance 1.04 MW)
OK | energy balance HRSG: residual +2.088 MW vs stated casing loss 2.065 MW (tolerance 0.98 MW)
OK | energy balance PIPE: residual +0.274 MW (tolerance 1.15 MW)
OK | energy balance ST: residual -0.003 MW (tolerance 0.83 MW)
OK | gas flow 109,544 Sm3/h = 91.3 % of DP-OWNR-0033 (120,000 Sm3/h)
INFO | net export 662.8 MW vs DP-OWNR-0051 connection capacity 640 MW (this case); capability above the capacity, export limited: 640 MW net at the 380 kV revenue meters (TQ-027, TP-E1)