## Streams
ALP-HMB-SRC-LDO-100 - streams
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 776.006 | 1.012 | 15 |  | -10.09 | -7.831 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 811.855 | 1.049 | 592.73 |  | 631.09 | 512.358 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 811.855 | 1.014 | 89.73 |  | 68.18 | 55.35 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 87.438 | 161.253 | 577.4 |  | 3513.19 | 307.186 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 87.438 | 156.388 | 575.9 |  | 3513.81 | 307.24 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 87.438 | 36.527 | 357.09 |  | 3118.61 | 272.685 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 87.438 | 35.941 | 356.09 |  | 3117.48 | 272.586 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 21.253 | 37.262 | 312.59 |  | 3004.74 | 63.86 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 108.692 | 34.15 | 566.02 |  | 3602.1 | 391.519 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 108.692 | 32.829 | 564.52 |  | 3599.87 | 391.277 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 15.266 | 5.499 | 242.25 |  | 2943.17 | 44.931 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 15.266 | 4.907 | 241.25 |  | 2943.26 | 44.932 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 108.692 | 4.742 | 291.27 |  | 3047.25 | 331.211 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 123.958 | 0.0334 | 25.88 | 0.91254 | 2334.77 | 289.413 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 123.958 | 0.0334 | 25.83 |  | 108.31 | 13.426 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 123.958 | 16 | 26 |  | 110.49 | 13.697 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 123.958 | 15.5 | 26.01 |  | 110.49 | 13.696 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 108.692 | 6.307 | 160.74 |  | 678.79 | 73.779 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 87.438 | 178.995 | 163.95 |  | 702.8 | 61.451 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 21.253 | 41.833 | 161.44 |  | 683.89 | 14.535 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 16 |  | 65.11 | 663.918 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 22.65 |  | 92.17 | 939.859 | preliminary | source:SRC-IECE-0005
27 | LDO at liquid fuel skid inlet (IEC terminal point IF-02) | ldo | LDS | GT | 22.406 | 5 | 30 |  | 10 | 0.224 | preliminary | source:SRC-IECE-0005
28 | Demineralised water for NOx water injection (IF-03) | water | DMW | GT | 13.443 | 60 | 30 |  | 131.2 | 1.764 | preliminary | source:SRC-IECE-0005

## Node balances
ALP-HMB-SRC-LDO-100 - node balances
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 776.006 | 0 | -7.831 | 0 | 7.831 | 0
BFP | FALSE | 108.692 | 108.691 | 73.779 | 75.986 | 0 | -2.207 | 0
CEP | FALSE | 123.958 | 123.958 | 13.426 | 13.697 | 0 | -0.271 | 0
CMIX | FALSE | 123.958 | 123.958 | 13.697 | 13.696 | 0 | 0.001 | 0
COND | FALSE | 10320.762 | 10320.762 | 953.331 | 953.285 | 0 | 0.047 | 0
DMW | TRUE | 0 | 13.443 | 0 | 1.764 | 0 | -1.764 | 0
GT | FALSE | 811.855 | 811.855 | 921.128 | 512.358 | 408.754 | 0.016 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 1131.942 | 1131.943 | 874.626 | 872.766 | 0 | 1.86 | 1.828 | HRSG: gas-side duty 457.01 MW; residual = casing loss
LDS | TRUE | 0 | 22.406 | 0 | 0.224 | 0 | -0.224 | 0
OUT | TRUE | 10196.804 | 0 | 939.859 | 0 | 0 | 939.859 | 0
PIPE | FALSE | 298.834 | 298.834 | 1016.321 | 1016.035 | 0 | 0.286 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 663.918 | 0 | -663.918 | 0
ST | FALSE | 211.396 | 211.396 | 743.449 | 562.098 | 181.353 | -0.002 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 811.855 | 0 | 55.35 | 0 | 0 | 55.35 | 0

## Auxiliary loads
ALP-HMB-SRC-LDO-100 - auxiliary loads
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-189 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-190 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-191 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-192 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-193 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-194 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-195 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-196 | GT water injection skid (LDO operation) | IEC | fixed | 200 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-197 | GT GSU losses at this case load | IEC | fixed | 1004 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-198 | ST GSU losses at this case load | IEC | fixed | 485 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-199 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 2286.9 | auxiliary | enthalpy rise 2,207 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-200 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 285 | auxiliary | enthalpy rise 271 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-201 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-202 | Closed cooling water pumps | IEPC | fixed | 160 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-203 | Electro-chlorination | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-204 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 250 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-205 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-206 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-207 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-208 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-209 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-210 | Fuel gas receiving station | IEPC | fixed | 20 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-211 | LDO system (forwarding pumps, fuel treatment) | IEPC | fixed | 170 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-SRC-LDO-100 - summary
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Item | Value | Unit
GT output | 400.5 | MW
ST output | 178.37 | MW
Gross output | 578.87 | MW
Auxiliary loads | 9.3455 | MW
Transformer losses | 1.729 | MW
Net output | 567.7955 | MW
Heat input (LHV) | 961.2174 | MW
Gross heat rate | 5977.8234 | kJ/kWh
Net heat rate | 6094.4173 | kJ/kWh
Net efficiency | 59.0705 | %
Auxiliary + transformer losses | 1.9131 | % of gross
Fuel LHV (ISO 6976) | 42.9 | MJ/kg
Fuel LHV volumetric |  | MJ/Sm3
Fuel flow | 22.406 | kg/s
Fuel flow |  | Sm3/h
HRSG gas-side duty | 457.0073 | MW
CW flow | 36111.9254 | m3/h
CW temperature rise | 6.65 | K
Condenser pressure | 33.4 | mbar(a)
Flue gas Ar (wet) | 0.874 | mol %
Flue gas CO2 (wet) | 5.687 | mol %
Flue gas H2O (wet) | 9.16 | mol %
Flue gas N2 (wet) | 73.047 | mol %
Flue gas O2 (wet) | 11.233 | mol %

## Checks
ALP-HMB-SRC-LDO-100 - checks
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Status | Check
OK | energy balance CMIX: residual +0.001 MW (tolerance 0.25 MW)
OK | energy balance COND: residual +0.047 MW (tolerance 0.95 MW)
OK | energy balance GT: residual +0.016 MW (tolerance 0.92 MW)
OK | energy balance HRSG: residual +1.860 MW vs stated casing loss 1.828 MW (tolerance 0.87 MW)
OK | energy balance PIPE: residual +0.286 MW (tolerance 1.02 MW)
OK | energy balance ST: residual -0.002 MW (tolerance 0.74 MW)
OK | net export 567.8 MW vs DP-OWNR-0051 connection capacity 640 MW (this case)
OK | gross output 578.87 MW vs IG-09 >= 572.00 (margin +1.20 %)
OK | gross heat rate 5,977.82 kJ/kWh vs IG-10 <= 6,020.00 (margin +0.70 %)
OK | net output 567.80 MW vs PG-15 >= 560.00 (margin +1.39 %)
OK | net heat rate 6,094.42 kJ/kWh vs PG-16 <= 6,150.00 (margin +0.90 %)
OK | guarantee cover: at IG-09/IG-10 limits and this HMB's auxiliaries the net plant is 560.9 MW / 6,139 kJ/kWh vs Owner PG-15 560 MW / PG-16 6,150 kJ/kWh