## Streams
ALP-HMB-SRC-NG-GT80 - streams
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 679.101 | 1.012 | 15 |  | -10.09 | -6.853 | preliminary | source:SRC-IECE-0005
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | fuel_gas | FGS | FGH | 17.398 | 38 | 25 |  | 0 | 0 | preliminary | source:SRC-IECE-0005
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 17.398 | 35.5 | 215 |  | 457.77 | 7.964 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 696.499 | 1.039 | 640 |  | 688.56 | 479.581 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 696.499 | 1.014 | 76.14 |  | 54.02 | 37.628 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 87.346 | 163.084 | 600 |  | 3571.92 | 311.993 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 87.346 | 158.287 | 598.5 |  | 3572.15 | 312.013 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 87.346 | 35.276 | 369.63 |  | 3151.31 | 275.254 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 87.346 | 34.67 | 368.63 |  | 3150.17 | 275.155 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 15.475 | 35.396 | 323.12 |  | 3037.32 | 47.003 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 103.126 | 33.002 | 600 |  | 3680.42 | 379.547 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 103.126 | 31.773 | 598.5 |  | 3677.98 | 379.296 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 10.253 | 4.709 | 243.95 |  | 2949.59 | 30.242 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 10.253 | 4.412 | 242.95 |  | 2948.59 | 30.232 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 103.126 | 4.337 | 310.68 |  | 3088.24 | 318.478 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 113.378 | 0.03204 | 25.18 | 0.9261 | 2366.47 | 268.306 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 113.378 | 0.03204 | 25.13 |  | 105.38 | 11.948 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 113.378 | 16 | 25.29 |  | 107.53 | 12.191 | preliminary | source:SRC-IECE-0005
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 11.002 | 37.068 | 75 |  | 316.93 | 3.487 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 124.381 | 15.5 | 29.74 |  | 126.07 | 15.681 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 114.128 | 5.134 | 152.79 |  | 644.31 | 73.534 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 85.959 | 180.153 | 155.9 |  | 668.41 | 57.456 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 26.477 | 40.068 | 153.44 |  | 649.24 | 17.19 | preliminary | source:SRC-IECE-0005
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 11.002 | 38.256 | 240.73 |  | 1041.04 | 11.454 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 16 |  | 65.11 | 663.918 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 22.18 |  | 90.26 | 920.356 | preliminary | source:SRC-IECE-0005
29 | HP attemperation spray water (BFP discharge) | water | BFP | HRSG | 1.386 | 180.153 | 155.9 |  | 668.41 | 0.926 | preliminary | source:SRC-IECE-0005
30 | Reheat attemperation spray water (BFP interstage) | water | BFP | HRSG | 0.305 | 40.068 | 153.44 |  | 649.24 | 0.198 | preliminary | source:SRC-IECE-0005
31 | Fuel gas to the station preheater burners (water-bath heaters) | fuel_gas | FGS | PHB | 0.0269 | 2.5 | 15 |  | -21.08 | -0.001 | preliminary | decision:DEC-EPCE-0014

## Node balances
ALP-HMB-SRC-NG-GT80 - node balances
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 679.101 | 0 | -6.853 | 0 | 6.853 | 0
BFP | FALSE | 114.128 | 114.127 | 73.534 | 75.771 | 0 | -2.237 | 0
CEP | FALSE | 113.378 | 113.378 | 11.948 | 12.191 | 0 | -0.243 | 0
CMIX | FALSE | 124.38 | 124.381 | 15.678 | 15.681 | 0 | -0.002 | 0
COND | FALSE | 10310.182 | 10310.182 | 932.224 | 932.304 | 0 | -0.081 | 0
FGH | FALSE | 28.4 | 28.4 | 11.454 | 11.451 | 0 | 0.002 | 0
FGS | TRUE | 0 | 17.425 | 0 | -0.001 | 0 | 0.001 | 0
GT | FALSE | 696.499 | 696.499 | 827.167 | 479.581 | 347.582 | 0.005 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 1022.353 | 1022.354 | 846.186 | 844.398 | 0 | 1.789 | 1.768 | HRSG: gas-side duty 441.95 MW; residual = casing loss
OUT | TRUE | 10196.804 | 0 | 920.356 | 0 | 0 | 920.356 | 0
PHB | TRUE | 0.027 | 0 | -0.001 | 0 | 0 | -0.001 | 0
PIPE | FALSE | 288.071 | 288.071 | 997.037 | 996.695 | 0 | 0.342 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 663.918 | 0 | -663.918 | 0
ST | FALSE | 200.725 | 200.724 | 721.54 | 543.56 | 177.977 | 0.003 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 696.499 | 0 | 37.628 | 0 | 0 | 37.628 | 0

## Auxiliary loads
ALP-HMB-SRC-NG-GT80 - auxiliary loads
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-123 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-124 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-125 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-126 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-127 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-128 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-129 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-130 | GT GSU losses at this case load | IEC | fixed | 777 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-131 | ST GSU losses at this case load | IEC | fixed | 471 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-132 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 2317.9 | auxiliary | enthalpy rise 2,237 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-133 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 256.1 | auxiliary | enthalpy rise 243 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-134 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-135 | Closed cooling water pumps | IEPC | fixed | 160 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-136 | Electro-chlorination | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-137 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 250 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-138 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-139 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-140 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-141 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-142 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-143 | Fuel gas receiving station | IEPC | fixed | 60 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-144 | LDO system (standby on gas) | IEPC | fixed | 30 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-SRC-NG-GT80 - summary
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Item | Value | Unit
GT output | 340 | MW
ST output | 175.05 | MW
Gross output | 515.05 | MW
Auxiliary loads | 9.0475 | MW
Transformer losses | 1.488 | MW
Net output | 504.5145 | MW
Heat input (LHV) | 827.3334 | MW
Gross heat rate | 5773.8125 | kJ/kWh
Net heat rate | 5903.4979 | kJ/kWh
Net efficiency | 60.9808 | %
Auxiliary + transformer losses | 2.0455 | % of gross
Fuel LHV (ISO 6976) | 47.4799 | MJ/kg
Fuel LHV volumetric | 34.7797 | MJ/Sm3
Fuel flow | 17.4249 | kg/s
Fuel flow | 85636.1534 | Sm3/h
HRSG gas-side duty | 441.9529 | MW
CW flow | 36111.9254 | m3/h
CW temperature rise | 6.18 | K
Condenser pressure | 32.04 | mbar(a)
Flue gas Ar (wet) | 0.884 | mol %
Flue gas CO2 (wet) | 4.309 | mol %
Flue gas H2O (wet) | 9.362 | mol %
Flue gas N2 (wet) | 73.976 | mol %
Flue gas O2 (wet) | 11.469 | mol %

## Checks
ALP-HMB-SRC-NG-GT80 - checks
engine hmb v1.2.0 ¦ data 015d1cd1c6fdda54 ¦ 2026-09-29T03:07:46Z
Status | Check
OK | energy balance CMIX: residual -0.002 MW (tolerance 0.25 MW)
OK | energy balance COND: residual -0.081 MW (tolerance 0.93 MW)
OK | energy balance FGH: residual +0.002 MW (tolerance 0.25 MW)
OK | energy balance GT: residual +0.005 MW (tolerance 0.83 MW)
OK | energy balance HRSG: residual +1.789 MW vs stated casing loss 1.768 MW (tolerance 0.85 MW)
OK | energy balance PIPE: residual +0.342 MW (tolerance 1.00 MW)
OK | energy balance ST: residual +0.003 MW (tolerance 0.72 MW)
OK | gas flow 85,636 Sm3/h = 71.4 % of DP-OWNR-0033 (120,000 Sm3/h)
OK | net export 504.5 MW vs DP-OWNR-0051 connection capacity 640 MW (this case)