IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Generators, GCB and Isolated Phase Busduct - Datasheet

| Document number | IEC-ALP-DS-102 |
| --- | --- |
| Revision | A |
| Date | 2026-12-04 |
| Status | Revised for EPC engineering - supersedes Rev 0 |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-12-04 | signed 2026-12-04 | signed 2026-12-04 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |
| 0 | 2026-09-27 | Issued for EPC engineering |
| A | 2026-12-04 | TQ-IEC-025: tags of neutral earthing / excitation transformers and protection panels |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. Generator data

| Item | GT generator IE-GH560 | ST generator IE-GA270 |
| --- | --- | --- |
| Rated apparent power | 560 MVA | 270 MVA |
| Rated power factor / active power | 0.85 lagging / 476 MW | 0.85 lagging / 229.5 MW |
| Reactive capability at rated active power | 0.85 lagging to 0.95 leading (ER-04.08) | 0.85 lagging to 0.95 leading |
| Rated voltage / frequency / speed | 21.0 kV +/- 5 % / 50 Hz / 3,000 rpm | 15.75 kV +/- 5 % / 50 Hz / 3,000 rpm |
| Cooling | hydrogen-cooled rotor and stator core, 4.0 barg H2; water-cooled stator winding | TEWAC (air, water coolers) |
| Efficiency at SRC load (incl. excitation) | 98.90 % | 98.80 % |
| Losses to cooling water at SRC | 4.3 MW (H2 coolers + stator water) | 2.2 MW (air coolers) |
| Excitation | static, from generator terminals via excitation transformer | static |
| Short-circuit ratio / Xd'' (unsaturated) | 0.50 / 0.21 pu | 0.52 / 0.18 pu |
| Insulation / temperature rise | class F / class B | class F / class B |
| Generator circuit breaker (GCB) | included, IEC 62271-37-013, 21 kV, 20 kA rated current, 130 kA | included, 15.75 kV, 12.5 kA, 100 kA |
| Isolated phase busduct (IPB) | generator - GCB - GSU LV, with tap-off to unit auxiliary transformer (UAT by EPC) | as GT |
| Stator transport weight / dimensions | 340 t / 10.8 x 4.6 x 4.9 m | 185 t / 8.6 x 4.1 x 4.2 m |
| Rotor weight (maintenance lift) | 72 t | 46 t |
| H2 / CO2 consumption | H2 make-up 12 Nm3/day; CO2 for purging 150 Nm3 per purge | - |
| Protection | IEC generator protection panels (IEEE C37.102 functions, duplicated main 1 / main 2) | as GT |

# 2. Interfaces

H2 and CO2 bottle racks and supply piping to the IEC gas control panel: by EPC (IEC-ALP-DOR-001 item 5.6).

Closed cooling water for H2 coolers, stator water coolers and TEWAC coolers: by EPC (IEC-ALP-REQ-001 table 5.1).

UAT tap-off from the IPB between GCB and GSU: IPB tap-off flange by IEC, UAT and MV busduct by EPC.

Neutral earthing: high-resistance earthing transformer in the generator neutral cubicle by IEC.

# 3. Tagged items (Rev A, TQ-IEC-025)

| Tag | Item | Rating |
| --- | --- | --- |
| 10MKA20 | GT generator neutral earthing transformer with secondary resistor | 21 kV / 240 V, 50 kVA, 10 s; limits earth fault current to 8 A |
| 20MKA20 | ST generator neutral earthing transformer with secondary resistor | 15.75 kV / 240 V, 40 kVA, 10 s; 7 A |
| 10MKC30 | GT excitation transformer | 21 / 0.9 kV, 5.5 MVA, dry type |
| 20MKC20 | ST excitation transformer | 15.75 / 0.7 kV, 2.5 MVA, dry type |
| 10MKA30 | GT generator protection panels (main 1 / main 2) | IEC 61850, 220 V DC |
| 20MKA30 | ST generator protection panels (main 1 / main 2) | IEC 61850, 220 V DC |