IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Steam Turbine IE-ST3R - Datasheet

| Document number | IEC-ALP-DS-103 |
| --- | --- |
| Revision | A |
| Date | 2026-12-04 |
| Status | Revised for EPC engineering - supersedes Rev 0 |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-12-04 | signed 2026-12-04 | signed 2026-12-04 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |
| 0 | 2026-09-27 | Issued for EPC engineering |
| A | 2026-12-04 | TQ-IEC-025: steam conditions per heat balance Rev B, bypass valve tags |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. General

| Item | Data |
| --- | --- |
| Model | IE-ST3R reheat condensing steam turbine, 3,000 rpm, two casings: HP barrel turbine and combined IP/LP turbine with double-flow LP section, side exhaust (both sides) to the condenser |
| Last stage blade / exhaust annulus | 1,070 mm, 12 % Cr steel with erosion shields / 2 x 10.8 m2 |
| Output at SRC-NG-100 | 200.73 MW at the generator terminals |
| Maximum continuous output | 235 MW (cold ambient and valves wide open) |
| Section efficiencies (SRC, isentropic, shaft) | HP 89.0 %, IP 92.5 %, LP 88.5 % (to the ELEP, incl. moisture) |
| Exhaust loss at SRC | 24.0 kJ/kg |
| Governing | throttle (sliding pressure above 50 % load), HP/IP combined stop-control valves, LP admission valve |
| Bypass valves (supplied by IEC, installed in EPC piping) | HP bypass 100 % to cold reheat; IP bypass 100 % and LP bypass 100 % to condenser dump devices; tags 10LBA10AA501 (HP bypass), 10LBB10AA501 (IP bypass), 10LBD10AA501 (LP bypass) |
| Gland steam | self-sealing above 40 % load; start-up sealing steam 4.5 t/h at 10 bar(a), 250 - 300 degC from the EPC auxiliary boiler; gland steam condenser with 2 x 100 % exhausters (IEC) |
| Lube / control oil | ISO VG 46 lube oil, tank 32 m3, 2 x 100 % AC + DC pump; fire-resistant EHC fluid (ER-07.06) |
| Turning gear | hydraulic, 5 rpm |

# 2. Steam conditions (at the ST terminal points)

| Admission | Flow kg/s | Pressure bar(a) | Temperature degC | Design pressure / temperature |
| --- | --- | --- | --- | --- |
| HP main stop valve inlet (IF-06) | 100.15 | 181.5 | 598.5 | 200 bar(a) / 605 degC |
| HP exhaust / cold reheat (IF-07) | 100.15 | 40.2 | 366.2 | 52 bar(a) / 420 degC |
| IP stop-control valve inlet (IF-10) | 117.49 | 36.2 | 598.5 | 48 bar(a) / 605 degC |
| LP admission valve inlet (IF-12) | 11.90 | 5.05 | 249.0 | 8 bar(a) / 330 degC |
| LP exhaust (to condenser) | 129.39 | 0.0344 | 26.4 | full vacuum / 1.5 bar(a) |

# 3. Operating limits

| Parameter | Value |
| --- | --- |
| Exhaust pressure: continuous / alarm / trip | 120 / 150 / 250 mbar(a) |
| Main and reheat steam temperature: continuous maximum / 400 h per year | 605 degC / 615 degC |
| Start-up (ST roll to full load) after 8 h / 48 h / cold | 25 / 60 / 150 min |
| Allowable nozzle loads | per IEC-ALP-IF-001 attachment A (NEMA SM-23 x 3.0 for HP/IP, x 1.5 for LP admission) |

# 4. Weights

| Component | Weight (t) | Remark |
| --- | --- | --- |
| HP turbine (shipped assembled) | 92 | heaviest lift in the turbine hall for maintenance: IP/LP rotor 86 t |
| IP/LP outer casing lower half (2 pieces) | 2 x 78 |  |
| IP/LP rotor | 86 | turbine hall crane: 100 t main hook minimum |
| ST generator stator | 185 | erection by hydraulic jacking/skidding, not by crane |