IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Heat Recovery Steam Generator IE-HR3 - Datasheet

| Document number | IEC-ALP-DS-104 |
| --- | --- |
| Revision | C |
| Date | 2026-12-04 |
| Status | Revised for EPC engineering - supersedes Rev 0 |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-12-04 | signed 2026-12-04 | signed 2026-12-04 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |
| 0 | 2026-09-27 | Issued for EPC engineering |
| A | 2026-09-28 | TQ-IEC-016 |
| B | 2026-09-28 | TQ-IEC-018: SCR for LDO |
| C | 2026-12-04 | TQ-IEC-025: design temperatures |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. General

| Item | Data |
| --- | --- |
| Type | IE-HR3 horizontal gas flow, triple-pressure reheat, natural circulation (HP drum thin-wall design with external cyclone separators), modular (22 modules), self-supporting casing, internally insulated |
| Design code | ASME Section I, PED 2014/68/EU module G (notified body) |
| Cycling | 250 starts/year, 30-year fatigue life per EN 12952-3 (hot 180, warm 60, cold 10 per year) |
| Gas side pressure loss at SRC | 30 mbar (incl. SCR and CO catalyst, clean) |
| Outlet to stack | HRSG outlet transition duct flange, 9.2 m diameter (stack by EPC, IF-26) |
| SCR | V2O5/TiO2 honeycomb at 360 - 370 degC (between IP superheater and HP economiser 2), aqueous ammonia 24.5 % injection grid (IEC); design NOx at HRSG outlet 22 mg/Nm3 (15 % O2); NH3 slip <= 3 mg/Nm3; catalyst life 24,000 h |
| CO catalyst | Pt/Pd oxidation catalyst at 450 degC (after HP superheater/reheater) |
| Aqueous ammonia consumption | 125 kg/h at base load on gas; 480 kg/h on LDO (GT-outlet NOx 150 mg/Nm3, 67 % removal, TQ-IEC-018) |
| Stack damper | not included (stack by EPC) |

# 2. Thermal data at SRC-NG-100

Rev B (TQ-IEC-018): SCR catalyst volume increased by 35 % and ammonia injection grid resized for LDO operation with GT-outlet NOx up to 150 mg/Nm3 (water/fuel ratio 0.60); ammonium bisulphate protection: minimum SCR inlet temperature 330 degC on LDO.

| Circuit | Flow kg/s | Outlet pressure bar(a) | Outlet temperature degC | Drum pressure bar(a) | Design pressure bar(a) / temperature degC |
| --- | --- | --- | --- | --- | --- |
| HP superheater | 100.15 | 187.0 | 600.0 | 195.0 | 210 / 610 |
| Reheater | 117.49 | 37.6 | 600.0 | - | 50 / 610 |
| IP superheater | 17.34 | 40.3 | 330.0 | 41.8 | 50 / 350 |
| LP superheater | 11.90 | 5.40 | 250.0 | 5.9 | 10 / 300 |
| Condensate preheater | 141.87 | 6.9 | 153.2 | - | 25 / 180 |

| Section | Gas in degC | Gas out degC | Duty MW |
| --- | --- | --- | --- |
| HPSH / RH | 640.0 | 450.6 | 176.83 |
| HPEVAP | 450.6 | 371.6 | 71.38 |
| IPSH | 371.6 | 366.9 | 4.19 |
| HPECO2 | 366.9 | 295.1 | 63.71 |
| IPEVAP | 295.1 | 261.0 | 29.89 |
| LPSH | 261.0 | 258.2 | 2.43 |
| HPECO1 / IPECO | 258.2 | 198.7 | 51.64 |
| LPEVAP | 198.7 | 166.2 | 27.91 |
| CPH | 166.2 | 80.2 | 73.12 |

Stack temperature 80.2 degC at SRC. Condensate preheater inlet temperature is kept at not less than 50 degC (acid dew point margin, LDO) by a 2 x 100 % CPH recirculation pump (IEC); at SRC the mixed inlet from the condensate and the fuel gas heater return is 30.9 degC before recirculation.

# 3. Water/steam quality required

Per IEC-ALP-REQ-001 section 4 (IAPWS TGD and VGB-S-010): all-volatile treatment (AVT(O)) with trisodium phosphate provision for the HP drum; continuous blowdown 0.5 % maximum at start-up, 0 % in normal operation.

# 4. Weights and transport

| Item | Data |
| --- | --- |
| Heaviest pressure-part module (HP evaporator) | 185 t, 24.0 x 3.6 x 26.5 m (shipped horizontal) |
| HP drum | 96 t, 14.0 m long, OD 1.9 m |
| Total HRSG weight (pressure parts, casing, steel, catalysts) | 6,400 t |