IMAGINARY ELECTRIC COMPANY

Power Generation Division - Plant Integration

Alpilla 600 MW Combined Cycle Power Plant - 1 x IE-9H.02 multi-shaft power island

Seawater-Cooled Surface Condenser - Datasheet

| Document number | IEC-ALP-DS-105 |
| --- | --- |
| Revision | A |
| Date | 2026-12-04 |
| Status | Revised for EPC engineering - supersedes Rev 0 |
| Addressee | Istanbul EPC Muhendislik ve Taahhut A.S. (consortium leader) - EPC engineering |
| Contract | ALP-EPC-001 (Owner contract); consortium agreement IEPC-IEC |

|  | Prepared | Checked | Approved |
| --- | --- | --- | --- |
| Function | IEC plant integration engineer | IEC lead engineer (discipline) | IEC project engineering manager |
| Signature / date | signed 2026-12-04 | signed 2026-12-04 | signed 2026-12-04 |

| Rev | Date | Description |
| --- | --- | --- |
| 0 | 2026-09-27 | Issued for EPC engineering (reference data) |
| 0 | 2026-09-27 | Issued for EPC engineering |
| A | 2026-12-04 | TQ-IEC-025: flow per heat balance Rev B, water-side design pressure |

CASE STUDY - Imaginary Electric, its products and all data are fictional.

# 1. Thermal design (HEI 11th edition)

| Item | Value |
| --- | --- |
| Type | single-shell, two-pass surface condenser, divided water boxes (two halves), side-mounted to the ST |
| Design duty at SRC-NG-100 | 290.46 MW |
| Condenser pressure at SRC | 34.44 mbar(a) (guarantee 35.5 mbar(a); ER-07.08 limit 36 mbar(a)) |
| Seawater inlet / outlet | 16.0 / 23.0 degC |
| Circulating water flow | 36,113 m3/h (10,197 kg/s) |
| Seawater properties | density 1,016.5 kg/m3, cp 4.07 kJ/kg K (salinity 22 PSU, ALP-OWN-MAR-001) |
| Surface area (incl. 5 % plugging margin) | 15,200 m2 |
| Tubes | titanium Grade 2 welded, OD 25.4 mm, 0.5 mm wall (0.7 mm in the impingement zone), effective length 9.35 m, 20,400 tubes |
| Tube velocity | 2.1 m/s (ER-07.07: 1.8 - 2.2 m/s) |
| Cleanliness factor | 0.85 |
| Seawater pressure loss | 0.62 bar (water boxes and tubes, clean) |
| Water side design / test pressure (Rev A, TQ-IEC-025) | 4.0 barg / 6.0 barg; full vacuum on the water side not required (siphon break at the outlet water boxes) |
| Tube sheets / water boxes | titanium-clad carbon steel / rubber-lined carbon steel with impressed-current cathodic protection |
| Hotwell | 30 m3 working volume (3.9 min at SRC condensate flow) |
| Dissolved oxygen at hotwell outlet | <= 20 ug/l above 50 % load |
| Bypass operation | 100 % HP/IP/LP bypass at SRC: 365 MW; maximum (cold ambient, LDO): 395 MW; seawater rise then 8.8 - 9.5 K (transient) |
| Vacuum system | 2 x 100 % liquid-ring vacuum pumps 75 kW (holding) + hogging by both pumps in parallel (30 min to 150 mbar) |
| Tube cleaning | tube cleaning ball system and debris filters: not included (by EPC with the CW system); condenser inlet water boxes prepared for ball injection and strainer connection |

# 2. Performance at other seawater temperatures (base load, SRC steam flow)

| Seawater inlet degC | 6.9 | 11.0 | 16.0 | 22.0 | 24.0 | 27.0 |
| --- | --- | --- | --- | --- | --- | --- |
| Condenser pressure mbar(a) | 19.8 | 25.5 | 34.4 | 48.7 | 54.4 | 64.2 |

At 27 degC seawater the condenser pressure is 64 mbar(a), well inside the ST continuous limit of 120 mbar(a) (ER-07.08).

# 3. Weights

| Item | Weight (t) |
| --- | --- |
| Condenser shell with tube bundles (shipped in 4 modules) | 4 x 95 |
| Operating weight (water-filled) | 1,650 |
| Flooded weight (hydrotest) | 2,300 |