## Register
Alpilla 600 MW Combined Cycle Power Plant - Technical Query Register - ALP-CA-001 Consortium agreement IEPC - IEC: power island supply and division of responsibility
engine clarification_register v1.1.0 ¦ generated 2026-09-29T02:54:29Z by SETUP ¦ data 849c15aaf34be70d
TQ | Round | Follows | Raised by | Raised | Discipline | Subject | Question | Proposal | References | Answer | Answered | Status | Outcome | Impact | Price effect (EUR) | Records changed
TQ-IEC-001 | 1 |  | Istanbul EPC | 2026-09-27 | commercial | Back-to-back cover of the Owner performance guarantees | The EPC plant HMB (ALP-HMB-SRC-NG-100) gives net 613.1 MW / 5,763 kJ/kWh with 12.25 MW of auxiliary loads and transformer losses. At the IEC guarantee limits IG-01 (614.0 MW gross) and IG-02 (5,745 kJ/kWh gross) the plant would be 601.8 MW / 5,862 kJ/kWh net, i.e. the IEC heat-rate guarantee does not cover the Owner guarantee PG-02 (5,860 kJ/kWh). The consortium cannot carry an uncovered performance LD. Please tighten IG-01/IG-02. | IG-01 >= 615.0 MW and IG-02 <= 5,735 kJ/kWh (plant then 602.8 MW / 5,852 kJ/kWh at the IEC limits). | guarantee:IG-01 guarantee:IG-02 guarantee:PG-01 guarantee:PG-02 hmb_case:SRC-NG-100 source:SRC-EPCE-0001 | IEC accepts IG-01 >= 615.0 MW and IG-02 <= 5,735 kJ/kWh (expected values 625.3 MW / 5,651 kJ/kWh keep 1.7 % and 1.5 % margin). PER-001 Rev A section 7 will show the revised values. | 2026-09-27 | closed | contractor proposal accepted | technical_only |  | guarantee/IG-01 guarantee/IG-02
TQ-IEC-002 | 1 |  | Istanbul EPC | 2026-09-27 | process | Fuel LHV basis of the IEC performance | IEC-ALP-PER-001 uses LHV 47.48 MJ/kg calculated per ISO 6976 from the Owner reference composition; the Owner contract (ER-03.02, DP-CASE-0018) states 48.4 MJ/kg for the same composition. The EPC confirms 47.48 MJ/kg (34.78 MJ/Sm3). Please confirm that the IEC guarantees are on heat input = fuel mass flow x LHV of the actual test gas (on-line chromatograph, ISO 6976) and are therefore independent of the 48.4 MJ/kg figure. | Heat input from the measured composition per ISO 6976 in all tests; the consortium asks the Owner to correct ER-03.02 / DP-CASE-0018 to 47.48 MJ/kg. | requirement:ER-03.02 design_parameter:DP-CASE-0018 source:SRC-EPCE-0001 hmb_case:SRC-NG-100 | Confirmed: the IEC guarantees are on heat input = fuel mass flow x LHV of the test gas per ISO 6976 from the on-line chromatograph; 47.48 MJ/kg is correct for the reference composition. IEC supports the correction of ER-03.02 by the Owner. | 2026-09-27 | closed | confirmed as is | none
TQ-IEC-003 | 1 |  | Istanbul EPC | 2026-09-27 | piping | Steam piping pressure and temperature drop assumptions | PER-001 section 1 assumes HP 7.0 bar / 3 K, hot reheat 1.6 bar / 3 K, cold reheat 0.8 bar / 1 K, LP 0.45 bar / 2 K between HRSG and ST. The EPC HMB node balance shows these temperature drops imply 0.96 MW of piping heat loss; the EPC preliminary piping design (P91, 250 mm mineral wool) gives about 0.35 MW. EPC values: HP 5.5 bar / 1.5 K, HRH 1.4 bar / 1.5 K, CRH 0.7 bar / 1 K, LP 0.35 bar / 1 K. Please revise PER-001 with the EPC values or give the correction curves. | IEC issues PER-001 Rev A with the EPC piping values as the expected case; guarantee corrections for piping pressure drop by curve. | process_stream:SRC-NG-100_6 process_stream:SRC-NG-100_7 process_stream:SRC-NG-100_11 process_stream:SRC-NG-100_12 scope_item:DR-018 source:SRC-EPCE-0001 | IEC agrees to use the EPC piping values as the expected case and will issue PER-001 Rev A. Guarantee correction for piping pressure drop: +1 bar HP = -0.10 MW, +0.1 bar hot reheat = -0.12 MW, +0.1 bar LP = -0.04 MW ST output. | 2026-09-27 | closed | follow up required | technical_only
TQ-IEC-004 | 1 |  | Istanbul EPC | 2026-09-27 | i_and_c | Turbine control system integration (exception E-02) | The Owner contract (SC-013) requires the power island control system to be 'integrated in' the plant DCS. IEC-ALP-REQ-001 E-02 offers a stand-alone TCS with an OPC UA gateway. The Owner will read this as a deviation. What integration can IEC offer: common operator stations, alarm management, KKS tag list, time synchronisation, IEC 62443 zones? | TCS graphics and alarms native on the DCS operator stations (no separate IEC HMI in the control room), one KKS tag database, GPS/PTP time sync from the DCS, TCS as its own IEC 62443 zone with a conduit to the DCS. | scope_item:SC-013 scope_item:DR-034 scope_item:DR-035 tie_in:IF-40 source:SRC-EPCE-0010 | IEC offers the 'IE-Control T3 HMI integration package' at no price change: TCS graphics and alarms are rendered natively on the DCS operator stations through OPC UA (redundant), one KKS tag database exported to the DCS, time sync from the DCS master clock (PTP), TCS as its own IEC 62443 zone. The TCS controllers remain IEC hardware (proven, required for turbine protection). An IEC engineering station stays in the control room. Owner acceptance of this solution for SC-013 is needed. | 2026-09-27 | closed | contractor proposal accepted | technical_only |  | scope_item/DR-034
TQ-IEC-005 | 1 |  | Istanbul EPC | 2026-09-27 | mechanical | Condenser tube cleaning balls and debris filters (E-03) | ER-07.03 requires an automatic ball-type tube cleaning system; IEC excludes it (DoR 4.2 = EPC). The EPC accepts the scope but needs the interface: ball injection and strainer nozzle positions and sizes, the CW-side pressure drop with debris filters, and confirmation that IG-04 assumes ball cleaning in operation. | New interface IF-44 in IF-001; IG-04 condition 'ball cleaning in operation, debris filters clean'. | requirement:ER-07.03 scope_item:DR-022 guarantee:IG-04 source:SRC-EPCE-0008 | Confirmed: ball cleaning and debris filters by EPC. Interface added as IF-44: two ball injection nozzles DN150 per inlet water box half, ball strainer at each outlet box DN1800 flange; CW-side pressure drop 0.62 bar clean condenser plus 0.15 bar per debris filter. IG-04 applies with ball cleaning in operation. | 2026-09-27 | closed | contractor proposal accepted | technical_only |  | tie_in/IF-44 guarantee/IG-04
TQ-IEC-006 | 1 |  | Istanbul EPC | 2026-09-27 | mechanical | Evaporative cooler provision (E-01) | ER-05.02 asks for an evaporative cooler provision. Please define what the provision includes: filter house space, structural capacity for the cooler modules and water, blanked water supply/drain connections, spare I/O. | Provision = space, structure, blanked connections and 10 % spare I/O, no price change. | requirement:ER-05.02 scope_item:DR-002 source:SRC-EPCE-0010 | Provision confirmed: filter house bay and support steel for the cooler modules (operating weight 38 t), blanked DN100 water supply and DN150 drain connections, 10 % spare I/O in the TCS. No price change. | 2026-09-27 | closed | contractor proposal accepted | none |  | scope_item/DR-002
TQ-IEC-007 | 1 |  | Istanbul EPC | 2026-09-27 | electrical | Winter output above the 640 MW grid connection capacity | PER-001 gives 683 MW gross at -4.8 degC (GT at its 470 MW limit). The Owner's connection capacity is 640 MW export (DP-OWNR-0051). Please confirm (a) a plant export limiter in the TCS acting on GT load with the MW setpoint at the HV metering point, (b) generator and GSU ratings at 470 MW GT output and 0.85 pf, (c) part-load heat rate at the export limit. | Export limiter in the TCS; the consortium asks the Owner whether the limit shall be 640 MW net. | design_parameter:DP-OWNR-0051 equipment:10MKA10 equipment:10BAT10 source:SRC-EPCE-0001 | (a) Confirmed: the TCS includes a plant export limiter acting on GT load with the MW setpoint at the HV metering point (signal from the EPC revenue meters). (b) GT generator 560 MVA covers 470 MW at 0.85 pf (553 MVA); GT GSU 560 MVA ONAF. (c) At 640 MW net export and -4.8 degC the GT runs at about 88 % load; gross heat rate about 5,690 kJ/kWh (estimate). | 2026-09-27 | closed | confirmed as is | none
TQ-IEC-008 | 1 |  | Istanbul EPC | 2026-09-27 | civil | Heavy transport of the GT (405 t) and generator stator (340 t) | Seven pieces exceed the 120 t road limit (REQ-001 section 10). Please confirm that the GT core engine and the GT generator stator cannot be split, provide transport drawings with centre of gravity and lashing points, and the planned delivery sequence, so the EPC can design the barge landing TP-M1 and the haul road for 480 t. | Transport drawings 6 weeks after NTP; deliveries by barge in the sequence GSUs, HRSG modules, GT, generators. | tie_in:TP-M1 scope_item:DR-040 source:SRC-EPCE-0010 | Confirmed: GT core engine (405 t) and GT generator stator (340 t) are single pieces. Transport drawings with centre of gravity and lashing points 6 weeks after NTP. Delivery by barge: GSUs month 14, HRSG modules months 12-16, GT month 16, generators month 17 after NTP. | 2026-09-27 | closed | confirmed as is | none
TQ-IEC-009 | 1 |  | Istanbul EPC | 2026-09-27 | process | Circulating water design flow and condenser guarantee conditions | The condenser needs 36,050 m3/h at SRC (7 K rise) against the indicative 43,000-47,000 m3/h of ER-07.11. The EPC proposes to size the CW system for 38,000 m3/h (margin for fouling, tube plugging and cold-ambient duty). Please confirm the condenser performance at 38,000 m3/h and the tube velocity limit, and whether IG-04 can be stated for 36,050-38,000 m3/h. | CW design flow 38,000 m3/h; IG-04 valid over 36,050-38,000 m3/h with the correction curve. | requirement:ER-07.11 requirement:ER-07.07 guarantee:IG-04 guarantee:PG-13 source:SRC-EPCE-0001 | Confirmed: at 38,000 m3/h the condenser pressure at SRC is 33.8 mbar(a), rise 6.6 K, tube velocity 2.2 m/s (upper ER-07.07 limit - do not exceed 38,000 m3/h). IG-04 applies from 36,050 to 38,000 m3/h with the correction curve in PER-001 Rev A. | 2026-09-27 | closed | contractor proposal accepted | technical_only |  | guarantee/IG-04 decision (CW design flow)
TQ-IEC-010 | 1 |  | Istanbul EPC | 2026-09-27 | process | Hot gas path interval and EOH start factors (E-04) | With 20 EOH per start and the ER-01.03 regime (8,000 h and 250 starts per year) the hot gas path inspection falls every 1.9 years. The Owner will read ER-05.07 as about three years. Please give start factors by start type and the resulting calendar intervals for 180 hot / 60 warm / 10 cold starts per year. | Start factors by type (hot 10, warm 15, cold 20 EOH). | requirement:ER-05.07 requirement:ER-01.03 source:SRC-EPCE-0002 | Start factors: hot 10, warm 15, cold 20 EOH; trips from base load 60 EOH. For 8,000 h and 180 hot / 60 warm / 10 cold starts per year: 10,900 EOH per year, hot gas path at 25,000 EOH after about 2.3 years, major inspection after about 4.6 years. ER-05.07 (EOH-based) is met; the calendar interval is for the Owner to note. | 2026-09-27 | closed | confirmed as is | none
TQ-IEC-011 | 1 |  | Istanbul EPC | 2026-09-27 | electrical | IEC auxiliary load list for the electrical load list | The auxiliary budget is tight: 1.96 % of gross against the 2.2 % limit (ER-04.10). Please provide the IEC consumer list with motor ratings, running/standby and load factors, and confirm that the SFC (8.5 MW) runs only during starts and is excluded from the base-load figure. | IEC load list (Excel) 4 weeks after NTP. | requirement:ER-04.10 guarantee:IG-05 aux_load:AL-01 source:SRC-EPCE-0010 | Confirmed: the SFC runs only during starts and is excluded from the base-load auxiliary figure. The IEC consumer list (motor ratings, running/standby, load factors) will be issued as IEC-ALP-REQ-001 Rev A attachment B, 4 weeks after NTP. | 2026-09-27 | closed | confirmed as is | none
TQ-IEC-012 | 2 | TQ-IEC-003 | Istanbul EPC | 2026-09-27 | process | PER-001 Rev A with the EPC piping values | Please issue IEC-ALP-PER-001 Rev A with the EPC piping pressure/temperature drops (TQ-IEC-003) and the revised guarantees (TQ-IEC-001), so the EPC can update the plant HMB and the steam piping design conditions. | Rev A issued as the new basis of SRC-NG-100. | hmb_case:SRC-NG-100 source:SRC-EPCE-0001 | PER-001 Rev A issued (2026-09-27): ST output 200.89 MW (+0.58 MW with the EPC piping values), power island gross 625.89 MW, gross heat rate 5,645.5 kJ/kWh; section 7 shows the revised guarantees and IG-07. | 2026-09-27 | closed | requirement changed | technical_only |  | process_stream/SRC-NG-100_1 process_stream/SRC-NG-100_2 process_stream/SRC-NG-100_3 process_stream/SRC-NG-100_4 process_stream/SRC-NG-100_5 process_stream/SRC-NG-100_6 process_stream/SRC-NG-100_7 process_stream/SRC-NG-100_8 process_stream/SRC-NG-100_9 process_stream/SRC-NG-100_10 process_stream/SRC-NG-100_11 process_stream/SRC-NG-100_12 process_stream/SRC-NG-100_13 process_stream/SRC-NG-100_14 process_stream/SRC-NG-100_15 process_stream/SRC-NG-100_16 process_stream/SRC-NG-100_17 process_stream/SRC-NG-100_18 process_stream/SRC-NG-100_19 process_stream/SRC-NG-100_20 process_stream/SRC-NG-100_21 process_stream/SRC-NG-100_22 process_stream/SRC-NG-100_23 process_stream/SRC-NG-100_24 process_stream/SRC-NG-100_25 process_stream/SRC-NG-100_26 hmb_case/SRC-NG-100 source (PER-001 Rev A) clarification/TQ-IEC-003
TQ-IEC-013 | 2 |  | Istanbul EPC | 2026-09-27 | process | Part-load heat rate cover for PG-03 (60 % plant load) | From the PER-001 part-load table, 60 % plant net load (368 MW) needs about 378.5 MW gross, between 50 % and 60 % GT load, with an interpolated gross heat rate of about 6,020 kJ/kWh. Net that is about 6,190 kJ/kWh against PG-03 (6,250 kJ/kWh), a 1 % margin, and there is no IEC part-load guarantee. Please give a part-load gross heat rate guarantee with sliding-pressure operation. | IG-07: gross heat rate <= 6,045 kJ/kWh at the GT load for 60 % plant net load. | guarantee:PG-03 source:SRC-EPCE-0001 | IEC gives IG-07: power island gross heat rate <= 6,060 kJ/kWh at the GT load for 60 % plant net load, sliding pressure, SRC (expected about 6,000 kJ/kWh). | 2026-09-27 | closed | contractor proposal accepted | technical_only |  | guarantee/IG-07
TQ-IEC-014 | 2 | TQ-IEC-002 | Istanbul EPC | 2026-09-27 | process | GT load versus fuel gas pressure at IF-01 | ER-03.03 (TQ-017 with the Owner) requires operation on gas at a pressure-limited load between 40 and 45 barg at TP-G1. With the EPC gas station losses of 4.7 bar, IF-01 sees 35.3 barg at 40 barg TP-G1. Please give the GT load versus IF-01 pressure curve below 36.5 barg for the load limiter. | Curve in the DS-101 revision; limiter in the TCS. | requirement:ER-03.03 tie_in:IF-01 tie_in:TP-G1 source:SRC-EPCE-0002 | GT load limit versus fuel gas pressure at IF-01 (natural gas, base-load fuel temperature): 36.5 barg 100 %, 35.0 barg 92 %, 34.0 barg 85 %, 31.5 barg 65 %, 29.0 barg 45 % (minimum for DLN operation). At 35.3 barg the GT carries about 94 % load - better than the 60 % assumed in ER-03.03. | 2026-09-27 | closed | confirmed as is | none |  | decision (GT load limiter)
TQ-IEC-015 | 3 |  | Istanbul EPC | 2026-09-27 | general | Close-out of round 1-2 and open items to the Owner | All IEC queries are answered. Please confirm the agreed changes: IG-01/02 revised, IG-04 conditions, IG-07 added, IF-44 added, DoR 1.2 and 6.1 clarified, PER-001 Rev A as the HMB basis. Items for the Owner (raised by the consortium): fuel LHV correction, TCS integration acceptance, export limit, HGP calendar interval. | Close the IEC round; carry the four Owner items in the Owner TQ register. | guarantee:IG-01 guarantee:IG-02 guarantee:IG-07 tie_in:IF-44 hmb_case:SRC-NG-100 | Confirmed. IEC will support the consortium in the Owner clarifications (TQ-025 to TQ-028). | 2026-09-27 | closed | confirmed as is | none
TQ-IEC-016 | 4 |  | Istanbul EPC | 2026-09-28 | process | HRSG temperature cross in PER-001 Rev A (IP SH and LP SH) | Rating the HRSG section by section (EPC off-design check) shows two impossible sections in PER-001 Rev A section 5: the IP superheater sits in gas at 299.9 -> 295.1 degC but delivers steam at 330 degC, and the LP superheater sits in gas at 201.5 -> 197.4 degC but delivers steam at 300 degC. Please correct the HRSG arrangement and reissue the heat balance and the HRSG datasheet. | IP SH directly after the HP evaporator; LP SH after the IP evaporator with a feasible LP steam temperature. | process_stream:SRC-NG-100_10 process_stream:SRC-NG-100_13 source:SRC-IECE-0001 source:SRC-EPCE-0005 | Confirmed - a drafting error in the Rev 0/A section order. Corrected arrangement in PER-001 Rev B and DS-104 Rev A: IP superheater directly after the HP evaporator (gas 371.6 -> 366.9 degC, steam 330 degC), LP superheater directly after the IP evaporator (gas 261.0 -> 258.2 degC) with LP steam at 250 degC. Effect: ST output 200.73 MW (-0.16 MW), LP steam 11.90 kg/s. IP-SH duty and all pinch points unchanged. | 2026-09-28 | closed | requirement changed | technical_only |  | source (PER-001 Rev B) source (DS-104 Rev A)
TQ-IEC-017 | 4 |  | Istanbul EPC | 2026-09-28 | process | Off-design heat balances for all design and guarantee cases | The plant HMB must cover all design and guarantee cases, not only SRC. Please provide rated off-design heat balances (fixed HRSG and condenser surfaces, sliding pressure, attemperation) for: SRC-NG-100; SRC-NG-GT80; SRC-NG-060 (60 % plant net load, PG-03); SRC-NG-MEL (minimum emissions-compliant load, PG-11); SRC-LDO-100 (LDO, PG-15/16); WIN-NG-100 (-4.8 degC, 99.6 %); MIN-NG-100 (-8 degC); SUM-NG-100 (32.8 degC, 0.4 %); MAX-NG-100 (40 degC with 27 degC seawater). Stream numbering as PER-001, with added streams for LDO, injection water and attemperation spray. | IEC-ALP-PER-003 case book with one stream table per case. | guarantee:PG-03 guarantee:PG-11 guarantee:PG-15 guarantee:PG-16 design_parameter:DP-OWNR-0001 design_parameter:DP-OWNR-0002 design_parameter:DP-CASE-0007 design_parameter:DP-CASE-0008 design_parameter:DP-OWNR-0012 | IEC-ALP-PER-003 Rev 0 issued with the nine cases, one stream table each; the rating model reproduces PER-001 Rev B exactly at SRC. Attemperation spray is in service at part load and at high ambient (streams 29/30). | 2026-09-28 | closed | confirmed as is | technical_only |  | source (PER-003 Rev 0)
TQ-IEC-018 | 5 |  | Istanbul EPC | 2026-09-28 | process | LDO case: net output below PG-15 and implausible air flow | The EPC HMB of PER-003 case SRC-LDO-100 gives 558.8 MW net against PG-15 (>= 560 MW), margin -0.21 %. In addition the case implies a compressor air flow of 701 kg/s on LDO against 776 kg/s on gas at the same ambient with the IGV fully open, which is not plausible: with the gas-operation air flow the stated LDO rating and water/fuel ratio 1.02 give an exhaust temperature of about 553 degC and about 543 MW / 6,300 kJ/kWh net, missing PG-15 and PG-16. Please re-rate the LDO case with the real air flow and propose how the LDO guarantees are met. | Reduce water injection and size the SCR for the higher GT-outlet NOx on LDO (ER-03.11 already requires an SCR designed for LDO). | guarantee:PG-15 guarantee:PG-16 hmb_case:SRC-LDO-100 requirement:ER-03.11 source:SRC-IECE-0004 | Agreed - the Rev 0 LDO case back-calculated the air flow. PER-003 Rev A: gas-operation air flow (776.0 kg/s), LDO rating 400.5 MW / 8,640 kJ/kWh, water/fuel 0.60 (13.4 kg/s) with GT-outlet NOx <= 150 mg/Nm3 and the IEC SCR sized for 67 % removal on LDO (DS-104 Rev B: catalyst +35 %, ammonia 480 kg/h on LDO). Exhaust 811.9 kg/s at 592.7 degC; ST 178.37 MW; about 567 MW / 6,100 kJ/kWh net with the EPC auxiliaries. New IEC guarantees IG-09/IG-10 on LDO. | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | source (PER-003 Rev A, DS-101 Rev A, DS-104 Rev B) guarantee/IG-09 guarantee/IG-10
TQ-IEC-019 | 5 |  | Istanbul EPC | 2026-09-28 | process | Minimum environmental load: 44.7 % against PG-11 (40 %) | With the GT minimum emissions-compliant load of 40 % (DS-101), case SRC-NG-MEL gives 274.3 MW net = 44.7 % of the SRC net output, against PG-11 (<= 40 % of plant net output). Please provide a lower MECL. | IEC low-load extension to reach <= 35 % plant load; as part of the power island scope (back-to-back PG-11). | guarantee:PG-11 hmb_case:SRC-NG-MEL source:SRC-EPCE-0002 | IEC includes the DLN-H2 low-load extension in the power island scope at no price change (back-to-back PG-11): MECL 30 % GT load with CO <= 30 mg/Nm3 at the stack (oxidation catalyst). PER-003 Rev A case SRC-NG-MEL at 30 % GT load: about 213 MW net = 34.8 % of the SRC net output. New IEC guarantee IG-08. | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | guarantee/IG-08 source (DS-101 Rev A)
TQ-IEC-020 | 5 | TQ-IEC-018 | Istanbul EPC | 2026-09-28 | commercial | IG-10 does not cover PG-16 | At the IG-09/IG-10 limits (572.0 MW / 6,030 kJ/kWh gross) and the EPC auxiliaries of case SRC-LDO-100 the plant is 560.2 MW / 6,157 kJ/kWh net against PG-16 (6,150 kJ/kWh). Please tighten IG-10. | IG-10 <= 6,020 kJ/kWh (expected 5,977 kJ/kWh). | guarantee:IG-09 guarantee:IG-10 guarantee:PG-16 hmb_case:SRC-LDO-100 | Accepted: IG-10 <= 6,020 kJ/kWh. | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | guarantee/IG-10
TQ-IEC-021 | 6 |  | Istanbul EPC | 2026-09-28 | general | Tie-in register: interface conditions IF-01..IF-44 for agreement | The EPC tie-in register (engine tie_in_register, draft) checks every terminal point against the nine PER-003 Rev A cases and against its upstream point. Please confirm or correct: (1) IF-06 (200 bar(a) / 605 degC), IF-10 (48 bar(a) / 605 degC) and IF-12 (8 bar(a)) are below the design of the HRSG outlets feeding them (IF-05 210 bar(a) / 610 degC, IF-09 50 bar(a) / 610 degC, IF-11 10 bar(a)); the EPC piping between them is designed for the HRSG side. State the ST valve casing design conditions, or the safety valve set points that protect the ST side. (2) HMB streams 29 and 30 (HP and reheat attemperation spray water from the EPC BFP discharge/interstage to the HRSG) cross the scope boundary but have no terminal point in IF-001 Rev 0. (3) PER-003 stream 28 (water injection) is at 60 bar(a), IF-03 is 4 in CL150 / 16 barg: confirm IF-03 is at the skid inlet upstream of IEC injection pumps, the pressure required there, and that the pump power is in the IEC auxiliaries. (4) IF-36: the EPC estimates 169 kA prospective short-circuit current at the GT generator bus (96 kA from the system via the GSU + 73 kA from the generator); state the IPB tap-off rating. (5) Confirm the operating envelopes, scope breaks, isolation, protection and dates of the attached draft (dates per the EPC commissioning sequence DEC-EPCE-0004) and re-issue IF-001. | (1) ST valve casings designed for the HRSG outlet conditions; (2) new IF-45 / IF-46 at the inlet of the IEC spray control stations; (3) IF-03 at the skid inlet, 3.0-6.0 barg; (4) tap-off rated >= 170 kA; (5) IF-001 Rev A with the agreed data. | tie_in:IF-03 tie_in:IF-06 tie_in:IF-10 tie_in:IF-12 tie_in:IF-36 process_stream:SRC-LDO-100_28 process_stream:MAX-NG-100_29 process_stream:MAX-NG-100_30 source:SRC-EPCE-0008 source:SRC-IECE-0005 | (1) The IF-001 Rev 0 values at IF-06/IF-10/IF-12 were the ST rated inlet conditions (IEC 60045-1). Valve casing design: main stop valve 215 bar(a) / 610 degC, IP stop/control valves 52 bar(a) / 610 degC, LP admission valve 10 bar(a) / 330 degC; the HRSG safety valves (HP SH <= 196 bar(a), HRH <= 48 bar(a), LP SH 8.0 bar(a)) protect both sides. (2) Accepted: IF-45 (HP spray, 3 in CL2500) and IF-46 (reheat spray, 2 in CL600) at the inlet of the IEC spray control stations. (3) Confirmed: IF-03 is the water injection skid inlet, 3.0-6.0 barg; stream 28 in PER-003 is the skid discharge; the injection pumps are in the IEC GT auxiliaries. (4) IPB tap-off rated 200 kA symmetrical / 550 kA peak. (5) Draft data confirmed with the corrections above; IEC-ALP-IF-001 Rev A issued. | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | tie_in/IF-01 tie_in/IF-02 tie_in/IF-03 tie_in/IF-04 tie_in/IF-05 tie_in/IF-06 tie_in/IF-07 tie_in/IF-08 tie_in/IF-09 tie_in/IF-10 tie_in/IF-11 tie_in/IF-12 tie_in/IF-13 tie_in/IF-14 tie_in/IF-15 tie_in/IF-16 tie_in/IF-17 tie_in/IF-18 tie_in/IF-19 tie_in/IF-20 tie_in/IF-21 tie_in/IF-22 tie_in/IF-23 tie_in/IF-24 tie_in/IF-25 tie_in/IF-26 tie_in/IF-27 tie_in/IF-28 tie_in/IF-29 tie_in/IF-30 tie_in/IF-31 tie_in/IF-32 tie_in/IF-33 tie_in/IF-34 tie_in/IF-35 tie_in/IF-36 tie_in/IF-37 tie_in/IF-38 tie_in/IF-39 tie_in/IF-40 tie_in/IF-41 tie_in/IF-42 tie_in/IF-43 tie_in/IF-44 tie_in/IF-45 tie_in/IF-46
TQ-IEC-022 | 6 |  | Istanbul EPC | 2026-09-28 | general | Codes and standards back-to-back, and IEC deliverables for permits | The codes and standards register (Appendix A.19, proposed to the Owner in TQ-033) names IEC as responsible for 62 entries (power island design, tests, Turkish regulations applicable to the IEC supply). Please confirm compliance back-to-back and state any deviation, in particular: (1) ER-06.02 allows ASME Section I or EN 12952 - which code, which PED module; ER-06.05 cites EN 12952-3 for the cyclic assessment; (2) HEI edition for the condenser (ER-07.07: 11th or later); (3) GT enclosure fire protection (ER-10.05: water mist or CO2); (4) IEC 62443 SL2 for the TCS. (5) Confirm the IEC deliverables for the permits PMT-004, 005, 008, 009, 013, 014, 015, 016, 018 and 021 with the dates of the permits register. | ASME Section I with PED module G; EN 12952-3 for fatigue of thick-walled parts; HEI 12th edition; CO2 per NFPA 12; SL2; IEC deliverables 30 days before each apply-by date. | reference:REF-CONS-0042 reference:REF-CONS-0043 reference:REF-CONS-0045 reference:REF-CONS-0082 requirement:ER-06.02 requirement:ER-06.05 requirement:ER-07.07 requirement:ER-10.05 permit:PMT-004 permit:PMT-015 | Confirmed back-to-back for all entries naming IEC, with: (1) HRSG to ASME Section I, PED module G by a notified body; EN 12952-3 for the low-cycle fatigue of the HP drum and SH/RH outlet headers; (2) HEI 12th edition; (3) GT enclosure CO2 total flooding per NFPA 12; (4) TCS system SL2 (IEC 62443-3-3) with certified components; please add ISO 20816-2 for the vibration limits of the turbines and generators. (5) IEC deliverables for the permits 30 days before each apply-by date of the permits register: generator/GSU data and models (PMT-004, PMT-021), foundation loads (PMT-005), heavy piece list and transport drawings (PMT-008, PMT-009), NDT source licences of IEC's site subcontractors (PMT-013), GT gas demand (PMT-014), inventories (PMT-015), declarations of conformity and notified body certificates (PMT-016), GT emission data (PMT-018). | 2026-09-28 | closed | contractor proposal accepted | technical_only |  | reference/REF-CONS-0043 reference/REF-CONS-0042 reference/REF-CONS-0045 reference/REF-CONS-0048 reference/REF-CONS-0082
TQ-IEC-023 | 7 |  | Istanbul EPC | 2026-09-28 | general | Engineering start: project KKS and document numbering, VDRL dates, generator delivery | (1) ER-01.06 requires KKS for all systems, equipment and documents. Please confirm that the power island (main groups MB, MK, HA, MA, BA/BAT for the GSUs, CJ/MBY for the TCS) is tagged with the project KKS key list (proposal ALP-EPC-00000-GE-PRC-0001) to component level B, and that your internal part numbers stay below component level. (2) Please confirm that every IEC deliverable carries the project document number ALP-IEC-<KKS>-<DISC>-<TYPE>-<NNNN> as primary number and the IEC number as secondary (vendor reference), as allocated in the MDL. (3) Please confirm the VDRL first-issue and final dates in the MDL (weeks after NTP). (4) The MDL / AWP timeline shows the GT generator (MR-EL-101, 52 weeks + 4 weeks sea transport) on site 2027-11-29, while GT erection CWP-01-ME-01 starts 2027-11-15 (generator set directly after the GT). Can the GT generator ship with the GT (50 weeks)? | Ship the GT generator with the GT; ST generator unchanged (needed at CWP-02-ME-01 start). | requirement:ER-01.06 requirement:ER-17.01 source:SRC-EPCE-0009 | (1) Confirmed. IEC tags the power island with the project KKS to component level (B), systems and equipment units per the project key list; IEC part numbers are kept as vendor attributes below component level. IEC checks the key titles of its main groups against its VGB-S-811 licence copy and reports deviations with the KKS manual review (IFR). (2) Confirmed: project number primary, IEC number as vendor reference on the title block. (3) Confirmed: the VDRL dates in the MDL are the IEC commitment. (4) Confirmed with an improvement: generator shop tests are brought forward; the GT generators leave the works in week 49 together with the GT (sea transport 4 weeks), on site 2027-11-08. The ST generator follows the ST train (no change). | 2026-09-28 | closed | contractor proposal accepted | none |  | mr/MR-EL-101
TQ-IEC-024 | 8 |  | Istanbul EPC | 2026-09-28 | general | Power island VDRL completed to the rule-based MDL Rev B | MDL Rev B derives the supplier documents per package from rules (mdl_rule DL-V-*). For the six IEC packages this adds 83 documents to the 37 committed in TQ-IEC-023: certified datasheets, GA, foundation loads, P&IDs, design calculations, electrical schematics, I/O lists, instrument lists, logic diagrams (TCS), ITPs, FAT procedures and reports, erection and O&M manuals, spare parts and special tools lists, manufacturing record books and commissioning procedures. Dates: weeks after the PO (NTP) for design documents, weeks before delivery for FAT, erection and O&M documents (rule fields po_weeks_ifr / po_weeks_final). Please confirm the list and the timing, and that IEC provides the heavy and oversized piece data and the transport drawings for the Harbour Master and abnormal load permits (PMT-008, PMT-009). |  | requirement:ER-15.03 requirement:ER-16.01 requirement:ER-17.04 requirement:ER-17.06 | Confirmed. The rule-based VDRL is accepted as the IEC document commitment; documents already committed in TQ-IEC-023 keep their dates. IEC provides the heavy piece data (dimensions, weights, centre of gravity, lifting points) and the transport drawings of the GT, generators, HRSG modules, ST and GSUs 12 weeks after NTP as input to the EPC heavy piece list and route survey. TCS logic diagrams are issued in two batches (protection first); the rule dates (PO + 20 / 32 weeks) are met. | 2026-09-28 | closed | confirmed as is | none
TQ-IEC-025 | 9 |  | Istanbul EPC | 2026-11-18 | general | EPC review of the power island datasheets: heat balance consistency, missing design data and tags | Review of the IEC datasheets against heat balance Rev B and the plant equipment list (review codes 2 on ALP-IEC-20MAA-ME-DSH-0001 Rev 0, ALP-IEC-10HAA-ME-DSH-0001 Rev B, ALP-IEC-10MBA-ME-DSH-0001 Rev A, ALP-IEC-10MKA-EL-DSH-0001 Rev 0, ALP-IEC-20MAG-ME-DSH-0001 Rev 0 and the GT / ST GA drawings): (1) update the ST datasheet LP flows to heat balance Rev B; (2) give the HRSG design temperatures per section; (3) state whether the GT 425 MW is shaft output and how it relates to IG-03 (418 MW at the terminals); (4) provide tags and ratings of the condensate preheater recirculation pumps, the HP / IP / LP bypass valves and dump devices, the generator neutral earthing and excitation transformers and the generator protection panels; (5) confirm the condenser circulating water design flow and give the water-side design and test pressure; (6) give the SFC starting load profile; (7) state the heaviest maintenance lift weights on the GT and ST GA drawings. |  | guarantee:IG-03 source:SRC-EPCE-0004 source:SRC-IECE-0007 source:SRC-EPCE-0006 |  |  | open

## Summary
By round | Raised | Closed | Open | Price effect (EUR)
Round 1 | 11 | 11 | 0 | 0
Round 2 | 3 | 3 | 0 | 0
Round 3 | 1 | 1 | 0 | 0
Round 4 | 2 | 2 | 0 | 0
Round 5 | 3 | 3 | 0 | 0
Round 6 | 2 | 2 | 0 | 0
Round 7 | 1 | 1 | 0 | 0
Round 8 | 1 | 1 | 0 | 0
Round 9 | 1 | 0 | 1 | 0
Total | 25 | 24 | 1 | 0
By outcome | Count
confirmed as is | 9
contractor proposal accepted | 12
follow up required | 1
none | 1
requirement changed | 2