## Streams
ALP-HMB-MAX-NG-100 - streams
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 678.416 | 1.012 | 40 |  | 15.27 | 10.359 | preliminary | source:SRC-IECE-0005
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | fuel_gas | FGS | FGH | 17.51 | 38 | 25 |  | 0 | 0 | preliminary | source:SRC-IECE-0005
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 17.51 | 35.5 | 215 |  | 457.77 | 8.016 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 695.926 | 1.039 | 653 |  | 709.62 | 493.846 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 695.926 | 1.014 | 81.92 |  | 60.59 | 42.169 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 91.085 | 170.065 | 600 |  | 3565.8 | 324.791 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 91.085 | 165.063 | 598.5 |  | 3566.19 | 324.827 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 91.085 | 36.635 | 368.13 |  | 3144.96 | 286.459 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 91.085 | 36 | 367.13 |  | 3143.88 | 286.36 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 15.05 | 36.661 | 327.03 |  | 3043.83 | 45.81 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 107.082 | 34.268 | 600 |  | 3679.42 | 393.999 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 107.082 | 32.992 | 598.5 |  | 3677.01 | 393.742 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 10.156 | 4.84 | 245.65 |  | 2952.65 | 29.987 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 10.156 | 4.558 | 244.65 |  | 2951.58 | 29.976 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 107.082 | 4.485 | 309.46 |  | 3085.37 | 330.388 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 117.238 | 0.06113 | 36.5 | 0.93755 | 2416.5 | 283.306 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 117.238 | 0.06113 | 36.45 |  | 152.7 | 17.903 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 117.238 | 16 | 36.63 |  | 154.88 | 18.158 | preliminary | source:SRC-IECE-0005
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 10.917 | 38.089 | 75 |  | 317.02 | 3.461 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 128.155 | 15.5 | 39.95 |  | 168.7 | 21.62 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 118 | 5.246 | 153.61 |  | 647.86 | 76.447 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 89.026 | 188.077 | 156.87 |  | 673.05 | 59.919 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 25.967 | 41.089 | 154.28 |  | 652.92 | 16.954 | preliminary | source:SRC-IECE-0005
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 10.917 | 39.404 | 242.91 |  | 1051.47 | 11.479 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 27 |  | 109.87 | 1120.362 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 33.4 |  | 135.92 | 1385.929 | preliminary | source:SRC-IECE-0005
29 | HP attemperation spray water (BFP discharge) | water | BFP | HRSG | 2.058 | 188.077 | 156.87 |  | 673.05 | 1.385 | preliminary | source:SRC-IECE-0005
30 | Reheat attemperation spray water (BFP interstage) | water | BFP | HRSG | 0.948 | 41.089 | 154.28 |  | 652.92 | 0.619 | preliminary | source:SRC-IECE-0005

## Node balances
ALP-HMB-MAX-NG-100 - node balances
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 678.416 | 0 | 10.359 | 0 | -10.359 | 0
BFP | FALSE | 118 | 117.999 | 76.447 | 78.877 | 0 | -2.43 | 0
CEP | FALSE | 117.238 | 117.238 | 17.903 | 18.158 | 0 | -0.255 | 0
CMIX | FALSE | 128.155 | 128.155 | 21.619 | 21.62 | 0 | -0.001 | 0
COND | FALSE | 10314.042 | 10314.042 | 1403.667 | 1403.832 | 0 | -0.164 | 0
FGH | FALSE | 28.427 | 28.427 | 11.479 | 11.476 | 0 | 0.003 | 0
FGS | TRUE | 0 | 17.51 | 0 | 0 | 0 | 0 | 0
GT | FALSE | 695.926 | 695.926 | 849.748 | 493.846 | 355.907 | -0.005 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 1033.165 | 1033.166 | 880.703 | 878.873 | 0 | 1.83 | 1.807 | HRSG: gas-side duty 451.68 MW; residual = casing loss
OUT | TRUE | 10196.804 | 0 | 1385.929 | 0 | 0 | 1385.929 | 0
PIPE | FALSE | 299.408 | 299.408 | 1035.236 | 1034.905 | 0 | 0.331 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 1120.362 | 0 | -1120.362 | 0
ST | FALSE | 208.323 | 208.323 | 748.545 | 569.765 | 178.78 | 0 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 695.926 | 0 | 42.169 | 0 | 0 | 42.169 | 0

## Auxiliary loads
ALP-HMB-MAX-NG-100 - auxiliary loads
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-278 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-279 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-280 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-281 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-282 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-283 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-284 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-285 | GT GSU losses at this case load | IEC | fixed | 805 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-286 | ST GSU losses at this case load | IEC | fixed | 474 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-287 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 2518.1 | auxiliary | enthalpy rise 2,430 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-288 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 268.8 | auxiliary | enthalpy rise 255 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-289 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-290 | Closed cooling water pumps | IEPC | fixed | 160 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-291 | Electro-chlorination | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-292 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 250 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-293 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-294 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-295 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-296 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-297 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-298 | Fuel gas receiving station | IEPC | fixed | 60 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-299 | LDO system (standby on gas) | IEPC | fixed | 30 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-MAX-NG-100 - summary
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
Item | Value | Unit
GT output | 348.234 | MW
ST output | 175.84 | MW
Gross output | 524.074 | MW
Auxiliary loads | 9.2604 | MW
Transformer losses | 1.519 | MW
Net output | 513.2946 | MW
Heat input (LHV) | 831.3739 | MW
Gross heat rate | 5710.9226 | kJ/kWh
Net heat rate | 5830.8543 | kJ/kWh
Net efficiency | 61.7405 | %
Auxiliary + transformer losses | 2.0568 | % of gross
Fuel LHV (ISO 6976) | 47.4799 | MJ/kg
Fuel LHV volumetric | 34.7797 | MJ/Sm3
Fuel flow | 17.51 | kg/s
Fuel flow | 86054.3846 | Sm3/h
HRSG gas-side duty | 451.6766 | MW
CW flow | 36190.25 | m3/h
CW temperature rise | 6.4 | K
Condenser pressure | 61.13 | mbar(a)
Flue gas Ar (wet) | 0.872 | mol %
Flue gas CO2 (wet) | 4.318 | mol %
Flue gas H2O (wet) | 10.696 | mol %
Flue gas N2 (wet) | 72.941 | mol %
Flue gas O2 (wet) | 11.173 | mol %

## Checks
ALP-HMB-MAX-NG-100 - checks
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
Status | Check
OK | energy balance CMIX: residual -0.001 MW (tolerance 0.25 MW)
OK | energy balance COND: residual -0.164 MW (tolerance 1.40 MW)
OK | energy balance FGH: residual +0.003 MW (tolerance 0.25 MW)
OK | energy balance GT: residual -0.005 MW (tolerance 0.85 MW)
OK | energy balance HRSG: residual +1.830 MW vs stated casing loss 1.807 MW (tolerance 0.88 MW)
OK | energy balance PIPE: residual +0.331 MW (tolerance 1.04 MW)
OK | energy balance ST: residual -0.000 MW (tolerance 0.75 MW)
OK | gas flow 86,054 Sm3/h = 71.7 % of DP-OWNR-0033 (120,000 Sm3/h)