## Streams
ALP-HMB-SRC-NG-060 - streams
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
No | Description | Fluid | From | To | Flow kg/s | p bar(a) | T degC | Quality | h kJ/kg | Energy flow MW | Status | Basis
1 | Ambient air to GT compressor inlet | air | AMB | GT | 559.914 | 1.012 | 15 |  | -10.09 | -5.65 | preliminary | source:SRC-IECE-0005
2 | Fuel gas at performance gas heater inlet (IEC terminal point IF-01) | fuel_gas | FGS | FGH | 13.356 | 38 | 25 |  | 0 | 0 | preliminary | source:SRC-IECE-0005
3 | Heated fuel gas to GT combustion system | fuel_gas | FGH | GT | 13.356 | 35.5 | 215 |  | 457.77 | 6.114 | preliminary | source:SRC-IECE-0005
4 | GT exhaust gas to HRSG inlet | flue_gas | GT | HRSG | 573.27 | 1.03 | 636.63 |  | 682.2 | 391.085 | preliminary | source:SRC-IECE-0005
5 | Flue gas at HRSG outlet to stack | flue_gas | HRSG | STK | 573.27 | 1.014 | 71.02 |  | 48.46 | 27.78 | preliminary | source:SRC-IECE-0005
6 | HP steam at HRSG outlet (HP SH outlet) | steam | HRSG | PIPE | 71.022 | 132.605 | 600 |  | 3598.28 | 255.557 | preliminary | source:SRC-IECE-0005
7 | HP steam at ST main stop valve inlet | steam | PIPE | ST | 71.022 | 128.705 | 598.5 |  | 3597.8 | 255.523 | preliminary | source:SRC-IECE-0005
8 | Cold reheat steam at HP turbine exhaust | steam | ST | PIPE | 71.022 | 29.015 | 377.29 |  | 3181.43 | 225.952 | preliminary | source:SRC-IECE-0005
9 | Cold reheat steam at HRSG reheater inlet | steam | PIPE | HRSG | 71.022 | 28.528 | 376.29 |  | 3180.06 | 225.854 | preliminary | source:SRC-IECE-0005
10 | IP superheated steam (joins cold reheat inside the HRSG) | steam | HRSG | HRSG | 13.43 | 29.192 | 310.9 |  | 3024.06 | 40.613 | preliminary | source:SRC-IECE-0005
11 | Hot reheat steam at HRSG outlet | steam | HRSG | PIPE | 84.855 | 27.155 | 600 |  | 3685.06 | 312.696 | preliminary | source:SRC-IECE-0005
12 | Hot reheat steam at ST IP stop/control valve inlet | steam | PIPE | ST | 84.855 | 26.144 | 598.5 |  | 3682.47 | 312.476 | preliminary | source:SRC-IECE-0005
13 | LP steam at HRSG outlet | steam | HRSG | PIPE | 8.244 | 3.845 | 235.08 |  | 2934.44 | 24.192 | preliminary | source:SRC-IECE-0005
14 | LP steam at ST LP admission | steam | PIPE | ST | 8.244 | 3.61 | 234.08 |  | 2933.27 | 24.182 | preliminary | source:SRC-IECE-0005
15 | IP turbine exhaust (crossover, internal) | steam | ST | ST | 84.855 | 3.562 | 316.36 |  | 3101.71 | 263.196 | preliminary | source:SRC-IECE-0005
16 | LP turbine exhaust to condenser (UEEP) | steam | ST | COND | 93.1 | 0.02925 | 23.66 | 0.93977 | 2396.87 | 223.149 | preliminary | source:SRC-IECE-0005
17 | Condensate at hotwell outlet / CEP suction | water | COND | CEP | 93.1 | 0.02925 | 23.61 |  | 99.02 | 9.219 | preliminary | source:SRC-IECE-0005
18 | Condensate at CEP discharge | water | CEP | CMIX | 93.1 | 16 | 23.77 |  | 101.18 | 9.42 | preliminary | source:SRC-IECE-0005
19 | Fuel gas heater water return to condensate | water | FGH | CMIX | 9.062 | 29.824 | 75 |  | 316.35 | 2.867 | preliminary | source:SRC-IECE-0005
20 | Condensate to HRSG condensate preheater inlet | water | CMIX | HRSG | 102.161 | 15.5 | 28.36 |  | 120.31 | 12.291 | preliminary | source:SRC-IECE-0005
21 | Feedwater from LP drum to boiler feed pumps | water | HRSG | BFP | 93.917 | 4.182 | 145.17 |  | 611.43 | 57.423 | preliminary | source:SRC-IECE-0005
22 | HP feedwater at BFP discharge to HP economiser | water | BFP | HRSG | 69.435 | 144.757 | 147.58 |  | 630.69 | 43.792 | preliminary | source:SRC-IECE-0005
23 | IP feedwater at BFP interstage to IP economiser | water | BFP | HRSG | 22.491 | 32.824 | 145.69 |  | 615.47 | 13.843 | preliminary | source:SRC-IECE-0005
24 | IP economiser water to performance fuel gas heater | water | HRSG | FGH | 9.062 | 31.935 | 230.21 |  | 991.27 | 8.983 | preliminary | source:SRC-IECE-0005
25 | Circulating seawater to condenser inlet | seawater | SEA | COND | 10196.804 | 2.5 | 16 |  | 65.11 | 663.918 | preliminary | source:SRC-IECE-0005
26 | Circulating seawater from condenser outlet | seawater | COND | OUT | 10196.804 | 1.7 | 21.16 |  | 86.11 | 878.032 | preliminary | source:SRC-IECE-0005
29 | HP attemperation spray water (BFP discharge) | water | BFP | HRSG | 1.587 | 144.757 | 147.58 |  | 630.69 | 1.001 | preliminary | source:SRC-IECE-0005
30 | Reheat attemperation spray water (BFP interstage) | water | BFP | HRSG | 0.404 | 32.824 | 145.69 |  | 615.47 | 0.249 | preliminary | source:SRC-IECE-0005

## Node balances
ALP-HMB-SRC-NG-060 - node balances
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
Node | Boundary | Mass in kg/s | Mass out kg/s | Energy in MW | Energy out MW | Work MW | Residual MW | Expected loss MW | Note
AMB | TRUE | 0 | 559.914 | 0 | -5.65 | 0 | 5.65 | 0
BFP | FALSE | 93.917 | 93.917 | 57.423 | 58.884 | 0 | -1.461 | 0
CEP | FALSE | 93.1 | 93.1 | 9.219 | 9.42 | 0 | -0.2 | 0
CMIX | FALSE | 102.162 | 102.161 | 12.286 | 12.291 | 0 | -0.004 | 0
COND | FALSE | 10289.904 | 10289.904 | 887.067 | 887.251 | 0 | -0.184 | 0
FGH | FALSE | 22.418 | 22.418 | 8.983 | 8.981 | 0 | 0.002 | 0
FGS | TRUE | 0 | 13.356 | 0 | 0 | 0 | 0 | 0
GT | FALSE | 573.27 | 573.27 | 634.606 | 391.085 | 243.508 | 0.013 | 0 | GT: shaft power (output / generator efficiency) + other losses
HRSG | FALSE | 840.37 | 840.37 | 688.113 | 686.631 | 0 | 1.482 | 1.453 | HRSG: gas-side duty 363.30 MW; residual = casing loss
OUT | TRUE | 10196.804 | 0 | 878.032 | 0 | 0 | 878.032 | 0
PIPE | FALSE | 235.143 | 235.143 | 818.396 | 818.034 | 0 | 0.362 | 0
SEA | TRUE | 0 | 10196.804 | 0 | 663.918 | 0 | -663.918 | 0
ST | FALSE | 164.121 | 164.122 | 592.18 | 449.1 | 143.082 | -0.002 | 0 | ST: shaft power (output / mechanical / generator efficiency)
STK | TRUE | 573.27 | 0 | 27.78 | 0 | 0 | 27.78 | 0

## Auxiliary loads
ALP-HMB-SRC-NG-060 - auxiliary loads
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
Id | Consumer | Supplier | Method | kW | Counts as | Calculation | Status | Basis
AL-145 | GT package auxiliaries (lube oil, hydraulic, enclosure ventilation, fuel skid, filter house) | IEC | fixed | 1180 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-146 | GT generator auxiliaries (seal oil, stator water, excitation) | IEC | fixed | 420 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-147 | ST auxiliaries (lube oil, EHC, gland steam exhausters) | IEC | fixed | 380 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-148 | ST generator auxiliaries (excitation, TEWAC) | IEC | fixed | 260 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-149 | HRSG auxiliaries (CPH recirculation pump, ammonia skid, drains) | IEC | fixed | 210 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-150 | Condenser vacuum pump (1 running) | IEC | fixed | 75 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-151 | Turbine control system and UPS load | IEC | fixed | 60 | auxiliary | fixed | preliminary | source:SRC-EPCE-0010
AL-152 | GT GSU losses at this case load | IEC | fixed | 475 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-153 | ST GSU losses at this case load | IEC | fixed | 343 | transformer_loss | fixed | preliminary | source:SRC-IECE-0005
AL-154 | Boiler feed pumps 2 x 100 % (1 running) | IEPC | pump_node | 1513.6 | auxiliary | enthalpy rise 1,461 kW / motor 0.965 | assumption | decision:DEC-EPCE-0001
AL-155 | Condensate extraction pumps 2 x 100 % (1 running) | IEPC | pump_node | 211 | auxiliary | enthalpy rise 200 kW / motor 0.95 | assumption | decision:DEC-EPCE-0001
AL-156 | Circulating water pumps 2 x 50 % | IEPC | cw_pump | 1938.6 | auxiliary | 10,197 kg/s x g x 16.0 m / (0.86 x 0.96) | assumption | decision:DEC-EPCE-0001
AL-157 | Closed cooling water pumps | IEPC | fixed | 160 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-158 | Electro-chlorination | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-159 | Water treatment (SWRO, demineralisation, condensate polishing) | IEPC | fixed | 250 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-160 | Compressed air | IEPC | fixed | 180 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-161 | HVAC and lighting | IEPC | fixed | 750 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-162 | Ammonia and chemical dosing | IEPC | fixed | 40 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-163 | UAT and MV/LV transformer losses | IEPC | fixed | 240 | transformer_loss | fixed | assumption | decision:DEC-EPCE-0001
AL-164 | Miscellaneous (workshop, lighting outdoor, cathodic protection) | IEPC | fixed | 300 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-165 | Fuel gas receiving station | IEPC | fixed | 60 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001
AL-166 | LDO system (standby on gas) | IEPC | fixed | 30 | auxiliary | fixed | assumption | decision:DEC-EPCE-0001

## Summary
ALP-HMB-SRC-NG-060 - summary
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
Item | Value | Unit
GT output | 237.071 | MW
ST output | 140.729 | MW
Gross output | 377.8 | MW
Auxiliary loads | 8.1982 | MW
Transformer losses | 1.058 | MW
Net output | 368.5438 | MW
Heat input (LHV) | 634.1422 | MW
Gross heat rate | 6042.6467 | kJ/kWh
Net heat rate | 6194.4107 | kJ/kWh
Net efficiency | 58.1169 | %
Auxiliary + transformer losses | 2.45 | % of gross
Fuel LHV (ISO 6976) | 47.4799 | MJ/kg
Fuel LHV volumetric | 34.7797 | MJ/Sm3
Fuel flow | 13.356 | kg/s
Fuel flow | 65639.1982 | Sm3/h
HRSG gas-side duty | 363.3044 | MW
CW flow | 36111.9254 | m3/h
CW temperature rise | 5.16 | K
Condenser pressure | 29.25 | mbar(a)
Flue gas Ar (wet) | 0.887 | mol %
Flue gas CO2 (wet) | 4.026 | mol %
Flue gas H2O (wet) | 8.821 | mol %
Flue gas N2 (wet) | 74.187 | mol %
Flue gas O2 (wet) | 12.08 | mol %

## Checks
ALP-HMB-SRC-NG-060 - checks
engine hmb v1.1.1 ¦ data a6baea26d6584942 ¦ 2026-09-29T02:54:45Z
Status | Check
OK | energy balance CMIX: residual -0.004 MW (tolerance 0.25 MW)
OK | energy balance COND: residual -0.184 MW (tolerance 0.89 MW)
OK | energy balance FGH: residual +0.002 MW (tolerance 0.25 MW)
OK | energy balance GT: residual +0.013 MW (tolerance 0.63 MW)
OK | energy balance HRSG: residual +1.482 MW vs stated casing loss 1.453 MW (tolerance 0.69 MW)
OK | energy balance PIPE: residual +0.362 MW (tolerance 0.82 MW)
OK | energy balance ST: residual -0.002 MW (tolerance 0.59 MW)
OK | gross heat rate 6,042.65 kJ/kWh vs IG-07 <= 6,060.00 (margin +0.29 %)
OK | net heat rate 6,194.41 kJ/kWh vs PG-03 <= 6,250.00 (margin +0.89 %)