## Rules
Alpilla 600 MW Combined Cycle Power Plant - Document release control - rules and summary
engine release_control v1.2.0 ¦ generated 2026-09-29T02:52:27Z by SETUP ¦ data 6d73bc5813f68e2b ¦ release rules: engine/core/release.py; gates: gate_rule records
Item | Rule / result
How to use | Before issuing a document run 'python -m engine doc status <document>' (next purpose, revision and what blocks it); issue with 'python -m engine doc issue <document> --purpose IFR¦IFA¦IFC¦AB --date ... --reason ...' (refused while blocked; --override records the justification); record the Owner / EPC review with 'python -m engine doc review <document> --rev <revision> --code 1¦2¦3¦4 --date ... --reason ...'. Gates: 'python -m engine gate [--process ...] [--scope ...] [--detail]'.
Status ladder | NONE < IFR (first issue, also IFI / IFD / IFP) < IFA < ACCEPTED (review code 1 or 2 on the latest issue; information and internal EPC documents are accepted when issued) < IFC (issued for construction; final / certified for supplier documents) < AB (as built)
Release rules | IFR / IFA: every input at least at the maturity its type requires (doc_type.input_maturity IFR or IFC); IFA needs a reviewed IFR. IFC: every EPC input IFC, every supplier input ACCEPTED, the document itself ACCEPTED by the Owner (approval / review class) or by the EPC (supplier documents), no code 3. AB: the document is IFC. An input in CHECK REQUIRED blocks.
Revisions | Letters before IFC (A, B, C ...), numbers from IFC (0, 1, 2 ...). Every revision records the input revisions it was based on; an input revised later makes the document CHECK REQUIRED (re-issue, or confirm with a new revision of the same purpose).
Release order | Sheet 'Release plan' is in network order: a document comes after all its inputs (wave = longest input chain). Within the plan the dates come from the levelled engineering timeline; priorities follow the gate need dates (PO, CWP start, key dates, milestones).
Gates | A process step (enquiry, PO, fabrication, FAT, shipment, CWP / IWP release, mechanical completion, start of commissioning, handover, Taking-Over, as-built) starts only when the documents its gate requires have the required status. Gate float = need date - planned date all requirements are met.
Commissioning / acceptance | 182 gate instance(s): 0 open now, 0 planned late
Construction | 118 gate instance(s): 0 open now, 0 planned late
Operations | 92 gate instance(s): 0 open now, 0 planned late
Owner acceptance | 4 gate instance(s): 0 open now, 0 planned late
Procurement | 259 gate instance(s): 0 open now, 0 planned late
Findings | 0 WARN line(s): 0 gate(s) planned late, 0 gate(s) with a requirement selecting no document, 0 document(s) CHECK REQUIRED

## Gates
Alpilla 600 MW Combined Cycle Power Plant - Process gates (sorted by float)
engine release_control v1.2.0 ¦ generated 2026-09-29T02:52:27Z by SETUP ¦ data 6d73bc5813f68e2b ¦ planned dates from the levelled workflow network and the CPM (working days)
Gate | Process | Scope | Title | Description | Now | Need | Planned ready | Float wd | Documents | Not met now | Requirement without documents
G-OWN-TO | Owner acceptance | 00000 | Taking-Over | test reports accepted, O&M manual, spares and special tools lists, punch list | blocked | 2029-04-18 | 2029-04-18 | 0 | 36 | 36
G-PRC-PO | Procurement | MR-EL-011 | Purchase Order Award |  | blocked | 2026-11-16 | 2026-11-16 | 0 | 4 | 4
G-PRC-FAB | Procurement | MR-EL-011 | Manufacturing Release | certified supplier data accepted | blocked | 2026-12-08 | 2026-12-07 | 1 | 1 | 1
G-CON-CWP | Construction | CWP-07-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-04-05 | 2027-03-31 | 3 | 5 | 5
G-PRC-PO | Procurement | MR-ME-011 | Purchase Order Award |  | blocked | 2027-05-17 | 2027-05-12 | 3 | 4 | 4
G-CON-CWP | Construction | CWP-12-CV-02 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-03-22 | 2027-03-16 | 4 | 10 | 10
G-PRC-ENQ | Procurement | MR-EL-011 | Enquiry Issued to Bidders |  | blocked | 2026-11-09 | 2026-11-02 | 5 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-011 | Enquiry Issued to Bidders |  | blocked | 2027-04-05 | 2027-03-26 | 6 | 2 | 2
G-PRC-PO | Procurement | MR-EL-001 | Purchase Order Award |  | blocked | 2026-12-15 | 2026-12-07 | 6 | 4 | 4
G-PRC-PO | Procurement | MR-EL-009 | Purchase Order Award |  | blocked | 2027-02-08 | 2027-01-28 | 7 | 3 | 3
G-OWN-BDP2 | Owner acceptance | 00000 | Basic Design Package Batch 2 Approved | payment milestone MS-13 (TQ-038) | blocked | 2027-08-02 | 2027-07-21 | 8 | 10 | 10
G-CON-CWP | Construction | CWP-01-CV-02 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-04-19 | 2027-04-06 | 9 | 14 | 14
G-CON-CWP | Construction | CWP-12-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-01-18 | 2027-01-05 | 9 | 4 | 5
G-PRC-FAB | Procurement | MR-ME-011 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-28 | 2027-07-15 | 9 | 5 | 5
G-CON-CWP | Construction | CWP-02-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-03-22 | 2027-03-08 | 10 | 1 | 1
G-PRC-ENQ | Procurement | MR-EL-009 | Enquiry Issued to Bidders |  | blocked | 2026-12-21 | 2026-12-07 | 10 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-001 | Enquiry Issued to Bidders |  | blocked | 2026-11-16 | 2026-11-02 | 10 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-009 | Enquiry Issued to Bidders |  | blocked | 2026-11-16 | 2026-11-02 | 10 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-012 | Enquiry Issued to Bidders |  | blocked | 2026-11-16 | 2026-11-02 | 10 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-015 | Enquiry Issued to Bidders |  | blocked | 2026-11-16 | 2026-11-02 | 10 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-016 | Enquiry Issued to Bidders |  | blocked | 2026-11-16 | 2026-11-02 | 10 | 2 | 2
G-PRC-ENQ | Procurement | MR-PI-002 | Enquiry Issued to Bidders |  | blocked | 2026-12-21 | 2026-12-07 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-001 | Release for Shipment |  | blocked | 2027-12-14 | 2027-11-30 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-002 | Release for Shipment |  | blocked | 2027-11-25 | 2027-11-11 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-003 | Release for Shipment |  | blocked | 2027-09-23 | 2027-09-09 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-004 | Release for Shipment |  | blocked | 2027-08-31 | 2027-08-17 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-005 | Release for Shipment |  | blocked | 2027-09-02 | 2027-08-19 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-006 | Release for Shipment |  | blocked | 2027-09-23 | 2027-09-09 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-007 | Release for Shipment |  | blocked | 2027-09-08 | 2027-08-25 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-008 | Release for Shipment |  | blocked | 2027-08-02 | 2027-07-19 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-EL-009 | Release for Shipment |  | blocked | 2027-05-20 | 2027-05-06 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-EL-010 | Release for Shipment |  | blocked | 2027-08-31 | 2027-08-17 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-011 | Release for Shipment |  | blocked | 2027-01-11 | 2026-12-28 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-101 | Release for Shipment |  | blocked | 2027-10-11 | 2027-09-27 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-EL-102 | Release for Shipment |  | blocked | 2027-10-18 | 2027-10-04 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-HV-001 | Release for Shipment |  | blocked | 2027-08-26 | 2027-08-12 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-IC-001 | Release for Shipment |  | blocked | 2027-10-28 | 2027-10-14 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-IC-002 | Release for Shipment |  | blocked | 2027-10-15 | 2027-10-01 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-IC-003 | Release for Shipment |  | blocked | 2027-10-19 | 2027-10-05 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-IC-004 | Release for Shipment |  | blocked | 2027-09-22 | 2027-09-08 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-IC-005 | Release for Shipment |  | blocked | 2027-10-11 | 2027-09-27 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-IC-006 | Release for Shipment |  | blocked | 2027-10-18 | 2027-10-04 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-IC-007 | Release for Shipment |  | blocked | 2027-10-11 | 2027-09-27 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-IC-008 | Release for Shipment |  | blocked | 2027-10-28 | 2027-10-14 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-IC-009 | Release for Shipment |  | blocked | 2028-02-17 | 2028-02-03 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-IC-010 | Release for Shipment |  | blocked | 2027-08-25 | 2027-08-11 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-IC-101 | Release for Shipment |  | blocked | 2027-08-09 | 2027-07-26 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-001 | Release for Shipment |  | blocked | 2027-10-21 | 2027-10-07 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-002 | Release for Shipment |  | blocked | 2027-11-01 | 2027-10-18 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-003 | Release for Shipment |  | blocked | 2027-11-18 | 2027-11-04 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-004 | Release for Shipment |  | blocked | 2027-10-22 | 2027-10-08 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-005 | Release for Shipment |  | blocked | 2027-10-25 | 2027-10-11 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-006 | Release for Shipment |  | blocked | 2027-10-13 | 2027-09-29 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-007 | Release for Shipment |  | blocked | 2027-09-16 | 2027-09-02 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-008 | Release for Shipment |  | blocked | 2027-09-16 | 2027-09-02 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-009 | Release for Shipment |  | blocked | 2027-10-21 | 2027-10-07 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-010 | Release for Shipment |  | blocked | 2027-10-05 | 2027-09-21 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-011 | Release for Shipment |  | blocked | 2027-11-10 | 2027-10-27 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-012 | Release for Shipment |  | blocked | 2027-12-02 | 2027-11-18 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-013 | Release for Shipment |  | blocked | 2027-07-23 | 2027-07-09 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-014 | Release for Shipment |  | blocked | 2027-08-26 | 2027-08-12 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-015 | Release for Shipment |  | blocked | 2027-10-21 | 2027-10-07 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-016 | Release for Shipment |  | blocked | 2027-09-23 | 2027-09-09 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-018 | Release for Shipment |  | blocked | 2027-09-20 | 2027-09-06 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-019 | Release for Shipment |  | blocked | 2027-08-16 | 2027-08-02 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-020 | Release for Shipment |  | blocked | 2027-09-09 | 2027-08-26 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-021 | Release for Shipment |  | blocked | 2027-09-23 | 2027-09-09 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-101 | Release for Shipment |  | blocked | 2027-10-18 | 2027-10-04 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-102 | Release for Shipment |  | blocked | 2027-10-04 | 2027-09-20 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-ME-103 | Release for Shipment |  | blocked | 2027-11-29 | 2027-11-15 | 10 | 2 | 2
G-PRC-SHP | Procurement | MR-PI-001 | Release for Shipment |  | blocked | 2027-06-17 | 2027-06-03 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-PI-002 | Release for Shipment |  | blocked | 2027-11-18 | 2027-11-04 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-PI-003 | Release for Shipment |  | blocked | 2027-09-13 | 2027-08-30 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-PI-004 | Release for Shipment |  | blocked | 2027-08-11 | 2027-07-28 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-PI-005 | Release for Shipment |  | blocked | 2027-09-16 | 2027-09-02 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-PI-006 | Release for Shipment |  | blocked | 2027-07-26 | 2027-07-12 | 10 | 1 | 1
G-PRC-SHP | Procurement | MR-PI-007 | Release for Shipment |  | blocked | 2027-08-19 | 2027-08-05 | 10 | 1 | 1
G-CON-IWP | Construction | CWP-02-PI-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-05-15 | 2028-04-27 | 12 | 11 | 11
G-PRC-PO | Procurement | MR-CV-002 | Purchase Order Award |  | blocked | 2027-01-11 | 2026-12-24 | 12 | 3 | 3
G-PRC-PO | Procurement | MR-ME-001 | Purchase Order Award |  | blocked | 2027-01-25 | 2027-01-07 | 12 | 4 | 4
G-PRC-PO | Procurement | MR-ME-009 | Purchase Order Award |  | blocked | 2027-01-25 | 2027-01-07 | 12 | 4 | 4
G-PRC-PO | Procurement | MR-ME-015 | Purchase Order Award |  | blocked | 2027-01-25 | 2027-01-07 | 12 | 4 | 4
G-PRC-PO | Procurement | MR-ME-016 | Purchase Order Award |  | blocked | 2027-01-25 | 2027-01-07 | 12 | 4 | 4
G-PRC-PO | Procurement | MR-PI-002 | Purchase Order Award |  | blocked | 2027-02-22 | 2027-02-04 | 12 | 3 | 3
G-PRC-FAB | Procurement | MR-EL-101 | Manufacturing Release | certified supplier data accepted | blocked | 2027-03-18 | 2027-03-01 | 13 | 6 | 5
G-CON-IWP | Construction | CWP-07-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-06-21 | 2027-06-01 | 14 | 5 | 5
G-CON-CWP | Construction | CWP-02-CV-02 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-04-19 | 2027-03-29 | 15 | 5 | 5
G-PRC-ENQ | Procurement | MR-CV-002 | Enquiry Issued to Bidders |  | blocked | 2026-11-23 | 2026-11-02 | 15 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-003 | Enquiry Issued to Bidders |  | blocked | 2026-11-23 | 2026-11-02 | 15 | 2 | 2
G-PRC-ENQ | Procurement | MR-PI-004 | Enquiry Issued to Bidders |  | blocked | 2026-12-21 | 2026-11-30 | 15 | 2 | 2
G-CON-CWP | Construction | CWP-01-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-03-22 | 2027-02-26 | 16 | 4 | 4
G-CON-IWP | Construction | CWP-07-PI-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-04-03 | 2028-03-10 | 16 | 13 | 13
G-PRC-PO | Procurement | MR-ME-003 | Purchase Order Award |  | blocked | 2027-02-01 | 2027-01-07 | 17 | 4 | 4
G-PRC-PO | Procurement | MR-ME-012 | Purchase Order Award |  | blocked | 2027-02-08 | 2027-01-14 | 17 | 4 | 4
G-PRC-PO | Procurement | MR-PI-001 | Purchase Order Award |  | blocked | 2027-02-22 | 2027-01-28 | 17 | 3 | 3
G-CON-IWP | Construction | CWP-01-PI-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-03-27 | 2028-03-01 | 18 | 19 | 19
G-PRC-FAB | Procurement | MR-ME-016 | Manufacturing Release | certified supplier data accepted | blocked | 2027-05-05 | 2027-04-09 | 18 | 6 | 6
G-CON-IWP | Construction | CWP-03-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-05-17 | 2027-04-20 | 19 | 6 | 6
G-OWN-BDP | Owner acceptance | 00000 | Basic Design Package Batch 1 Approved | payment milestone MS-02 (TQ-038) | blocked | 2027-04-02 | 2027-03-08 | 19 | 15 | 15
G-CON-IWP | Construction | CWP-01-CV-02 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-07-19 | 2027-06-21 | 20 | 14 | 14
G-CON-IWP | Construction | CWP-02-CV-02 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-07-26 | 2027-06-28 | 20 | 5 | 5
G-CON-IWP | Construction | CWP-11-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-05-24 | 2027-04-26 | 20 | 13 | 13
G-PRC-ENQ | Procurement | MR-IC-001 | Enquiry Issued to Bidders |  | blocked | 2026-11-30 | 2026-11-02 | 20 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-021 | Enquiry Issued to Bidders |  | blocked | 2026-11-30 | 2026-11-02 | 20 | 2 | 2
G-PRC-ENQ | Procurement | MR-PI-001 | Enquiry Issued to Bidders |  | blocked | 2027-01-04 | 2026-12-07 | 20 | 2 | 2
G-CON-IWP | Construction | CWP-04-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-05-17 | 2027-04-16 | 21 | 6 | 6
G-PRC-FAB | Procurement | MR-ME-102 | Manufacturing Release | certified supplier data accepted | blocked | 2027-03-16 | 2027-02-15 | 21 | 6 | 4
G-PRC-FAB | Procurement | MR-ME-001 | Manufacturing Release | certified supplier data accepted | blocked | 2027-05-17 | 2027-04-15 | 22 | 6 | 6
G-PRC-FAB | Procurement | MR-ME-009 | Manufacturing Release | certified supplier data accepted | blocked | 2027-05-17 | 2027-04-15 | 22 | 6 | 6
G-PRC-FAB | Procurement | MR-ME-015 | Manufacturing Release | certified supplier data accepted | blocked | 2027-05-17 | 2027-04-15 | 22 | 6 | 6
G-PRC-PO | Procurement | MR-ME-021 | Purchase Order Award |  | blocked | 2027-02-08 | 2027-01-07 | 22 | 4 | 4
G-CON-CWP | Construction | CWP-08-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-05-04 | 2027-04-01 | 23 | 5 | 5
G-CON-IWP | Construction | CWP-05-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-07-08 | 2027-06-04 | 24 | 9 | 9
G-PRC-PO | Procurement | MR-IC-001 | Purchase Order Award |  | blocked | 2027-02-15 | 2027-01-12 | 24 | 4 | 4
G-PRC-ENQ | Procurement | MR-EL-003 | Enquiry Issued to Bidders |  | blocked | 2026-12-07 | 2026-11-02 | 25 | 2 | 2
G-PRC-ENQ | Procurement | MR-EL-006 | Enquiry Issued to Bidders |  | blocked | 2026-12-07 | 2026-11-02 | 25 | 2 | 2
G-PRC-FAB | Procurement | MR-ME-101 | Manufacturing Release | certified supplier data accepted | blocked | 2027-03-22 | 2027-02-15 | 25 | 6 | 4
G-CON-IWP | Construction | CWP-03-HV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-11-29 | 2027-10-22 | 26 | 7 | 7
G-CON-IWP | Construction | CWP-08-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-07-13 | 2027-06-07 | 26 | 5 | 5
G-CON-IWP | Construction | CWP-08-PI-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-03-06 | 2028-01-27 | 27 | 25 | 25
G-PRC-FAB | Procurement | MR-ME-103 | Manufacturing Release | certified supplier data accepted | blocked | 2027-04-07 | 2027-03-01 | 27 | 6 | 4
G-PRC-PO | Procurement | MR-EL-003 | Purchase Order Award |  | blocked | 2027-02-15 | 2027-01-07 | 27 | 4 | 4
G-PRC-PO | Procurement | MR-EL-006 | Purchase Order Award |  | blocked | 2027-02-15 | 2027-01-07 | 27 | 4 | 4
G-PRC-PO | Procurement | MR-IC-008 | Purchase Order Award |  | blocked | 2027-06-07 | 2027-04-29 | 27 | 4 | 4
G-PRC-PO | Procurement | MR-IC-009 | Purchase Order Award |  | blocked | 2027-06-21 | 2027-05-13 | 27 | 4 | 4
G-CON-IWP | Construction | CWP-10-PI-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-03-06 | 2028-01-26 | 28 | 7 | 7
G-CON-IWP | Construction | CWP-12-PI-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-11-29 | 2027-10-20 | 28 | 12 | 12
G-PRC-PO | Procurement | MR-PI-004 | Purchase Order Award |  | blocked | 2027-02-22 | 2027-01-13 | 28 | 3 | 3
G-PRC-PO | Procurement | MR-EL-010 | Purchase Order Award |  | blocked | 2027-06-21 | 2027-05-11 | 29 | 4 | 4
G-PRC-PO | Procurement | MR-ME-010 | Purchase Order Award |  | blocked | 2027-06-28 | 2027-05-18 | 29 | 4 | 4
G-COM-MC-FF | Commissioning / acceptance | 10MBN | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 10MBP | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 10MBU | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 10MBV | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 10MBY | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 4 | 4
G-COM-MC-FF | Commissioning / acceptance | 10MKA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 4 | 4
G-COM-MC-FF | Commissioning / acceptance | 10MKC | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 10MKG | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 20MAY | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 2 | 2
G-COM-MC-FF | Commissioning / acceptance | 20MKA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 2 | 2
G-COM-MC-FF | Commissioning / acceptance | 20MKC | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-15 | 30 | 1 | 1
G-CON-CWP | Construction | CWP-01-ME-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-10-18 | 2027-09-06 | 30 | 18 | 22
G-PRC-FAB | Procurement | MR-IC-101 | Manufacturing Release | certified supplier data accepted | blocked | 2027-02-22 | 2027-01-11 | 30 | 4 | 4
G-PRC-FAB | Procurement | MR-ME-012 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-10 | 2027-04-29 | 30 | 6 | 6
G-PRC-FAT | Procurement | MR-EL-011 | Factory Acceptance Test | procedure approved | blocked | 2026-12-14 | 2026-11-02 | 30 | 1 | 1
G-PRC-PO | Procurement | MR-ME-018 | Purchase Order Award |  | blocked | 2027-04-05 | 2027-02-22 | 30 | 4 | 4
G-CON-IWP | Construction | CWP-09-PI-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-01-24 | 2027-12-10 | 31 | 5 | 5
G-CON-IWP | Construction | CWP-10-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-08-05 | 2027-06-23 | 31 | 5 | 5
G-PRC-ENQ | Procurement | MR-EL-001 | Enquiry Issued to Bidders |  | blocked | 2026-12-15 | 2026-11-02 | 31 | 2 | 2
G-CON-CWP | Construction | CWP-05-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-03-25 | 2027-02-09 | 32 | 9 | 9
G-PRC-ENQ | Procurement | MR-ME-010 | Enquiry Issued to Bidders |  | blocked | 2027-05-10 | 2027-03-25 | 32 | 2 | 2
G-PRC-PO | Procurement | MR-EL-002 | Purchase Order Award |  | blocked | 2027-04-05 | 2027-02-18 | 32 | 4 | 4
G-PRC-PO | Procurement | MR-HV-001 | Purchase Order Award |  | blocked | 2027-03-15 | 2027-01-28 | 32 | 4 | 4
G-PRC-PO | Procurement | MR-ME-007 | Purchase Order Award |  | blocked | 2027-04-05 | 2027-02-18 | 32 | 4 | 4
G-PRC-PO | Procurement | MR-ME-008 | Purchase Order Award |  | blocked | 2027-04-05 | 2027-02-18 | 32 | 4 | 4
G-PRC-FAB | Procurement | MR-ME-010 | Manufacturing Release | certified supplier data accepted | blocked | 2027-08-23 | 2027-07-06 | 34 | 5 | 5
G-PRC-PO | Procurement | MR-SS-001 | Purchase Order Award |  | blocked | 2027-03-23 | 2027-02-03 | 34 | 3 | 3
G-PRC-PO | Procurement | MR-SS-002 | Purchase Order Award |  | blocked | 2027-03-22 | 2027-02-02 | 34 | 3 | 3
G-CON-IWP | Construction | CWP-02-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-04-26 | 2027-03-08 | 35 | 1 | 1
G-CON-IWP | Construction | CWP-12-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-03-01 | 2027-01-11 | 35 | 3 | 3
G-PRC-ENQ | Procurement | MR-IC-008 | Enquiry Issued to Bidders |  | blocked | 2027-04-12 | 2027-02-22 | 35 | 2 | 2
G-PRC-ENQ | Procurement | MR-IC-009 | Enquiry Issued to Bidders |  | blocked | 2027-04-12 | 2027-02-22 | 35 | 2 | 2
G-PRC-FAB | Procurement | MR-ME-003 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-03 | 2027-04-15 | 35 | 6 | 6
G-PRC-PO | Procurement | MR-IC-006 | Purchase Order Award |  | blocked | 2027-07-19 | 2027-05-31 | 35 | 4 | 4
G-PRC-PO | Procurement | MR-ME-002 | Purchase Order Award |  | blocked | 2027-04-12 | 2027-02-22 | 35 | 4 | 4
G-CON-IWP | Construction | CWP-09-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-09-15 | 2027-07-27 | 36 | 8 | 8
G-PRC-ENQ | Procurement | MR-EL-010 | Enquiry Issued to Bidders |  | blocked | 2027-04-26 | 2027-03-04 | 37 | 2 | 2
G-PRC-PO | Procurement | MR-EL-005 | Purchase Order Award |  | blocked | 2027-03-29 | 2027-02-04 | 37 | 4 | 4
G-PRC-PO | Procurement | MR-ME-020 | Purchase Order Award |  | blocked | 2027-03-22 | 2027-01-28 | 37 | 4 | 4
G-PRC-FAB | Procurement | MR-ME-018 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-28 | 2027-05-05 | 38 | 6 | 6
G-COM-MC-FF | Commissioning / acceptance | 00QJB | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00QUA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00SAA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 6 | 6
G-COM-MC-FF | Commissioning / acceptance | 00SGA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 6 | 6
G-COM-MC-FF | Commissioning / acceptance | 00SGC | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00SGY | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00SMA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 10HAA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 10HNA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 10HNE | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 10HSA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 10HSB | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 10MBA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 10MBL | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-05-01 | 40 | 1 | 1
G-PRC-FAB | Procurement | MR-HV-001 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-07 | 2027-04-12 | 40 | 5 | 5
G-PRC-FAB | Procurement | MR-ME-007 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-28 | 2027-05-03 | 40 | 6 | 6
G-PRC-FAB | Procurement | MR-ME-008 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-28 | 2027-05-03 | 40 | 6 | 6
G-PRC-FAT | Procurement | MR-EL-001 | Factory Acceptance Test | procedure approved | blocked | 2027-11-16 | 2027-09-21 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-002 | Factory Acceptance Test | procedure approved | blocked | 2027-10-28 | 2027-09-02 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-003 | Factory Acceptance Test | procedure approved | blocked | 2027-08-26 | 2027-07-01 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-004 | Factory Acceptance Test | procedure approved | blocked | 2027-08-03 | 2027-06-08 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-005 | Factory Acceptance Test | procedure approved | blocked | 2027-08-05 | 2027-06-10 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-006 | Factory Acceptance Test | procedure approved | blocked | 2027-08-26 | 2027-07-01 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-007 | Factory Acceptance Test | procedure approved | blocked | 2027-08-11 | 2027-06-16 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-010 | Factory Acceptance Test | procedure approved | blocked | 2027-08-03 | 2027-06-08 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-101 | Factory Acceptance Test | procedure approved | blocked | 2027-09-13 | 2027-07-19 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-EL-102 | Factory Acceptance Test | procedure approved | blocked | 2027-09-20 | 2027-07-26 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-HV-001 | Factory Acceptance Test | procedure approved | blocked | 2027-07-29 | 2027-06-03 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-IC-001 | Factory Acceptance Test | procedure approved | blocked | 2027-09-30 | 2027-08-05 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-IC-002 | Factory Acceptance Test | procedure approved | blocked | 2027-09-17 | 2027-07-23 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-IC-003 | Factory Acceptance Test | procedure approved | blocked | 2027-09-21 | 2027-07-27 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-IC-006 | Factory Acceptance Test | procedure approved | blocked | 2027-09-20 | 2027-07-26 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-IC-007 | Factory Acceptance Test | procedure approved | blocked | 2027-09-13 | 2027-07-19 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-IC-008 | Factory Acceptance Test | procedure approved | blocked | 2027-09-30 | 2027-08-05 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-IC-009 | Factory Acceptance Test | procedure approved | blocked | 2028-01-20 | 2027-11-25 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-IC-101 | Factory Acceptance Test | procedure approved | blocked | 2027-07-12 | 2027-05-17 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-001 | Factory Acceptance Test | procedure approved | blocked | 2027-09-23 | 2027-07-29 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-002 | Factory Acceptance Test | procedure approved | blocked | 2027-10-04 | 2027-08-09 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-003 | Factory Acceptance Test | procedure approved | blocked | 2027-10-21 | 2027-08-26 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-004 | Factory Acceptance Test | procedure approved | blocked | 2027-09-24 | 2027-07-30 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-005 | Factory Acceptance Test | procedure approved | blocked | 2027-09-27 | 2027-08-02 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-006 | Factory Acceptance Test | procedure approved | blocked | 2027-09-15 | 2027-07-21 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-007 | Factory Acceptance Test | procedure approved | blocked | 2027-08-19 | 2027-06-24 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-008 | Factory Acceptance Test | procedure approved | blocked | 2027-08-19 | 2027-06-24 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-009 | Factory Acceptance Test | procedure approved | blocked | 2027-09-23 | 2027-07-29 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-010 | Factory Acceptance Test | procedure approved | blocked | 2027-09-07 | 2027-07-13 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-011 | Factory Acceptance Test | procedure approved | blocked | 2027-10-13 | 2027-08-18 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-012 | Factory Acceptance Test | procedure approved | blocked | 2027-11-04 | 2027-09-09 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-013 | Factory Acceptance Test | procedure approved | blocked | 2027-06-25 | 2027-04-30 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-014 | Factory Acceptance Test | procedure approved | blocked | 2027-07-29 | 2027-06-03 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-015 | Factory Acceptance Test | procedure approved | blocked | 2027-09-23 | 2027-07-29 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-016 | Factory Acceptance Test | procedure approved | blocked | 2027-08-26 | 2027-07-01 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-018 | Factory Acceptance Test | procedure approved | blocked | 2027-08-23 | 2027-06-28 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-019 | Factory Acceptance Test | procedure approved | blocked | 2027-07-19 | 2027-05-24 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-020 | Factory Acceptance Test | procedure approved | blocked | 2027-08-12 | 2027-06-17 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-021 | Factory Acceptance Test | procedure approved | blocked | 2027-08-26 | 2027-07-01 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-101 | Factory Acceptance Test | procedure approved | blocked | 2027-09-20 | 2027-07-26 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-102 | Factory Acceptance Test | procedure approved | blocked | 2027-09-06 | 2027-07-12 | 40 | 1 | 1
G-PRC-FAT | Procurement | MR-ME-103 | Factory Acceptance Test | procedure approved | blocked | 2027-11-01 | 2027-09-06 | 40 | 1 | 1
G-PRC-PO | Procurement | MR-IC-007 | Purchase Order Award |  | blocked | 2027-07-19 | 2027-05-24 | 40 | 4 | 4
G-PRC-PO | Procurement | MR-ME-005 | Purchase Order Award |  | blocked | 2027-04-12 | 2027-02-15 | 40 | 4 | 4
G-PRC-FAB | Procurement | MR-EL-010 | Manufacturing Release | certified supplier data accepted | blocked | 2027-08-04 | 2027-06-08 | 41 | 1 | 1
G-PRC-PO | Procurement | MR-ME-004 | Purchase Order Award |  | blocked | 2027-04-12 | 2027-02-12 | 41 | 4 | 4
G-CON-IWP | Construction | CWP-01-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-05-03 | 2027-03-04 | 42 | 4 | 4
G-PRC-ENQ | Procurement | MR-IC-006 | Enquiry Issued to Bidders |  | blocked | 2027-05-24 | 2027-03-24 | 43 | 2 | 2
G-PRC-FAB | Procurement | MR-IC-008 | Manufacturing Release | certified supplier data accepted | blocked | 2027-08-18 | 2027-06-18 | 43 | 4 | 4
G-PRC-FAB | Procurement | MR-ME-021 | Manufacturing Release | certified supplier data accepted | blocked | 2027-05-19 | 2027-03-19 | 43 | 5 | 5
G-PRC-PO | Procurement | MR-EL-007 | Purchase Order Award |  | blocked | 2027-05-10 | 2027-03-10 | 43 | 4 | 4
G-PRC-PO | Procurement | MR-ME-023 | Purchase Order Award |  | blocked | 2027-11-15 | 2027-09-15 | 43 | 3 | 3
G-PRC-ENQ | Procurement | MR-HV-001 | Enquiry Issued to Bidders |  | blocked | 2027-01-04 | 2026-11-02 | 45 | 2 | 2
G-PRC-ENQ | Procurement | MR-SS-002 | Enquiry Issued to Bidders |  | blocked | 2027-01-11 | 2026-11-09 | 45 | 2 | 2
G-PRC-FAB | Procurement | MR-IC-006 | Manufacturing Release | certified supplier data accepted | blocked | 2027-09-13 | 2027-07-12 | 45 | 4 | 4
G-PRC-FAB | Procurement | MR-ME-020 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-18 | 2027-04-16 | 45 | 6 | 6
G-PRC-PO | Procurement | MR-IC-005 | Purchase Order Award |  | blocked | 2027-05-17 | 2027-03-15 | 45 | 3 | 3
G-CON-CWP | Construction | CWP-10-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-06-03 | 2027-03-31 | 46 | 5 | 5
G-CON-IWP | Construction | CWP-05-PI-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-12-13 | 2027-10-08 | 46 | 10 | 10
G-PRC-ENQ | Procurement | MR-ME-023 | Enquiry Issued to Bidders |  | blocked | 2027-08-30 | 2027-06-25 | 46 | 2 | 2
G-PRC-FAB | Procurement | MR-ME-002 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-21 | 2027-05-18 | 46 | 6 | 6
G-PRC-PO | Procurement | MR-CV-003 | Purchase Order Award |  | blocked | 2027-05-14 | 2027-03-11 | 46 | 3 | 3
G-PRC-FAB | Procurement | MR-IC-001 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-07 | 2027-04-01 | 47 | 4 | 4
G-PRC-PO | Procurement | MR-CV-001 | Purchase Order Award |  | blocked | 2027-03-22 | 2027-01-14 | 47 | 3 | 3
G-PRC-ENQ | Procurement | MR-IC-007 | Enquiry Issued to Bidders |  | blocked | 2027-05-24 | 2027-03-17 | 48 | 2 | 2
G-PRC-FAB | Procurement | MR-EL-003 | Manufacturing Release | certified supplier data accepted | blocked | 2027-05-26 | 2027-03-19 | 48 | 4 | 4
G-PRC-FAB | Procurement | MR-EL-006 | Manufacturing Release | certified supplier data accepted | blocked | 2027-05-26 | 2027-03-19 | 48 | 5 | 5
G-CON-CWP | Construction | CWP-11-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-03-29 | 2027-01-19 | 49 | 13 | 14
G-PRC-PO | Procurement | MR-EL-004 | Purchase Order Award |  | blocked | 2027-05-10 | 2027-03-02 | 49 | 4 | 4
G-COM-MC-EL | Commissioning / acceptance | 20BAA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-02-01 | 50 | 1 | 1
G-COM-MC-EL | Commissioning / acceptance | 20BAC | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-02-01 | 50 | 1 | 1
G-COM-MC-EL | Commissioning / acceptance | 20BAT | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-02-01 | 50 | 2 | 2
G-COM-MC-EL | Commissioning / acceptance | 20BBT | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-02-01 | 50 | 1 | 1
G-COM-MC-FF | Commissioning / acceptance | 00GMA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 4 | 4
G-COM-MC-FF | Commissioning / acceptance | 00GNA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00GUA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00LDA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00PAA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00PAB | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 4 | 4
G-COM-MC-FF | Commissioning / acceptance | 00PAC | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00PAH | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00PBA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00PGA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00QCA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00QEA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00QHA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00QJA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-17 | 50 | 5 | 5
G-COM-MC-WS | Commissioning / acceptance | 20MAG | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-19 | 50 | 2 | 2
G-COM-MC-WS | Commissioning / acceptance | 20MAJ | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-19 | 50 | 1 | 1
G-COM-MC-WS | Commissioning / acceptance | 20MAN | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-19 | 50 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 20MAV | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-19 | 50 | 1 | 1
G-COM-MC-WS | Commissioning / acceptance | 20MAW | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-19 | 50 | 1 | 1
G-COM-MC-WS | Commissioning / acceptance | 20MAX | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-19 | 50 | 1 | 1
G-COM-SC-FF | Commissioning / acceptance | 10MBN | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10MBP | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10MBU | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10MBV | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10MBY | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10MKA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10MKC | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10MKG | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 20MAY | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 20MKA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 20MKC | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-15 | 50 | 3 | 3
G-PRC-ENQ | Procurement | MR-ME-020 | Enquiry Issued to Bidders |  | blocked | 2027-01-11 | 2026-11-02 | 50 | 2 | 2
G-PRC-FAB | Procurement | MR-EL-102 | Manufacturing Release | certified supplier data accepted | blocked | 2027-03-22 | 2027-01-11 | 50 | 5 | 3
G-PRC-FAB | Procurement | MR-IC-007 | Manufacturing Release | certified supplier data accepted | blocked | 2027-09-13 | 2027-07-05 | 50 | 4 | 4
G-PRC-ENQ | Procurement | MR-SS-001 | Enquiry Issued to Bidders |  | blocked | 2027-01-19 | 2026-11-09 | 51 | 2 | 2
G-PRC-FAB | Procurement | MR-ME-005 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-21 | 2027-05-11 | 51 | 6 | 6
G-PRC-FAB | Procurement | MR-ME-004 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-21 | 2027-05-10 | 52 | 6 | 6
G-CON-CWP | Construction | CWP-03-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-03-29 | 2027-01-13 | 53 | 6 | 7
G-CON-CWP | Construction | CWP-08-ME-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-11-01 | 2027-08-18 | 53 | 26 | 27
G-PRC-FAB | Procurement | MR-EL-001 | Manufacturing Release | certified supplier data accepted | blocked | 2027-05-10 | 2027-02-23 | 54 | 5 | 5
G-PRC-ENQ | Procurement | MR-EL-005 | Enquiry Issued to Bidders |  | blocked | 2027-01-18 | 2026-11-02 | 55 | 2 | 2
G-PRC-PO | Procurement | MR-ME-019 | Purchase Order Award |  | blocked | 2027-05-03 | 2027-02-15 | 55 | 4 | 4
G-PRC-PO | Procurement | MR-ME-024 | Purchase Order Award |  | blocked | 2027-11-15 | 2027-08-30 | 55 | 3 | 3
G-PRC-FAB | Procurement | MR-EL-005 | Manufacturing Release | certified supplier data accepted | blocked | 2027-06-21 | 2027-04-01 | 57 | 4 | 4
G-PRC-FAB | Procurement | MR-IC-009 | Manufacturing Release | certified supplier data accepted | blocked | 2027-10-11 | 2027-07-22 | 57 | 4 | 4
G-CON-CWP | Construction | CWP-12-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-05-17 | 2027-02-24 | 58 | 8 | 8
G-CON-IWP | Construction | CWP-01-SS-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-09-27 | 2027-07-06 | 59 | 5 | 5
G-CON-IWP | Construction | CWP-02-SS-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-09-27 | 2027-07-06 | 59 | 3 | 3
G-PRC-FAB | Procurement | MR-EL-007 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-21 | 2027-04-29 | 59 | 4 | 4
G-COM-MC-EL | Commissioning / acceptance | 00ACA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 3 | 3
G-COM-MC-EL | Commissioning / acceptance | 00BBA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 3 | 3
G-COM-MC-EL | Commissioning / acceptance | 00BFA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 16 | 16
G-COM-MC-EL | Commissioning / acceptance | 00BFT | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 2 | 2
G-COM-MC-EL | Commissioning / acceptance | 00BLA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 1 | 1
G-COM-MC-EL | Commissioning / acceptance | 00BMA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 1 | 1
G-COM-MC-EL | Commissioning / acceptance | 00BRA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 3 | 3
G-COM-MC-EL | Commissioning / acceptance | 00BTA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 1 | 1
G-COM-MC-EL | Commissioning / acceptance | 00BXA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 1 | 1
G-COM-MC-EL | Commissioning / acceptance | 00XJA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 3 | 3
G-COM-MC-EL | Commissioning / acceptance | 10BAA | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 1 | 1
G-COM-MC-EL | Commissioning / acceptance | 10BAC | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 1 | 1
G-COM-MC-EL | Commissioning / acceptance | 10BAT | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 3 | 3
G-COM-MC-EL | Commissioning / acceptance | 10BBT | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | blocked | 2028-04-11 | 2028-01-18 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00CJA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00CJG | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00CKA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00CQA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00CYA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00EGA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00EGB | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00EGC | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00EKA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00EKC | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00GBA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00GCA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 3 | 3
G-COM-MC-FF | Commissioning / acceptance | 00GHA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 5 | 5
G-COM-MC-FF | Commissioning / acceptance | 00GKA | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | blocked | 2028-06-26 | 2028-04-03 | 60 | 4 | 4
G-COM-MC-WS | Commissioning / acceptance | 00LBG | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 10HAN | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 5 | 5
G-COM-MC-WS | Commissioning / acceptance | 10LAB | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 10LAC | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 5 | 5
G-COM-MC-WS | Commissioning / acceptance | 10LAE | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 10LAF | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 10LBA | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 10LBB | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 10LBC | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 10LBD | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 20LCA | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 20LCB | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 5 | 5
G-COM-MC-WS | Commissioning / acceptance | 20MAA | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 3 | 3
G-COM-MC-WS | Commissioning / acceptance | 20MAB | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | blocked | 2028-08-28 | 2028-06-05 | 60 | 1 | 1
G-COM-SC-FF | Commissioning / acceptance | 00QJB | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00QUA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00SAA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00SGA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00SGC | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00SGY | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00SMA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10HAA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10HNA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10HNE | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 2 | 2
G-COM-SC-FF | Commissioning / acceptance | 10HSA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10HSB | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 10MBA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 10MBL | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-05-01 | 60 | 3 | 3
G-CON-CWP | Construction | CWP-11-SS-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-05-24 | 2027-03-01 | 60 | 12 | 12
G-CON-IWP | Construction | CWP-08-SS-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-09-07 | 2027-06-15 | 60 | 3 | 3
G-PRC-ENQ | Procurement | MR-EL-002 | Enquiry Issued to Bidders |  | blocked | 2027-01-25 | 2026-11-02 | 60 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-007 | Enquiry Issued to Bidders |  | blocked | 2027-01-25 | 2026-11-02 | 60 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-008 | Enquiry Issued to Bidders |  | blocked | 2027-01-25 | 2026-11-02 | 60 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-018 | Enquiry Issued to Bidders |  | blocked | 2027-01-25 | 2026-11-02 | 60 | 2 | 2
G-PRC-FAB | Procurement | MR-ME-019 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-14 | 2027-04-20 | 61 | 6 | 6
G-CON-CWP | Construction | CWP-03-SS-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-05-24 | 2027-02-25 | 62 | 4 | 4
G-PRC-FAB | Procurement | MR-EL-002 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-26 | 2027-04-29 | 62 | 5 | 5
G-PRC-ENQ | Procurement | MR-ME-024 | Enquiry Issued to Bidders |  | blocked | 2027-09-20 | 2027-06-23 | 63 | 2 | 2
G-CON-CWP | Construction | CWP-04-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-04-05 | 2027-01-05 | 64 | 6 | 7
G-CON-IWP | Construction | CWP-06-CV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-12-03 | 2027-09-06 | 64 | 11 | 11
G-PRC-ENQ | Procurement | MR-CV-001 | Enquiry Issued to Bidders |  | blocked | 2027-02-01 | 2026-11-02 | 65 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-002 | Enquiry Issued to Bidders |  | blocked | 2027-02-01 | 2026-11-02 | 65 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-004 | Enquiry Issued to Bidders |  | blocked | 2027-02-01 | 2026-11-02 | 65 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-005 | Enquiry Issued to Bidders |  | blocked | 2027-02-01 | 2026-11-02 | 65 | 2 | 2
G-PRC-FAB | Procurement | MR-EL-004 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-21 | 2027-04-21 | 65 | 4 | 4
G-PRC-PO | Procurement | MR-PI-003 | Purchase Order Award |  | blocked | 2027-06-14 | 2027-03-15 | 65 | 3 | 3
G-CON-CWP | Construction | CWP-09-ME-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-11-01 | 2027-07-29 | 67 | 4 | 5
G-CON-CWP | Construction | CWP-10-ME-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-10-04 | 2027-07-01 | 67 | 4 | 5
G-PRC-PO | Procurement | MR-PI-005 | Purchase Order Award |  | blocked | 2027-08-30 | 2027-05-27 | 67 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 20BAA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-02-01 | 70 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 20BAC | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-02-01 | 70 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 20BAT | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-02-01 | 70 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 20BBT | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-02-01 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00GMA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00GNA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00GUA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00LDA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00PAA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00PAB | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 00PAC | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00PAH | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00PBA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00PGA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00QCA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00QEA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00QHA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00QJA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-17 | 70 | 4 | 4
G-COM-SC-WS | Commissioning / acceptance | 20MAG | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-19 | 70 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 20MAJ | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-19 | 70 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 20MAN | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-19 | 70 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 20MAV | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-19 | 70 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 20MAW | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-19 | 70 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 20MAX | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-19 | 70 | 3 | 3
G-CON-IWP | Construction | CWP-11-SS-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-09-27 | 2027-06-21 | 70 | 12 | 12
G-PRC-ENQ | Procurement | MR-IC-005 | Enquiry Issued to Bidders |  | blocked | 2027-03-15 | 2026-12-07 | 70 | 2 | 2
G-PRC-PO | Procurement | MR-EL-008 | Purchase Order Award |  | blocked | 2027-06-21 | 2027-03-15 | 70 | 3 | 3
G-CON-CWP | Construction | CWP-05-PI-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-09-20 | 2027-06-11 | 71 | 10 | 10
G-CON-IWP | Construction | CWP-07-SS-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-08-23 | 2027-05-14 | 71 | 4 | 4
G-CON-IWP | Construction | CWP-03-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-12-27 | 2027-09-15 | 73 | 31 | 31
G-CON-CWP | Construction | CWP-02-ME-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-12-20 | 2027-09-06 | 75 | 9 | 10
G-CON-CWP | Construction | CWP-04-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-01-04 | 2027-09-21 | 75 | 12 | 12
G-CON-CWP | Construction | CWP-07-SS-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-06-14 | 2027-03-01 | 75 | 4 | 4
G-PRC-ENQ | Procurement | MR-PI-005 | Enquiry Issued to Bidders |  | blocked | 2027-07-12 | 2027-03-29 | 75 | 2 | 2
G-CON-IWP | Construction | CWP-04-SS-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-08-09 | 2027-04-23 | 76 | 4 | 4
G-CON-CWP | Construction | CWP-04-SS-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-05-31 | 2027-02-11 | 77 | 4 | 4
G-CON-CWP | Construction | CWP-07-ME-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-12-27 | 2027-09-09 | 77 | 10 | 11
G-CON-CWP | Construction | CWP-11-IC-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-11-22 | 2027-08-05 | 77 | 21 | 21
G-PRC-ENQ | Procurement | MR-PI-003 | Enquiry Issued to Bidders |  | blocked | 2027-04-12 | 2026-12-24 | 77 | 2 | 2
G-PRC-PO | Procurement | MR-ME-006 | Purchase Order Award |  | blocked | 2027-07-05 | 2027-03-17 | 78 | 4 | 4
G-PRC-PO | Procurement | MR-IC-003 | Purchase Order Award |  | blocked | 2027-07-12 | 2027-03-23 | 79 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 00ACA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 00BBA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 00BFA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 00BFT | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 00BLA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 00BMA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 00BRA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 00BTA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 00BXA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 00XJA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-EL | Commissioning / acceptance | 10BAA | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 10BAC | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 10BAT | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 3 | 3
G-COM-SC-EL | Commissioning / acceptance | 10BBT | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | blocked | 2028-05-09 | 2028-01-18 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00CJA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00CJG | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00CKA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00CQA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00CYA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00EGA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00EGB | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 00EGC | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00EKA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00EKC | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 3 | 3
G-COM-SC-FF | Commissioning / acceptance | 00GBA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00GCA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00GHA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-FF | Commissioning / acceptance | 00GKA | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | blocked | 2028-07-24 | 2028-04-03 | 80 | 4 | 4
G-COM-SC-WS | Commissioning / acceptance | 00LBG | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 10HAN | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 4 | 4
G-COM-SC-WS | Commissioning / acceptance | 10LAB | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 10LAC | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 4 | 4
G-COM-SC-WS | Commissioning / acceptance | 10LAE | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 10LAF | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 10LBA | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 10LBB | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 10LBC | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 10LBD | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 20LCA | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 20LCB | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 4 | 4
G-COM-SC-WS | Commissioning / acceptance | 20MAA | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-COM-SC-WS | Commissioning / acceptance | 20MAB | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | blocked | 2028-09-25 | 2028-06-05 | 80 | 3 | 3
G-PRC-ENQ | Procurement | MR-EL-008 | Enquiry Issued to Bidders |  | blocked | 2027-05-03 | 2027-01-08 | 81 | 2 | 2
G-PRC-PO | Procurement | MR-IC-002 | Purchase Order Award |  | blocked | 2027-07-12 | 2027-03-19 | 81 | 4 | 4
G-PRC-PO | Procurement | MR-ME-013 | Purchase Order Award |  | blocked | 2027-05-17 | 2027-01-22 | 81 | 4 | 4
G-CON-CWP | Construction | CWP-03-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-10-25 | 2027-07-01 | 82 | 36 | 36
G-CON-CWP | Construction | CWP-05-ME-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-12-20 | 2027-08-26 | 82 | 10 | 11
G-CON-IWP | Construction | CWP-03-SS-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-09-06 | 2027-05-13 | 82 | 4 | 4
G-CON-CWP | Construction | CWP-08-SS-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-06-29 | 2027-03-03 | 84 | 3 | 3
G-CON-IWP | Construction | CWP-11-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-01-03 | 2027-09-07 | 84 | 6 | 6
G-CON-CWP | Construction | CWP-12-PI-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-07-12 | 2027-03-15 | 85 | 12 | 12
G-PRC-ENQ | Procurement | MR-EL-004 | Enquiry Issued to Bidders |  | blocked | 2027-03-22 | 2026-11-23 | 85 | 2 | 2
G-PRC-ENQ | Procurement | MR-EL-007 | Enquiry Issued to Bidders |  | blocked | 2027-03-22 | 2026-11-23 | 85 | 2 | 2
G-PRC-FAB | Procurement | MR-ME-006 | Manufacturing Release | certified supplier data accepted | blocked | 2027-09-27 | 2027-05-28 | 86 | 5 | 5
G-CON-IWP | Construction | CWP-12-CV-02 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-10-18 | 2027-06-17 | 87 | 10 | 10
G-PRC-FAB | Procurement | MR-IC-003 | Manufacturing Release | certified supplier data accepted | blocked | 2027-10-04 | 2027-06-03 | 87 | 5 | 5
G-PRC-FAB | Procurement | MR-ME-013 | Manufacturing Release | certified supplier data accepted | blocked | 2027-07-28 | 2027-03-29 | 87 | 6 | 6
G-PRC-PO | Procurement | MR-ME-014 | Purchase Order Award |  | blocked | 2027-05-31 | 2027-01-28 | 87 | 4 | 4
G-PRC-PO | Procurement | MR-ME-017 | Purchase Order Award |  | blocked | 2027-07-26 | 2027-03-25 | 87 | 3 | 3
G-PRC-PO | Procurement | MR-PI-007 | Purchase Order Award |  | blocked | 2027-08-02 | 2027-04-01 | 87 | 3 | 3
G-PRC-PO | Procurement | MR-IC-004 | Purchase Order Award |  | blocked | 2027-07-26 | 2027-03-24 | 88 | 3 | 3
G-PRC-ENQ | Procurement | MR-CV-003 | Enquiry Issued to Bidders |  | blocked | 2027-03-05 | 2026-11-02 | 89 | 2 | 2
G-CON-CWP | Construction | CWP-01-SS-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-07-12 | 2027-03-08 | 90 | 5 | 5
G-CON-CWP | Construction | CWP-09-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-08-04 | 2027-03-31 | 90 | 8 | 8
G-CON-CWP | Construction | CWP-01-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-01-10 | 2027-09-02 | 92 | 13 | 13
G-CON-CWP | Construction | CWP-03-HV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-10-11 | 2027-06-03 | 92 | 8 | 8
G-PRC-ENQ | Procurement | MR-ME-019 | Enquiry Issued to Bidders |  | blocked | 2027-03-15 | 2026-11-02 | 95 | 2 | 2
G-PRC-FAB | Procurement | MR-ME-014 | Manufacturing Release | certified supplier data accepted | blocked | 2027-08-23 | 2027-04-12 | 95 | 6 | 6
G-CON-CWP | Construction | CWP-01-HV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-11-01 | 2027-06-17 | 97 | 3 | 3
G-CON-IWP | Construction | CWP-11-IC-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-01-31 | 2027-09-16 | 97 | 17 | 17
G-CON-CWP | Construction | CWP-02-SS-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-07-12 | 2027-02-23 | 99 | 3 | 3
G-PRC-ENQ | Procurement | MR-ME-014 | Enquiry Issued to Bidders |  | blocked | 2027-03-22 | 2026-11-02 | 100 | 2 | 2
G-CON-IWP | Construction | CWP-11-HV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-12-27 | 2027-08-06 | 101 | 2 | 2
G-PRC-FAB | Procurement | MR-IC-002 | Manufacturing Release | certified supplier data accepted | blocked | 2027-10-04 | 2027-05-14 | 101 | 4 | 4
G-PRC-ENQ | Procurement | MR-ME-013 | Enquiry Issued to Bidders |  | blocked | 2027-03-29 | 2026-11-02 | 105 | 2 | 2
G-PRC-PO | Procurement | MR-PI-006 | Purchase Order Award |  | blocked | 2027-08-30 | 2027-04-05 | 105 | 3 | 3
G-CON-IWP | Construction | CWP-12-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-11-08 | 2027-06-10 | 107 | 8 | 8
G-CON-CWP | Construction | CWP-02-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-02-28 | 2027-09-27 | 110 | 6 | 6
G-CON-CWP | Construction | CWP-07-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-02-21 | 2027-09-17 | 111 | 4 | 4
G-CON-CWP | Construction | CWP-11-HV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-11-08 | 2027-06-03 | 112 | 3 | 3
G-CON-IWP | Construction | CWP-09-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-01-31 | 2027-08-25 | 113 | 4 | 4
G-CON-IWP | Construction | CWP-01-ME-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-02-14 | 2027-09-06 | 115 | 14 | 14
G-CON-IWP | Construction | CWP-10-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-03-06 | 2027-09-27 | 115 | 4 | 4
G-CON-IWP | Construction | CWP-05-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-03-20 | 2027-10-08 | 116 | 4 | 4
G-PRC-PO | Procurement | MR-EL-012 | Purchase Order Award |  | blocked | 2027-11-22 | 2027-06-09 | 118 | 3 | 3
G-CON-CWP | Construction | CWP-10-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-01-24 | 2027-08-09 | 120 | 4 | 4
G-PRC-ENQ | Procurement | MR-IC-004 | Enquiry Issued to Bidders |  | blocked | 2027-05-24 | 2026-12-07 | 120 | 2 | 2
G-CON-CWP | Construction | CWP-05-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-01-31 | 2027-08-13 | 121 | 4 | 4
G-PRC-ENQ | Procurement | MR-EL-012 | Enquiry Issued to Bidders |  | blocked | 2027-09-06 | 2027-03-19 | 121 | 2 | 2
G-CON-IWP | Construction | CWP-09-IC-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-02-28 | 2027-09-09 | 122 | 5 | 5
G-CON-IWP | Construction | CWP-08-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-03-20 | 2027-09-28 | 124 | 4 | 4
G-CON-IWP | Construction | CWP-08-ME-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-01-24 | 2027-08-03 | 124 | 17 | 17
G-PRC-ENQ | Procurement | MR-ME-006 | Enquiry Issued to Bidders |  | blocked | 2027-04-26 | 2026-11-02 | 125 | 2 | 2
G-PRC-ENQ | Procurement | MR-ME-017 | Enquiry Issued to Bidders |  | blocked | 2027-05-17 | 2026-11-23 | 125 | 2 | 2
G-CON-IWP | Construction | CWP-04-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-03-14 | 2027-09-16 | 128 | 11 | 11
G-PRC-PO | Procurement | MR-IC-010 | Purchase Order Award |  | blocked | 2027-11-29 | 2027-06-02 | 128 | 3 | 3
G-CON-IWP | Construction | CWP-07-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-04-17 | 2027-10-19 | 129 | 4 | 4
G-PRC-ENQ | Procurement | MR-IC-002 | Enquiry Issued to Bidders |  | blocked | 2027-05-03 | 2026-11-02 | 130 | 2 | 2
G-PRC-ENQ | Procurement | MR-IC-003 | Enquiry Issued to Bidders |  | blocked | 2027-05-03 | 2026-11-02 | 130 | 2 | 2
G-CON-IWP | Construction | CWP-01-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-04-10 | 2027-10-07 | 132 | 11 | 11
G-CON-CWP | Construction | CWP-01-PI-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-12-13 | 2027-06-09 | 133 | 19 | 19
G-CON-CWP | Construction | CWP-09-IC-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-01-24 | 2027-07-19 | 135 | 5 | 5
G-PRC-ENQ | Procurement | MR-PI-007 | Enquiry Issued to Bidders |  | blocked | 2027-06-14 | 2026-12-07 | 135 | 2 | 2
G-CON-IWP | Construction | CWP-02-EL-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-05-15 | 2027-11-04 | 137 | 4 | 4
G-CON-CWP | Construction | CWP-02-PI-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-01-31 | 2027-07-21 | 138 | 12 | 12
G-PRC-PO | Procurement | MR-ME-022 | Purchase Order Award |  | blocked | 2028-01-10 | 2027-06-30 | 138 | 3 | 3
G-CON-CWP | Construction | CWP-01-IC-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-02-07 | 2027-07-27 | 139 | 16 | 16
G-PRC-ENQ | Procurement | MR-IC-010 | Enquiry Issued to Bidders |  | blocked | 2027-10-25 | 2027-04-09 | 141 | 2 | 2
G-CON-IWP | Construction | CWP-08-IC-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-04-24 | 2027-10-04 | 145 | 6 | 6
G-PRC-ENQ | Procurement | MR-ME-022 | Enquiry Issued to Bidders |  | blocked | 2027-11-15 | 2027-04-23 | 146 | 2 | 2
G-CON-IWP | Construction | CWP-09-ME-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-12-13 | 2027-05-20 | 147 | 3 | 3
G-CON-IWP | Construction | CWP-10-IC-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-04-03 | 2027-09-08 | 148 | 4 | 4
G-CON-CWP | Construction | CWP-08-PI-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-12-13 | 2027-05-17 | 150 | 25 | 25
G-CON-CWP | Construction | CWP-10-IC-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-02-21 | 2027-07-23 | 151 | 4 | 4
G-CON-IWP | Construction | CWP-01-HV-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2027-12-27 | 2027-05-27 | 152 | 1 | 1
G-CON-CWP | Construction | CWP-06-CV-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-09-03 | 2027-02-02 | 153 | 11 | 12
G-CON-IWP | Construction | CWP-01-IC-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-05-01 | 2027-09-29 | 153 | 13 | 13
G-CON-IWP | Construction | CWP-05-IC-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-04-10 | 2027-09-08 | 153 | 5 | 5
G-PRC-ENQ | Procurement | MR-PI-006 | Enquiry Issued to Bidders |  | blocked | 2027-07-12 | 2026-12-07 | 155 | 2 | 2
G-CON-IWP | Construction | CWP-07-IC-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-05-08 | 2027-09-20 | 165 | 5 | 5
G-CON-CWP | Construction | CWP-09-PI-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-11-29 | 2027-04-05 | 170 | 5 | 5
G-CON-IWP | Construction | CWP-10-ME-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-01-10 | 2027-05-07 | 176 | 3 | 3
G-CON-IWP | Construction | CWP-05-ME-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-02-14 | 2027-06-08 | 179 | 7 | 7
G-CON-CWP | Construction | CWP-11-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-11-08 | 2027-03-01 | 180 | 6 | 6
G-CON-IWP | Construction | CWP-02-IC-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-06-12 | 2027-09-27 | 185 | 5 | 5
G-CON-CWP | Construction | CWP-08-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-01-10 | 2027-04-15 | 192 | 4 | 4
G-OPS-HO-FF | Operations | 10MBA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-07-24 | 192 | 2 | 2
G-OPS-HO-FF | Operations | 10MBL | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-07-24 | 192 | 2 | 2
G-OPS-HO-FF | Operations | 10MBN | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-07-24 | 192 | 2 | 2
G-OPS-HO-FF | Operations | 10MBP | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-07-24 | 192 | 2 | 2
G-OPS-HO-FF | Operations | 10MBU | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-07-24 | 192 | 2 | 2
G-OPS-HO-FF | Operations | 10MBV | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-07-24 | 192 | 2 | 2
G-CON-CWP | Construction | CWP-09-EL-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-12-27 | 2027-03-31 | 193 | 4 | 4
G-CON-CWP | Construction | CWP-10-PI-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2027-12-27 | 2027-03-31 | 193 | 7 | 7
G-OWN-TOC | Owner acceptance | 00000 | Tests on Completion Procedures Approved | 90 days before the tests | blocked | 2028-08-21 | 2027-11-24 | 193 | 6 | 6
G-CON-IWP | Construction | CWP-07-ME-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-03-06 | 2027-06-03 | 197 | 7 | 7
G-CON-IWP | Construction | CWP-02-ME-01 | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | blocked | 2028-04-03 | 2027-06-15 | 209 | 5 | 5
G-OPS-HO-WS | Operations | 20MAG | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-26 | 212 | 2 | 2
G-OPS-HO-WS | Operations | 20MAJ | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-26 | 212 | 2 | 2
G-OPS-HO-WS | Operations | 20MAN | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-26 | 212 | 2 | 2
G-OPS-HO-WS | Operations | 20MAV | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-26 | 212 | 2 | 2
G-OPS-HO-WS | Operations | 20MAW | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-26 | 212 | 2 | 2
G-OPS-HO-WS | Operations | 20MAX | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-26 | 212 | 2 | 2
G-CON-CWP | Construction | CWP-07-PI-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-01-24 | 2027-03-31 | 213 | 13 | 13
G-OPS-HO-WS | Operations | 00LBG | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 10HAN | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 3 | 3
G-OPS-HO-WS | Operations | 10LAB | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 10LAC | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 3 | 3
G-OPS-HO-WS | Operations | 10LAE | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 10LAF | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 10LBA | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 10LBB | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 10LBC | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 10LBD | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 20LCA | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 20LCB | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 3 | 3
G-OPS-HO-WS | Operations | 20MAA | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-OPS-HO-WS | Operations | 20MAB | Handover of the System to Operations | water-steam cycle systems | blocked | 2029-04-18 | 2028-06-12 | 222 | 2 | 2
G-CON-CWP | Construction | CWP-02-IC-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-03-27 | 2027-05-17 | 225 | 6 | 6
G-CON-CWP | Construction | CWP-08-IC-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-02-21 | 2027-03-25 | 237 | 6 | 6
G-OPS-HO-FF | Operations | 10MBY | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-22 | 237 | 2 | 2
G-OPS-HO-FF | Operations | 10MKA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-22 | 237 | 2 | 2
G-OPS-HO-FF | Operations | 10MKC | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-22 | 237 | 2 | 2
G-OPS-HO-FF | Operations | 10MKG | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-22 | 237 | 2 | 2
G-OPS-HO-FF | Operations | 20MAY | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-22 | 237 | 2 | 2
G-OPS-HO-FF | Operations | 20MKA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-22 | 237 | 2 | 2
G-OPS-HO-FF | Operations | 20MKC | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-22 | 237 | 2 | 2
G-OPS-HO-FF | Operations | 00CKA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-11 | 244 | 3 | 3
G-CON-CWP | Construction | CWP-05-IC-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-02-28 | 2027-03-22 | 245 | 5 | 5
G-OPS-HO-FF | Operations | 00QJB | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 3 | 3
G-OPS-HO-FF | Operations | 00QUA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 3 | 3
G-OPS-HO-FF | Operations | 00SAA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 3 | 3
G-OPS-HO-FF | Operations | 00SGA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 3 | 3
G-OPS-HO-FF | Operations | 00SGC | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 3 | 3
G-OPS-HO-FF | Operations | 00SGY | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 3 | 3
G-OPS-HO-FF | Operations | 00SMA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 2 | 2
G-OPS-HO-FF | Operations | 10HAA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 2 | 2
G-OPS-HO-FF | Operations | 10HNA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 2 | 2
G-OPS-HO-FF | Operations | 10HNE | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 1 | 1
G-OPS-HO-FF | Operations | 10HSA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 2 | 2
G-OPS-HO-FF | Operations | 10HSB | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-05-08 | 247 | 3 | 3
G-CON-CWP | Construction | CWP-07-IC-01 | CWP Release | documents of the first IWPs IFC, installation manuals issued | blocked | 2028-03-20 | 2027-03-25 | 257 | 5 | 5
G-OPS-HO-FF | Operations | 00GMA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00GNA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00GUA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00LDA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00PAA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00PAB | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 2 | 2
G-OPS-HO-FF | Operations | 00PAC | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00PAH | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00PBA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00PGA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00QCA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00QEA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00QHA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00QJA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-24 | 257 | 3 | 3
G-OPS-HO-FF | Operations | 00CJA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00CJG | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00CQA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00CYA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00EGA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00EGB | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 2 | 2
G-OPS-HO-FF | Operations | 00EGC | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00EKA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00EKC | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 2 | 2
G-OPS-HO-FF | Operations | 00GBA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00GCA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00GHA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-FF | Operations | 00GKA | Handover of the System to Operations | fuel, GT and auxiliary systems | blocked | 2029-04-18 | 2028-04-10 | 267 | 3 | 3
G-OPS-HO-EL | Operations | 00ACA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-03-07 | 291 | 3 | 3
G-OPS-HO-EL | Operations | 10BBT | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-02-17 | 304 | 3 | 3
G-OPS-HO-EL | Operations | 20BBT | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-02-17 | 304 | 3 | 3
G-OPS-HO-EL | Operations | 20BAA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-02-08 | 311 | 2 | 2
G-OPS-HO-EL | Operations | 20BAC | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-02-08 | 311 | 2 | 2
G-OPS-HO-EL | Operations | 20BAT | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-02-08 | 311 | 2 | 2
G-OPS-HO-EL | Operations | 00BBA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 3 | 3
G-OPS-HO-EL | Operations | 00BFA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 3 | 3
G-OPS-HO-EL | Operations | 00BFT | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 3 | 3
G-OPS-HO-EL | Operations | 00BLA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 2 | 2
G-OPS-HO-EL | Operations | 00BMA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 3 | 3
G-OPS-HO-EL | Operations | 00BRA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 3 | 3
G-OPS-HO-EL | Operations | 00BTA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 3 | 3
G-OPS-HO-EL | Operations | 00BXA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 2 | 2
G-OPS-HO-EL | Operations | 00XJA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 3 | 3
G-OPS-HO-EL | Operations | 10BAA | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 2 | 2
G-OPS-HO-EL | Operations | 10BAC | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 2 | 2
G-OPS-HO-EL | Operations | 10BAT | Handover of the System to Operations | electrical systems | blocked | 2029-04-18 | 2028-01-25 | 321 | 2 | 2
G-OPS-AB | Operations | 00000 | As-Built Documentation, 3D Model and Engineering Database | 3 months after Taking-Over | blocked | 2029-07-18 |  |  | 134 | 134

## Gate requirements
Alpilla 600 MW Combined Cycle Power Plant - Gate requirements per gate instance
engine release_control v1.2.0 ¦ generated 2026-09-29T02:52:27Z by SETUP ¦ data 6d73bc5813f68e2b ¦ planned dates from the levelled workflow network and the CPM (working days)
Gate | Scope | Requirement | Documents | Not met now | Planned (last) | Driving document | Need | Float wd
G-COM-MC-EL | 00ACA | construction? IFC | 2 | 2 | 2027-04-20 | ALP-E01-00ACA-EL-WIR-0001 | 2028-04-11 | 255
G-COM-MC-EL | 00ACA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00ACA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00BBA | construction? IFC | 2 | 2 | 2027-05-03 | ALP-EPC-00BBA-EL-WIR-0001 | 2028-04-11 | 246
G-COM-MC-EL | 00BBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BBA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00BFA | construction? IFC | 15 | 15 | 2027-07-26 | ALP-EPC-00BFA-EL-WIR-0013 | 2028-04-11 | 186
G-COM-MC-EL | 00BFA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BFA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00BFT | construction? IFC | 1 | 1 | 2027-04-26 | ALP-E04-00BFT-ME-GAD-0001 | 2028-04-11 | 251
G-COM-MC-EL | 00BFT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BFT-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00BLA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BLA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00BMA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BMA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00BRA | construction? IFC | 2 | 2 | 2027-06-01 | ALP-E07-00BRA-EL-WIR-0001 | 2028-04-11 | 225
G-COM-MC-EL | 00BRA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BRA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00BTA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BTA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00BXA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BXA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 00XJA | construction? IFC | 2 | 2 | 2027-05-07 | ALP-E06-00XJA-EL-WIR-0001 | 2028-04-11 | 242
G-COM-MC-EL | 00XJA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00XJA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 10BAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-10BAA-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 10BAC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-10BAC-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 10BAT | construction? IFC | 2 | 2 | 2027-03-08 | ALP-IEC-10BAT-EL-WIR-0001 | 2028-04-11 | 286
G-COM-MC-EL | 10BAT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-10BAT-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 10BBT | construction? IFC | 2 | 2 | 2027-06-24 | ALP-E02-10BBT-EL-WIR-0001 | 2028-04-11 | 208
G-COM-MC-EL | 10BBT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-10BBT-CM-MDB-0001 | 2028-04-11 | 60
G-COM-MC-EL | 20BAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-02-01 | ALP-EPC-20BAA-CM-MDB-0001 | 2028-04-11 | 50
G-COM-MC-EL | 20BAC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-02-01 | ALP-EPC-20BAC-CM-MDB-0001 | 2028-04-11 | 50
G-COM-MC-EL | 20BAT | construction? IFC | 1 | 1 | 2027-01-11 | ALP-IEC-10BAT-EL-GAD-0001 | 2028-04-11 | 326
G-COM-MC-EL | 20BAT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-02-01 | ALP-EPC-20BAT-CM-MDB-0001 | 2028-04-11 | 50
G-COM-MC-EL | 20BBT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-02-01 | ALP-EPC-20BBT-CM-MDB-0001 | 2028-04-11 | 50
G-COM-MC-FF | 00CJA | construction? IFC | 2 | 2 | 2027-05-27 | ALP-I01-00CJA-EL-WIR-0001 | 2028-06-26 | 282
G-COM-MC-FF | 00CJA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CJA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00CJG | construction? IFC | 2 | 2 | 2027-07-21 | ALP-I08-00CJG-EL-WIR-0001 | 2028-06-26 | 243
G-COM-MC-FF | 00CJG | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CJG-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00CKA | construction? IFC | 2 | 2 | 2027-09-16 | ALP-I09-00CKA-EL-WIR-0001 | 2028-06-26 | 202
G-COM-MC-FF | 00CKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CKA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00CQA | construction? IFC | 2 | 2 | 2027-06-23 | ALP-I02-00CQA-EL-WIR-0001 | 2028-06-26 | 263
G-COM-MC-FF | 00CQA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CQA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00CYA | construction? IFC | 2 | 2 | 2027-07-26 | ALP-I07-00CYA-EL-WIR-0001 | 2028-06-26 | 240
G-COM-MC-FF | 00CYA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CYA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00EGA | construction? IFC | 4 | 4 | 2028-01-21 | ALP-EPC-00EGA-PI-SUP-0001 | 2028-06-26 | 111
G-COM-MC-FF | 00EGA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EGA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00EGB | construction? IFC | 2 | 2 | 2028-01-24 | ALP-EPC-00EGB-PI-SUP-0001 | 2028-06-26 | 110
G-COM-MC-FF | 00EGB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EGB-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00EGC | construction? IFC | 2 | 2 | 2028-01-26 | ALP-EPC-00EGC-PI-SUP-0001 | 2028-06-26 | 108
G-COM-MC-FF | 00EGC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EGC-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00EKA | construction? IFC | 4 | 4 | 2027-12-01 | ALP-EPC-00EKA-PI-SUP-0001 | 2028-06-26 | 148
G-COM-MC-FF | 00EKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EKA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00EKC | construction? IFC | 2 | 2 | 2027-12-10 | ALP-EPC-00EKC-PI-SUP-0001 | 2028-06-26 | 141
G-COM-MC-FF | 00EKC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EKC-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00GBA | construction? IFC | 4 | 4 | 2028-02-21 | ALP-EPC-00GBA-PI-SUP-0001 | 2028-06-26 | 90
G-COM-MC-FF | 00GBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00GBA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00GCA | construction? IFC | 2 | 2 | 2028-02-25 | ALP-EPC-00GCA-PI-SUP-0001 | 2028-06-26 | 86
G-COM-MC-FF | 00GCA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00GCA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00GHA | construction? IFC | 4 | 4 | 2028-03-09 | ALP-EPC-00GHA-PI-SUP-0001 | 2028-06-26 | 77
G-COM-MC-FF | 00GHA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00GHA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00GKA | construction? IFC | 3 | 3 | 2027-09-30 | ALP-EPC-00GKA-PI-SUP-0001 | 2028-06-26 | 192
G-COM-MC-FF | 00GKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00GKA-CM-MDB-0001 | 2028-06-26 | 60
G-COM-MC-FF | 00GMA | construction? IFC | 3 | 3 | 2027-09-21 | ALP-EPC-00GMA-PI-SUP-0001 | 2028-06-26 | 199
G-COM-MC-FF | 00GMA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00GMA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00GNA | construction? IFC | 4 | 4 | 2028-03-01 | ALP-EPC-00GNA-PI-SUP-0001 | 2028-06-26 | 83
G-COM-MC-FF | 00GNA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00GNA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00GUA | construction? IFC | 2 | 2 | 2028-03-10 | ALP-EPC-00GUA-PI-SUP-0001 | 2028-06-26 | 76
G-COM-MC-FF | 00GUA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00GUA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00LDA | construction? IFC | 2 | 2 | 2028-03-03 | ALP-EPC-00LDA-PI-SUP-0001 | 2028-06-26 | 81
G-COM-MC-FF | 00LDA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00LDA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00PAA | construction? IFC | 4 | 4 | 2027-09-29 | ALP-EPC-00PAA-PI-SUP-0001 | 2028-06-26 | 193
G-COM-MC-FF | 00PAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PAA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00PAB | construction? IFC | 3 | 3 | 2027-10-06 | ALP-EPC-00PAB-PI-SUP-0001 | 2028-06-26 | 188
G-COM-MC-FF | 00PAB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PAB-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00PAC | construction? IFC | 4 | 4 | 2027-09-29 | ALP-EPC-00PAC-PI-SUP-0001 | 2028-06-26 | 193
G-COM-MC-FF | 00PAC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PAC-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00PAH | construction? IFC | 4 | 4 | 2028-03-20 | ALP-EPC-00PAH-PI-SUP-0001 | 2028-06-26 | 70
G-COM-MC-FF | 00PAH | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PAH-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00PBA | construction? IFC | 4 | 4 | 2027-10-08 | ALP-EPC-00PBA-PI-SUP-0001 | 2028-06-26 | 186
G-COM-MC-FF | 00PBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PBA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00PGA | construction? IFC | 4 | 4 | 2028-01-27 | ALP-EPC-00PGA-PI-SUP-0001 | 2028-06-26 | 107
G-COM-MC-FF | 00PGA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PGA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00QCA | construction? IFC | 4 | 4 | 2028-01-21 | ALP-EPC-00QCA-PI-SUP-0001 | 2028-06-26 | 111
G-COM-MC-FF | 00QCA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00QCA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00QEA | construction? IFC | 4 | 4 | 2028-01-27 | ALP-EPC-00QEA-PI-SUP-0001 | 2028-06-26 | 107
G-COM-MC-FF | 00QEA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00QEA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00QHA | construction? IFC | 4 | 4 | 2028-01-26 | ALP-EPC-00QHA-PI-SUP-0001 | 2028-06-26 | 108
G-COM-MC-FF | 00QHA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00QHA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00QJA | construction? IFC | 4 | 4 | 2028-01-21 | ALP-EPC-00QJA-PI-SUP-0001 | 2028-06-26 | 111
G-COM-MC-FF | 00QJA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00QJA-CM-MDB-0001 | 2028-06-26 | 50
G-COM-MC-FF | 00QJB | construction? IFC | 2 | 2 | 2028-02-28 | ALP-EPC-00QJB-PI-SUP-0001 | 2028-06-26 | 85
G-COM-MC-FF | 00QJB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00QJB-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 00QUA | construction? IFC | 4 | 4 | 2028-02-14 | ALP-EPC-00QUA-PI-SUP-0001 | 2028-06-26 | 95
G-COM-MC-FF | 00QUA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00QUA-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 00SAA | construction? IFC | 5 | 5 | 2027-10-22 | ALP-EPC-00SAA-PI-SUP-0001 | 2028-06-26 | 176
G-COM-MC-FF | 00SAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SAA-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 00SGA | construction? IFC | 5 | 5 | 2028-01-27 | ALP-EPC-00SGA-PI-SUP-0001 | 2028-06-26 | 107
G-COM-MC-FF | 00SGA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SGA-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 00SGC | construction? IFC | 2 | 2 | 2028-01-27 | ALP-EPC-00SGC-PI-SUP-0001 | 2028-06-26 | 107
G-COM-MC-FF | 00SGC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SGC-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 00SGY | construction? IFC | 2 | 2 | 2027-08-02 | ALP-I06-00SGY-EL-WIR-0001 | 2028-06-26 | 235
G-COM-MC-FF | 00SGY | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SGY-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 00SMA | construction? IFC | 2 | 2 | 2027-05-07 | ALP-M21-00SMA-EL-WIR-0001 | 2028-06-26 | 296
G-COM-MC-FF | 00SMA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SMA-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 10HAA | construction? IFC | 2 | 2 | 2027-03-08 | ALP-IEC-10HAA-EL-WIR-0001 | 2028-06-26 | 340
G-COM-MC-FF | 10HAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HAA-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 10HNA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HNA-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 10HNE | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HNE-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 10HSA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HSA-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 10HSB | construction? IFC | 4 | 4 | 2028-01-21 | ALP-EPC-10HSB-PI-SUP-0001 | 2028-06-26 | 111
G-COM-MC-FF | 10HSB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HSB-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 10MBA | construction? IFC | 4 | 4 | 2027-03-08 | ALP-IEC-10MBA-EL-WIR-0002 | 2028-06-26 | 340
G-COM-MC-FF | 10MBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10MBA-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 10MBL | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10MBL-CM-MDB-0001 | 2028-06-26 | 40
G-COM-MC-FF | 10MBN | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBN-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 10MBP | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBP-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 10MBU | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBU-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 10MBV | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBV-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 10MBY | construction? IFC | 3 | 3 | 2027-07-26 | ALP-IEC-10MBY-IC-CBL-0001 | 2028-06-26 | 240
G-COM-MC-FF | 10MBY | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBY-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 10MKA | construction? IFC | 3 | 3 | 2027-03-08 | ALP-IEC-10MKA-EL-WIR-0001 | 2028-06-26 | 340
G-COM-MC-FF | 10MKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MKA-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 10MKC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MKC-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 10MKG | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MKG-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 20MAY | construction? IFC | 1 | 1 | 2027-07-26 | ALP-IEC-10MBY-IC-CBL-0001 | 2028-06-26 | 240
G-COM-MC-FF | 20MAY | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-20MAY-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 20MKA | construction? IFC | 1 | 1 | 2027-01-11 | ALP-IEC-20MAA-ME-GAD-0001 | 2028-06-26 | 380
G-COM-MC-FF | 20MKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-20MKA-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-FF | 20MKC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-20MKC-CM-MDB-0001 | 2028-06-26 | 30
G-COM-MC-WS | 00LBG | construction? IFC | 2 | 2 | 2028-01-26 | ALP-EPC-00LBG-PI-SUP-0001 | 2028-08-28 | 153
G-COM-MC-WS | 00LBG | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-00LBG-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10HAN | construction? IFC | 4 | 4 | 2028-02-02 | ALP-EPC-10HAN-PI-SUP-0001 | 2028-08-28 | 148
G-COM-MC-WS | 10HAN | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10HAN-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10LAB | construction? IFC | 2 | 2 | 2028-01-27 | ALP-EPC-10LAB-PI-SUP-0001 | 2028-08-28 | 152
G-COM-MC-WS | 10LAB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LAB-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10LAC | construction? IFC | 4 | 4 | 2028-01-25 | ALP-EPC-10LAC-PI-SUP-0001 | 2028-08-28 | 154
G-COM-MC-WS | 10LAC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LAC-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10LAE | construction? IFC | 2 | 2 | 2028-03-01 | ALP-EPC-10LAE-PI-SUP-0001 | 2028-08-28 | 128
G-COM-MC-WS | 10LAE | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LAE-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10LAF | construction? IFC | 2 | 2 | 2028-03-01 | ALP-EPC-10LAF-PI-SUP-0001 | 2028-08-28 | 128
G-COM-MC-WS | 10LAF | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LAF-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10LBA | construction? IFC | 2 | 2 | 2028-02-03 | ALP-EPC-10LBA-PI-SUP-0001 | 2028-08-28 | 147
G-COM-MC-WS | 10LBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LBA-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10LBB | construction? IFC | 2 | 2 | 2028-02-09 | ALP-EPC-10LBB-PI-SUP-0001 | 2028-08-28 | 143
G-COM-MC-WS | 10LBB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LBB-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10LBC | construction? IFC | 2 | 2 | 2028-02-08 | ALP-EPC-10LBC-PI-SUP-0001 | 2028-08-28 | 144
G-COM-MC-WS | 10LBC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LBC-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 10LBD | construction? IFC | 2 | 2 | 2028-02-18 | ALP-EPC-10LBD-PI-SUP-0001 | 2028-08-28 | 136
G-COM-MC-WS | 10LBD | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LBD-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 20LCA | construction? IFC | 2 | 2 | 2028-04-27 | ALP-EPC-20LCA-PI-SUP-0001 | 2028-08-28 | 87
G-COM-MC-WS | 20LCA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-20LCA-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 20LCB | construction? IFC | 4 | 4 | 2028-04-14 | ALP-EPC-20LCB-PI-SUP-0001 | 2028-08-28 | 96
G-COM-MC-WS | 20LCB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-20LCB-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 20MAA | construction? IFC | 2 | 2 | 2027-03-08 | ALP-IEC-20MAA-EL-WIR-0001 | 2028-08-28 | 385
G-COM-MC-WS | 20MAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-20MAA-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 20MAB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-20MAB-CM-MDB-0001 | 2028-08-28 | 60
G-COM-MC-WS | 20MAG | construction? IFC | 1 | 1 | 2027-01-11 | ALP-IEC-20MAA-ME-GAD-0001 | 2028-08-28 | 425
G-COM-MC-WS | 20MAG | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAG-CM-MDB-0001 | 2028-08-28 | 50
G-COM-MC-WS | 20MAJ | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAJ-CM-MDB-0001 | 2028-08-28 | 50
G-COM-MC-WS | 20MAN | construction? IFC | 2 | 2 | 2028-04-21 | ALP-EPC-20MAN-PI-SUP-0001 | 2028-08-28 | 91
G-COM-MC-WS | 20MAN | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAN-CM-MDB-0001 | 2028-08-28 | 50
G-COM-MC-WS | 20MAV | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAV-CM-MDB-0001 | 2028-08-28 | 50
G-COM-MC-WS | 20MAW | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAW-CM-MDB-0001 | 2028-08-28 | 50
G-COM-MC-WS | 20MAX | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAX-CM-MDB-0001 | 2028-08-28 | 50
G-COM-SC-EL | 00ACA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-01-25 | ALP-EPC-00ACA-CM-CMP-0001 | 2028-05-09 | 336
G-COM-SC-EL | 00ACA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-10-19 | ALP-E01-00ACA-ME-OMM-0001 | 2028-05-09 | 145
G-COM-SC-EL | 00ACA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00ACA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00BBA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-01-25 | ALP-EPC-00BBA-CM-CMP-0001 | 2028-05-09 | 336
G-COM-SC-EL | 00BBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-29 | ALP-E03-00BBA-ME-OMM-0001 | 2028-05-09 | 203
G-COM-SC-EL | 00BBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BBA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00BFA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-01-25 | ALP-EPC-00BFA-CM-CMP-0001 | 2028-05-09 | 336
G-COM-SC-EL | 00BFA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-08 | ALP-E05-00BFA-ME-OMM-0001 | 2028-05-09 | 218
G-COM-SC-EL | 00BFA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BFA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00BFT | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-01-25 | ALP-EPC-00BFT-CM-CMP-0001 | 2028-05-09 | 336
G-COM-SC-EL | 00BFT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-06 | ALP-E04-00BFT-ME-OMM-0001 | 2028-05-09 | 220
G-COM-SC-EL | 00BFT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BFT-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00BLA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-01-25 | ALP-EPC-00BLA-CM-CMP-0001 | 2028-05-09 | 336
G-COM-SC-EL | 00BLA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-02-09 | ALP-EPC-00BLA-CM-OMM-0001 | 2028-05-09 | 325
G-COM-SC-EL | 00BLA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BLA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00BMA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-01-25 | ALP-EPC-00BMA-CM-CMP-0001 | 2028-05-09 | 336
G-COM-SC-EL | 00BMA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-08 | ALP-E05-00BFA-ME-OMM-0001 | 2028-05-09 | 218
G-COM-SC-EL | 00BMA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BMA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00BRA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-02-04 | ALP-EPC-00BRA-CM-CMP-0001 | 2028-05-09 | 328
G-COM-SC-EL | 00BRA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-14 | ALP-E07-00BRA-ME-OMM-0001 | 2028-05-09 | 214
G-COM-SC-EL | 00BRA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BRA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00BTA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-02-16 | ALP-EPC-00BTA-CM-CMP-0001 | 2028-05-09 | 320
G-COM-SC-EL | 00BTA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-14 | ALP-E07-00BRA-ME-OMM-0001 | 2028-05-09 | 214
G-COM-SC-EL | 00BTA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BTA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00BXA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-02-22 | ALP-EPC-00BXA-CM-CMP-0001 | 2028-05-09 | 316
G-COM-SC-EL | 00BXA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-07-06 | ALP-E10-00BXA-ME-OMM-0001 | 2028-05-09 | 220
G-COM-SC-EL | 00BXA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00BXA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 00XJA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-02-22 | ALP-EPC-00XJA-CM-CMP-0001 | 2028-05-09 | 316
G-COM-SC-EL | 00XJA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-29 | ALP-E06-00XJA-ME-OMM-0001 | 2028-05-09 | 203
G-COM-SC-EL | 00XJA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-00XJA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 10BAA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-05-09 | 231
G-COM-SC-EL | 10BAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-05-09 | 191
G-COM-SC-EL | 10BAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-10BAA-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 10BAC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-05-09 | 231
G-COM-SC-EL | 10BAC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-05-09 | 191
G-COM-SC-EL | 10BAC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-10BAC-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 10BAT | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-IEC-10BAT-CM-CMP-0001 | 2028-05-09 | 226
G-COM-SC-EL | 10BAT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-23 | ALP-IEC-10BAT-ME-OMM-0001 | 2028-05-09 | 186
G-COM-SC-EL | 10BAT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-10BAT-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 10BBT | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-02-22 | ALP-EPC-10BBT-CM-CMP-0001 | 2028-05-09 | 316
G-COM-SC-EL | 10BBT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-09-30 | ALP-E02-10BBT-ME-OMM-0001 | 2028-05-09 | 158
G-COM-SC-EL | 10BBT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-01-18 | ALP-EPC-10BBT-CM-MDB-0001 | 2028-05-09 | 80
G-COM-SC-EL | 20BAA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-05-09 | 231
G-COM-SC-EL | 20BAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-05-09 | 191
G-COM-SC-EL | 20BAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-02-01 | ALP-EPC-20BAA-CM-MDB-0001 | 2028-05-09 | 70
G-COM-SC-EL | 20BAC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-05-09 | 231
G-COM-SC-EL | 20BAC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-05-09 | 191
G-COM-SC-EL | 20BAC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-02-01 | ALP-EPC-20BAC-CM-MDB-0001 | 2028-05-09 | 70
G-COM-SC-EL | 20BAT | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-IEC-10BAT-CM-CMP-0001 | 2028-05-09 | 226
G-COM-SC-EL | 20BAT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-23 | ALP-IEC-10BAT-ME-OMM-0001 | 2028-05-09 | 186
G-COM-SC-EL | 20BAT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-02-01 | ALP-EPC-20BAT-CM-MDB-0001 | 2028-05-09 | 70
G-COM-SC-EL | 20BBT | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-02-22 | ALP-EPC-20BBT-CM-CMP-0001 | 2028-05-09 | 316
G-COM-SC-EL | 20BBT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-09-30 | ALP-E02-10BBT-ME-OMM-0001 | 2028-05-09 | 158
G-COM-SC-EL | 20BBT | rule:DL-CM-TOD IFR | 1 | 1 | 2028-02-01 | ALP-EPC-20BBT-CM-MDB-0001 | 2028-05-09 | 70
G-COM-SC-FF | 00CJA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-03-05 | ALP-EPC-00CJA-CM-CMP-0001 | 2028-07-24 | 361
G-COM-SC-FF | 00CJA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-09-02 | ALP-I01-00CJA-ME-OMM-0001 | 2028-07-24 | 232
G-COM-SC-FF | 00CJA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CJA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00CJG | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-03-16 | ALP-EPC-00CJG-CM-CMP-0001 | 2028-07-24 | 354
G-COM-SC-FF | 00CJG | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-09-02 | ALP-I08-00CJG-ME-OMM-0001 | 2028-07-24 | 232
G-COM-SC-FF | 00CJG | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CJG-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00CKA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-03-22 | ALP-EPC-00CKA-CM-CMP-0001 | 2028-07-24 | 350
G-COM-SC-FF | 00CKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-12-23 | ALP-I09-00CKA-ME-OMM-0001 | 2028-07-24 | 152
G-COM-SC-FF | 00CKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CKA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00CQA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-03-22 | ALP-EPC-00CQA-CM-CMP-0001 | 2028-07-24 | 350
G-COM-SC-FF | 00CQA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-20 | ALP-I02-00CQA-ME-OMM-0001 | 2028-07-24 | 241
G-COM-SC-FF | 00CQA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CQA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00CYA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-03-22 | ALP-EPC-00CYA-CM-CMP-0001 | 2028-07-24 | 350
G-COM-SC-FF | 00CYA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-16 | ALP-I07-00CYA-ME-OMM-0001 | 2028-07-24 | 245
G-COM-SC-FF | 00CYA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00CYA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00EGA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-10 | ALP-EPC-00EGA-CM-CMP-0001 | 2028-07-24 | 292
G-COM-SC-FF | 00EGA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-29 | ALP-M16-00EGA-ME-OMM-0001 | 2028-07-24 | 257
G-COM-SC-FF | 00EGA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EGA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00EGB | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-22 | ALP-EPC-00EGB-CM-CMP-0001 | 2028-07-24 | 284
G-COM-SC-FF | 00EGB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-07-06 | ALP-EPC-00EGB-CM-OMM-0001 | 2028-07-24 | 274
G-COM-SC-FF | 00EGB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EGB-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00EGC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-EPC-00EGC-CM-CMP-0001 | 2028-07-24 | 332
G-COM-SC-FF | 00EGC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-29 | ALP-M16-00EGA-ME-OMM-0001 | 2028-07-24 | 257
G-COM-SC-FF | 00EGC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EGC-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00EKA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-13 | ALP-EPC-00EKA-CM-CMP-0001 | 2028-07-24 | 334
G-COM-SC-FF | 00EKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-26 | ALP-M15-00EKA-ME-OMM-0001 | 2028-07-24 | 237
G-COM-SC-FF | 00EKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EKA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00EKC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-25 | ALP-EPC-00EKC-CM-CMP-0001 | 2028-07-24 | 281
G-COM-SC-FF | 00EKC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-07-09 | ALP-EPC-00EKC-CM-OMM-0001 | 2028-07-24 | 271
G-COM-SC-FF | 00EKC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00EKC-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00GBA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-05-18 | ALP-EPC-00GBA-CM-CMP-0001 | 2028-07-24 | 309
G-COM-SC-FF | 00GBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-10-07 | ALP-M12-00GBA-ME-OMM-0001 | 2028-07-24 | 207
G-COM-SC-FF | 00GBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00GBA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00GCA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-25 | ALP-EPC-00GCA-CM-CMP-0001 | 2028-07-24 | 281
G-COM-SC-FF | 00GCA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-10-07 | ALP-M12-00GBA-ME-OMM-0001 | 2028-07-24 | 207
G-COM-SC-FF | 00GCA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00GCA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00GHA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-EPC-00GHA-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 00GHA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-12 | ALP-EPC-00GHA-CM-OMM-0001 | 2028-07-24 | 270
G-COM-SC-FF | 00GHA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00GHA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00GKA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-02 | ALP-EPC-00GKA-CM-CMP-0001 | 2028-07-24 | 255
G-COM-SC-FF | 00GKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-16 | ALP-EPC-00GKA-CM-OMM-0001 | 2028-07-24 | 245
G-COM-SC-FF | 00GKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-03 | ALP-EPC-00GKA-CM-MDB-0001 | 2028-07-24 | 80
G-COM-SC-FF | 00GMA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-05-20 | ALP-EPC-00GMA-CM-CMP-0001 | 2028-07-24 | 307
G-COM-SC-FF | 00GMA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-01 | ALP-M14-00GNA-ME-OMM-0001 | 2028-07-24 | 277
G-COM-SC-FF | 00GMA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00GMA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00GNA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-05-21 | ALP-EPC-00GNA-CM-CMP-0001 | 2028-07-24 | 306
G-COM-SC-FF | 00GNA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-01 | ALP-M14-00GNA-ME-OMM-0001 | 2028-07-24 | 277
G-COM-SC-FF | 00GNA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00GNA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00GUA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-02 | ALP-EPC-00GUA-CM-CMP-0001 | 2028-07-24 | 255
G-COM-SC-FF | 00GUA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-16 | ALP-EPC-00GUA-CM-OMM-0001 | 2028-07-24 | 245
G-COM-SC-FF | 00GUA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00GUA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00LDA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-EPC-00LDA-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 00LDA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-10-07 | ALP-M12-00GBA-ME-OMM-0001 | 2028-07-24 | 207
G-COM-SC-FF | 00LDA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00LDA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00PAA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-05-21 | ALP-EPC-00PAA-CM-CMP-0001 | 2028-07-24 | 306
G-COM-SC-FF | 00PAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-27 | ALP-M04-00PAA-ME-OMM-0001 | 2028-07-24 | 236
G-COM-SC-FF | 00PAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PAA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00PAB | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-EPC-00PAB-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 00PAB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-07-12 | ALP-EPC-00PAB-CM-OMM-0001 | 2028-07-24 | 270
G-COM-SC-FF | 00PAB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PAB-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00PAC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-EPC-00PAC-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 00PAC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-09-23 | ALP-M03-00PAC-ME-OMM-0001 | 2028-07-24 | 217
G-COM-SC-FF | 00PAC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PAC-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00PAH | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-29 | ALP-EPC-00PAH-CM-CMP-0001 | 2028-07-24 | 279
G-COM-SC-FF | 00PAH | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-18 | ALP-M06-00PAH-ME-OMM-0001 | 2028-07-24 | 243
G-COM-SC-FF | 00PAH | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PAH-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00PBA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-05-21 | ALP-EPC-00PBA-CM-CMP-0001 | 2028-07-24 | 306
G-COM-SC-FF | 00PBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-30 | ALP-M05-00PBA-ME-OMM-0001 | 2028-07-24 | 235
G-COM-SC-FF | 00PBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PBA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00PGA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-05-03 | ALP-EPC-00PGA-CM-CMP-0001 | 2028-07-24 | 320
G-COM-SC-FF | 00PGA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-22 | ALP-M07-00PGA-ME-OMM-0001 | 2028-07-24 | 262
G-COM-SC-FF | 00PGA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00PGA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00QCA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-05-21 | ALP-EPC-00QCA-CM-CMP-0001 | 2028-07-24 | 306
G-COM-SC-FF | 00QCA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-09-15 | ALP-M11-00QCA-ME-OMM-0001 | 2028-07-24 | 223
G-COM-SC-FF | 00QCA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00QCA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00QEA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-05-24 | ALP-EPC-00QEA-CM-CMP-0001 | 2028-07-24 | 305
G-COM-SC-FF | 00QEA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-29 | ALP-EPC-00QEA-CM-OMM-0001 | 2028-07-24 | 257
G-COM-SC-FF | 00QEA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00QEA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00QHA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-10 | ALP-EPC-00QHA-CM-CMP-0001 | 2028-07-24 | 292
G-COM-SC-FF | 00QHA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-26 | ALP-M09-00QHA-ME-OMM-0001 | 2028-07-24 | 237
G-COM-SC-FF | 00QHA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00QHA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00QJA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-07-14 | ALP-EPC-00QJA-CM-CMP-0001 | 2028-07-24 | 268
G-COM-SC-FF | 00QJA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-10 | ALP-M10-00QJA-ME-OMM-0001 | 2028-07-24 | 249
G-COM-SC-FF | 00QJA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-04-17 | ALP-EPC-00QJA-CM-MDB-0001 | 2028-07-24 | 70
G-COM-SC-FF | 00QJB | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-07-16 | ALP-EPC-00QJB-CM-CMP-0001 | 2028-07-24 | 266
G-COM-SC-FF | 00QJB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-10 | ALP-M10-00QJA-ME-OMM-0001 | 2028-07-24 | 249
G-COM-SC-FF | 00QJB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00QJB-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 00QUA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-07-23 | ALP-EPC-00QUA-CM-CMP-0001 | 2028-07-24 | 261
G-COM-SC-FF | 00QUA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-24 | ALP-I03-00QUA-ME-OMM-0001 | 2028-07-24 | 239
G-COM-SC-FF | 00QUA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00QUA-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 00SAA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-21 | ALP-EPC-00SAA-CM-CMP-0001 | 2028-07-24 | 328
G-COM-SC-FF | 00SAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-15 | ALP-EPC-00SAA-CM-OMM-0001 | 2028-07-24 | 267
G-COM-SC-FF | 00SAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SAA-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 00SGA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-14 | ALP-EPC-00SGA-CM-CMP-0001 | 2028-07-24 | 333
G-COM-SC-FF | 00SGA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-19 | ALP-EPC-00SGA-CM-OMM-0001 | 2028-07-24 | 265
G-COM-SC-FF | 00SGA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SGA-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 00SGC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-14 | ALP-EPC-00SGC-CM-CMP-0001 | 2028-07-24 | 333
G-COM-SC-FF | 00SGC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-07-28 | ALP-EPC-00SGC-CM-OMM-0001 | 2028-07-24 | 258
G-COM-SC-FF | 00SGC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SGC-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 00SGY | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-02 | ALP-EPC-00SGY-CM-CMP-0001 | 2028-07-24 | 341
G-COM-SC-FF | 00SGY | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-23 | ALP-I06-00SGY-ME-OMM-0001 | 2028-07-24 | 240
G-COM-SC-FF | 00SGY | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SGY-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 00SMA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-05 | ALP-EPC-00SMA-CM-CMP-0001 | 2028-07-24 | 340
G-COM-SC-FF | 00SMA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-07-29 | ALP-M21-00SMA-ME-OMM-0001 | 2028-07-24 | 257
G-COM-SC-FF | 00SMA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-00SMA-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 10HAA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-14 | ALP-IEC-10HAA-CM-CMP-0001 | 2028-07-24 | 290
G-COM-SC-FF | 10HAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-09 | ALP-IEC-10HAA-ME-OMM-0001 | 2028-07-24 | 250
G-COM-SC-FF | 10HAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HAA-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 10HNA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-14 | ALP-IEC-10HAA-CM-CMP-0001 | 2028-07-24 | 290
G-COM-SC-FF | 10HNA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-09 | ALP-IEC-10HAA-ME-OMM-0001 | 2028-07-24 | 250
G-COM-SC-FF | 10HNA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HNA-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 10HNE | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-08 | ALP-EPC-10HNE-CM-CMP-0001 | 2028-07-24 | 337
G-COM-SC-FF | 10HNE | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HNE-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 10HSA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-14 | ALP-IEC-10HAA-CM-CMP-0001 | 2028-07-24 | 290
G-COM-SC-FF | 10HSA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-09 | ALP-IEC-10HAA-ME-OMM-0001 | 2028-07-24 | 250
G-COM-SC-FF | 10HSA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HSA-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 10HSB | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-02 | ALP-EPC-10HSB-CM-CMP-0001 | 2028-07-24 | 255
G-COM-SC-FF | 10HSB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-08-17 | ALP-EPC-10HSB-CM-OMM-0001 | 2028-07-24 | 244
G-COM-SC-FF | 10HSB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10HSB-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 10MBA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-IEC-10MBA-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 10MBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2028-03-06 | ALP-IEC-10MBA-ME-OMM-0001 | 2028-07-24 | 100
G-COM-SC-FF | 10MBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10MBA-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 10MBL | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-IEC-10MBA-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 10MBL | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2028-03-06 | ALP-IEC-10MBA-ME-OMM-0001 | 2028-07-24 | 100
G-COM-SC-FF | 10MBL | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-01 | ALP-EPC-10MBL-CM-MDB-0001 | 2028-07-24 | 60
G-COM-SC-FF | 10MBN | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-IEC-10MBA-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 10MBN | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2028-03-06 | ALP-IEC-10MBA-ME-OMM-0001 | 2028-07-24 | 100
G-COM-SC-FF | 10MBN | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBN-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 10MBP | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-IEC-10MBA-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 10MBP | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2028-03-06 | ALP-IEC-10MBA-ME-OMM-0001 | 2028-07-24 | 100
G-COM-SC-FF | 10MBP | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBP-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 10MBU | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-IEC-10MBA-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 10MBU | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2028-03-06 | ALP-IEC-10MBA-ME-OMM-0001 | 2028-07-24 | 100
G-COM-SC-FF | 10MBU | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBU-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 10MBV | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-IEC-10MBA-CM-CMP-0001 | 2028-07-24 | 280
G-COM-SC-FF | 10MBV | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2028-03-06 | ALP-IEC-10MBA-ME-OMM-0001 | 2028-07-24 | 100
G-COM-SC-FF | 10MBV | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBV-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 10MBY | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-19 | ALP-IEC-10MBY-CM-CMP-0001 | 2028-07-24 | 330
G-COM-SC-FF | 10MBY | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-06-14 | ALP-IEC-10MBY-ME-OMM-0001 | 2028-07-24 | 290
G-COM-SC-FF | 10MBY | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MBY-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 10MKA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-07-24 | 285
G-COM-SC-FF | 10MKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-07-24 | 245
G-COM-SC-FF | 10MKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MKA-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 10MKC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-07-24 | 285
G-COM-SC-FF | 10MKC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-07-24 | 245
G-COM-SC-FF | 10MKC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MKC-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 10MKG | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-07-24 | 285
G-COM-SC-FF | 10MKG | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-07-24 | 245
G-COM-SC-FF | 10MKG | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-10MKG-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 20MAY | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-04-19 | ALP-IEC-10MBY-CM-CMP-0001 | 2028-07-24 | 330
G-COM-SC-FF | 20MAY | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-06-14 | ALP-IEC-10MBY-ME-OMM-0001 | 2028-07-24 | 290
G-COM-SC-FF | 20MAY | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-20MAY-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 20MKA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-07-24 | 285
G-COM-SC-FF | 20MKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-07-24 | 245
G-COM-SC-FF | 20MKA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-20MKA-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-FF | 20MKC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-IEC-10MKA-CM-CMP-0001 | 2028-07-24 | 285
G-COM-SC-FF | 20MKC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-08-16 | ALP-IEC-10MKA-ME-OMM-0001 | 2028-07-24 | 245
G-COM-SC-FF | 20MKC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-05-15 | ALP-EPC-20MKC-CM-MDB-0001 | 2028-07-24 | 50
G-COM-SC-WS | 00LBG | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-09-21 | ALP-EPC-00LBG-CM-CMP-0001 | 2028-09-25 | 264
G-COM-SC-WS | 00LBG | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-13 | ALP-EPC-00LBG-CM-OMM-0001 | 2028-09-25 | 248
G-COM-SC-WS | 00LBG | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-00LBG-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10HAN | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-09-29 | ALP-EPC-10HAN-CM-CMP-0001 | 2028-09-25 | 258
G-COM-SC-WS | 10HAN | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-10-13 | ALP-EPC-10HAN-CM-OMM-0001 | 2028-09-25 | 248
G-COM-SC-WS | 10HAN | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10HAN-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10LAB | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-09-29 | ALP-EPC-10LAB-CM-CMP-0001 | 2028-09-25 | 258
G-COM-SC-WS | 10LAB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-15 | ALP-EPC-10LAB-CM-OMM-0001 | 2028-09-25 | 246
G-COM-SC-WS | 10LAB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LAB-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10LAC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-01 | ALP-EPC-10LAC-CM-CMP-0001 | 2028-09-25 | 256
G-COM-SC-WS | 10LAC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-10-15 | ALP-EPC-10LAC-CM-OMM-0001 | 2028-09-25 | 246
G-COM-SC-WS | 10LAC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LAC-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10LAE | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-01 | ALP-EPC-10LAE-CM-CMP-0001 | 2028-09-25 | 256
G-COM-SC-WS | 10LAE | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-15 | ALP-EPC-10LAE-CM-OMM-0001 | 2028-09-25 | 246
G-COM-SC-WS | 10LAE | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LAE-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10LAF | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-01 | ALP-EPC-10LAF-CM-CMP-0001 | 2028-09-25 | 256
G-COM-SC-WS | 10LAF | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-15 | ALP-EPC-10LAF-CM-OMM-0001 | 2028-09-25 | 246
G-COM-SC-WS | 10LAF | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LAF-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10LBA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-11 | ALP-EPC-10LBA-CM-CMP-0001 | 2028-09-25 | 250
G-COM-SC-WS | 10LBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-25 | ALP-EPC-10LBA-CM-OMM-0001 | 2028-09-25 | 240
G-COM-SC-WS | 10LBA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LBA-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10LBB | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-12 | ALP-EPC-10LBB-CM-CMP-0001 | 2028-09-25 | 249
G-COM-SC-WS | 10LBB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-26 | ALP-EPC-10LBB-CM-OMM-0001 | 2028-09-25 | 239
G-COM-SC-WS | 10LBB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LBB-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10LBC | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-12 | ALP-EPC-10LBC-CM-CMP-0001 | 2028-09-25 | 249
G-COM-SC-WS | 10LBC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-26 | ALP-EPC-10LBC-CM-OMM-0001 | 2028-09-25 | 239
G-COM-SC-WS | 10LBC | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LBC-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 10LBD | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-14 | ALP-EPC-10LBD-CM-CMP-0001 | 2028-09-25 | 247
G-COM-SC-WS | 10LBD | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-28 | ALP-EPC-10LBD-CM-OMM-0001 | 2028-09-25 | 237
G-COM-SC-WS | 10LBD | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-10LBD-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 20LCA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-14 | ALP-EPC-20LCA-CM-CMP-0001 | 2028-09-25 | 247
G-COM-SC-WS | 20LCA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-28 | ALP-EPC-20LCA-CM-OMM-0001 | 2028-09-25 | 237
G-COM-SC-WS | 20LCA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-20LCA-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 20LCB | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-19 | ALP-EPC-20LCB-CM-CMP-0001 | 2028-09-25 | 244
G-COM-SC-WS | 20LCB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 2 | 2 | 2027-11-02 | ALP-EPC-20LCB-CM-OMM-0001 | 2028-09-25 | 234
G-COM-SC-WS | 20LCB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-20LCB-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 20MAA | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-09 | ALP-IEC-20MAA-CM-CMP-0001 | 2028-09-25 | 295
G-COM-SC-WS | 20MAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-04 | ALP-IEC-20MAA-ME-OMM-0001 | 2028-09-25 | 255
G-COM-SC-WS | 20MAA | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-20MAA-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 20MAB | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-09 | ALP-IEC-20MAA-CM-CMP-0001 | 2028-09-25 | 295
G-COM-SC-WS | 20MAB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-04 | ALP-IEC-20MAA-ME-OMM-0001 | 2028-09-25 | 255
G-COM-SC-WS | 20MAB | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-05 | ALP-EPC-20MAB-CM-MDB-0001 | 2028-09-25 | 80
G-COM-SC-WS | 20MAG | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-09 | ALP-IEC-20MAA-CM-CMP-0001 | 2028-09-25 | 295
G-COM-SC-WS | 20MAG | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-04 | ALP-IEC-20MAA-ME-OMM-0001 | 2028-09-25 | 255
G-COM-SC-WS | 20MAG | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAG-CM-MDB-0001 | 2028-09-25 | 70
G-COM-SC-WS | 20MAJ | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-09 | ALP-IEC-20MAA-CM-CMP-0001 | 2028-09-25 | 295
G-COM-SC-WS | 20MAJ | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-04 | ALP-IEC-20MAA-ME-OMM-0001 | 2028-09-25 | 255
G-COM-SC-WS | 20MAJ | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAJ-CM-MDB-0001 | 2028-09-25 | 70
G-COM-SC-WS | 20MAN | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-10-27 | ALP-EPC-20MAN-CM-CMP-0001 | 2028-09-25 | 238
G-COM-SC-WS | 20MAN | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-11-10 | ALP-EPC-20MAN-CM-OMM-0001 | 2028-09-25 | 228
G-COM-SC-WS | 20MAN | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAN-CM-MDB-0001 | 2028-09-25 | 70
G-COM-SC-WS | 20MAV | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-09 | ALP-IEC-20MAA-CM-CMP-0001 | 2028-09-25 | 295
G-COM-SC-WS | 20MAV | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-04 | ALP-IEC-20MAA-ME-OMM-0001 | 2028-09-25 | 255
G-COM-SC-WS | 20MAV | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAV-CM-MDB-0001 | 2028-09-25 | 70
G-COM-SC-WS | 20MAW | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-09 | ALP-IEC-20MAA-CM-CMP-0001 | 2028-09-25 | 295
G-COM-SC-WS | 20MAW | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-04 | ALP-IEC-20MAA-ME-OMM-0001 | 2028-09-25 | 255
G-COM-SC-WS | 20MAW | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAW-CM-MDB-0001 | 2028-09-25 | 70
G-COM-SC-WS | 20MAX | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED | 1 | 1 | 2027-08-09 | ALP-IEC-20MAA-CM-CMP-0001 | 2028-09-25 | 295
G-COM-SC-WS | 20MAX | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR | 1 | 1 | 2027-10-04 | ALP-IEC-20MAA-ME-OMM-0001 | 2028-09-25 | 255
G-COM-SC-WS | 20MAX | rule:DL-CM-TOD IFR | 1 | 1 | 2028-06-19 | ALP-EPC-20MAX-CM-MDB-0001 | 2028-09-25 | 70
G-CON-CWP | CWP-01-CV-01 | any:ewp-all IFC | 4 | 4 | 2027-02-26 | ALP-EPC-00UBF-CV-FND-0002 | 2027-03-22 | 16
G-CON-CWP | CWP-01-CV-02 | any:ewp-all IFC | 14 | 14 | 2027-04-06 | ALP-EPC-10UMA-HS-GAD-0001 | 2027-04-19 | 9
G-CON-CWP | CWP-01-EL-01 | any:ewp-all IFC | 11 | 11 | 2027-01-11 | ALP-IEC-10BAT-EL-GAD-0001 | 2028-01-10 | 260
G-CON-CWP | CWP-01-EL-01 | rule:DL-V-ERC@mr? IFR | 2 | 2 | 2027-09-02 | ALP-E02-10BBT-ME-PRC-0001 | 2028-01-10 | 92
G-CON-CWP | CWP-01-HV-01 | any:ewp-all IFC | 1 | 1 | 2027-05-27 | ALP-EPC-10UMA-HV-GAD-0001 | 2027-11-01 | 112
G-CON-CWP | CWP-01-HV-01 | rule:DL-V-ERC@mr? IFR | 2 | 2 | 2027-06-17 | ALP-M20-00SGA-ME-PRC-0001 | 2027-11-01 | 97
G-CON-CWP | CWP-01-IC-01 | any:ewp-all IFC | 13 | 13 | 2027-01-25 | ALP-IEC-10MBY-ME-GAD-0001 | 2028-02-07 | 270
G-CON-CWP | CWP-01-IC-01 | rule:DL-V-ERC@mr? IFR | 3 | 3 | 2027-07-27 | ALP-I03-00QUA-ME-PRC-0001 | 2028-02-07 | 139
G-CON-CWP | CWP-01-ME-01 | ewp-first? IFC | 3 | 3 | 2027-09-06 | ALP-IEC-10MBA-ME-PRC-0001 | 2027-10-18 | 30
G-CON-CWP | CWP-01-ME-01 | any:ewp-all IFC | 14 | 14 | 2027-01-11 | ALP-IEC-10HAA-ME-GAD-0001 | 2027-10-18 | 200
G-CON-CWP | CWP-01-ME-01 | rule:DL-V-ERC@mr? IFR | 5 | 5 | 2027-07-19 | ALP-IEC-10MKA-ME-PRC-0001 | 2027-10-18 | 65
G-CON-CWP | CWP-01-PI-01 | any:ewp-all IFC | 19 | 19 | 2027-06-09 | ALP-EPC-10UMA-PI-PPL-0001 | 2027-12-13 | 133
G-CON-CWP | CWP-01-SS-01 | any:ewp-all IFC | 5 | 5 | 2027-03-08 | ALP-EPC-10UMA-CV-ARC-0001 | 2027-07-12 | 90
G-CON-CWP | CWP-02-CV-01 | any:ewp-all IFC | 1 | 1 | 2027-03-08 | ALP-EPC-20UMB-CV-FND-0001 | 2027-03-22 | 10
G-CON-CWP | CWP-02-CV-02 | any:ewp-all IFC | 5 | 5 | 2027-03-29 | ALP-EPC-20UMB-HS-GAD-0001 | 2027-04-19 | 15
G-CON-CWP | CWP-02-EL-01 | any:ewp-all IFC | 4 | 4 | 2027-09-27 | ALP-EPC-20UMB-EL-ELY-0001 | 2028-02-28 | 110
G-CON-CWP | CWP-02-EL-01 | rule:DL-V-ERC@mr? IFR | 2 | 2 | 2027-09-02 | ALP-E02-10BBT-ME-PRC-0001 | 2028-02-28 | 127
G-CON-CWP | CWP-02-IC-01 | any:ewp-all IFC | 5 | 5 | 2027-03-23 | ALP-EPC-20UMB-IC-ELY-0002 | 2028-03-27 | 264
G-CON-CWP | CWP-02-IC-01 | rule:DL-V-ERC@mr? IFR | 1 | 1 | 2027-05-17 | ALP-IEC-10MBY-ME-PRC-0001 | 2028-03-27 | 225
G-CON-CWP | CWP-02-ME-01 | ewp-first? IFC | 1 | 1 | 2027-01-22 | ALP-EPC-20UMB-PI-LAY-0001 | 2027-12-20 | 236
G-CON-CWP | CWP-02-ME-01 | any:ewp-all IFC | 5 | 5 | 2027-01-11 | ALP-IEC-20MAA-ME-GAD-0001 | 2027-12-20 | 245
G-CON-CWP | CWP-02-ME-01 | rule:DL-V-ERC@mr? IFR | 4 | 4 | 2027-09-06 | ALP-IEC-20MAA-ME-PRC-0001 | 2027-12-20 | 75
G-CON-CWP | CWP-02-PI-01 | any:ewp-all IFC | 11 | 11 | 2027-05-19 | ALP-M06-00PAH-ME-GAD-0001 | 2028-01-31 | 183
G-CON-CWP | CWP-02-PI-01 | rule:DL-V-ERC@mr? IFR | 1 | 1 | 2027-07-21 | ALP-M06-00PAH-ME-PRC-0001 | 2028-01-31 | 138
G-CON-CWP | CWP-02-SS-01 | any:ewp-all IFC | 3 | 3 | 2027-02-23 | ALP-EPC-20UMB-CV-ARC-0001 | 2027-07-12 | 99
G-CON-CWP | CWP-03-CV-01 | ewp-first? IFC | 1 | 1 | 2027-01-13 | ALP-EPC-00UBA-PI-LAY-0001 | 2027-03-29 | 53
G-CON-CWP | CWP-03-CV-01 | any:ewp-all IFC | 6 | 6 | 2027-01-13 | ALP-EPC-00UBA-PI-LAY-0001 | 2027-03-29 | 53
G-CON-CWP | CWP-03-EL-01 | any:ewp-all IFC | 31 | 31 | 2027-03-02 | ALP-EPC-00UBA-EL-ELY-0001 | 2027-10-25 | 169
G-CON-CWP | CWP-03-EL-01 | rule:DL-V-ERC@mr? IFR | 5 | 5 | 2027-07-01 | ALP-E06-00XJA-ME-PRC-0001 | 2027-10-25 | 82
G-CON-CWP | CWP-03-HV-01 | any:ewp-all IFC | 7 | 7 | 2027-04-01 | ALP-H01-00SAA-ME-GAD-0001 | 2027-10-11 | 137
G-CON-CWP | CWP-03-HV-01 | rule:DL-V-ERC@mr? IFR | 1 | 1 | 2027-06-03 | ALP-H01-00SAA-ME-PRC-0001 | 2027-10-11 | 92
G-CON-CWP | CWP-03-SS-01 | any:ewp-all IFC | 4 | 4 | 2027-02-25 | ALP-EPC-00UBA-CV-ARC-0001 | 2027-05-24 | 62
G-CON-CWP | CWP-04-CV-01 | ewp-first? IFC | 1 | 1 | 2027-01-05 | ALP-EPC-00UAC-PI-LAY-0001 | 2027-04-05 | 64
G-CON-CWP | CWP-04-CV-01 | any:ewp-all IFC | 6 | 6 | 2027-01-05 | ALP-EPC-00UAC-PI-LAY-0001 | 2027-04-05 | 64
G-CON-CWP | CWP-04-EL-01 | any:ewp-all IFC | 11 | 11 | 2027-03-09 | ALP-E01-00ACA-ME-GAD-0001 | 2028-01-04 | 215
G-CON-CWP | CWP-04-EL-01 | rule:DL-V-ERC@mr? IFR | 1 | 1 | 2027-09-21 | ALP-E01-00ACA-ME-PRC-0001 | 2028-01-04 | 75
G-CON-CWP | CWP-04-SS-01 | any:ewp-all IFC | 4 | 4 | 2027-02-11 | ALP-EPC-00UAC-CV-ARC-0001 | 2027-05-31 | 77
G-CON-CWP | CWP-05-CV-01 | any:ewp-all IFC | 9 | 9 | 2027-02-09 | ALP-EPC-00UPC-CV-ARC-0001 | 2027-03-25 | 32
G-CON-CWP | CWP-05-EL-01 | any:ewp-all IFC | 4 | 4 | 2027-08-13 | ALP-EPC-00UPC-EL-ELY-0001 | 2028-01-31 | 121
G-CON-CWP | CWP-05-IC-01 | any:ewp-all IFC | 5 | 5 | 2027-03-22 | ALP-EPC-00UPC-IC-ELY-0002 | 2028-02-28 | 245
G-CON-CWP | CWP-05-ME-01 | ewp-first? IFC | 1 | 1 | 2027-01-07 | ALP-EPC-00UPC-PI-LAY-0001 | 2027-12-20 | 247
G-CON-CWP | CWP-05-ME-01 | any:ewp-all IFC | 7 | 7 | 2027-01-07 | ALP-EPC-00UPC-PI-LAY-0001 | 2027-12-20 | 247
G-CON-CWP | CWP-05-ME-01 | rule:DL-V-ERC@mr? IFR | 3 | 3 | 2027-08-26 | ALP-M03-00PAC-ME-PRC-0001 | 2027-12-20 | 82
G-CON-CWP | CWP-05-PI-01 | any:ewp-all IFC | 10 | 10 | 2027-06-11 | ALP-EPC-00UPC-PI-PPL-0001 | 2027-09-20 | 71
G-CON-CWP | CWP-06-CV-01 | ewp-first? IFC | 1 | 1 | 2027-02-02 | ALP-EPC-00UPA-PI-LAY-0001 | 2027-09-03 | 153
G-CON-CWP | CWP-06-CV-01 | any:ewp-all IFC | 11 | 11 | 2027-02-02 | ALP-EPC-00UPA-PI-LAY-0001 | 2027-09-03 | 153
G-CON-CWP | CWP-07-CV-01 | any:ewp-all IFC | 5 | 5 | 2027-03-31 | ALP-EPC-00UGA-CV-FND-0001 | 2027-04-05 | 3
G-CON-CWP | CWP-07-EL-01 | any:ewp-all IFC | 4 | 4 | 2027-09-17 | ALP-EPC-00UGA-EL-ELY-0001 | 2028-02-21 | 111
G-CON-CWP | CWP-07-IC-01 | any:ewp-all IFC | 5 | 5 | 2027-03-25 | ALP-EPC-00UGA-IC-ELY-0002 | 2028-03-20 | 257
G-CON-CWP | CWP-07-ME-01 | ewp-first? IFC | 1 | 1 | 2027-01-19 | ALP-EPC-00UGA-PI-LAY-0001 | 2027-12-27 | 244
G-CON-CWP | CWP-07-ME-01 | any:ewp-all IFC | 7 | 7 | 2027-01-19 | ALP-EPC-00UGA-PI-LAY-0001 | 2027-12-27 | 244
G-CON-CWP | CWP-07-ME-01 | rule:DL-V-ERC@mr? IFR | 3 | 3 | 2027-09-09 | ALP-M12-00GBA-ME-PRC-0001 | 2027-12-27 | 77
G-CON-CWP | CWP-07-PI-01 | any:ewp-all IFC | 13 | 13 | 2027-03-31 | ALP-EPC-00UGA-PI-PPL-0001 | 2028-01-24 | 213
G-CON-CWP | CWP-07-SS-01 | any:ewp-all IFC | 4 | 4 | 2027-03-01 | ALP-EPC-00UGA-CV-ARC-0001 | 2027-06-14 | 75
G-CON-CWP | CWP-08-CV-01 | any:ewp-all IFC | 5 | 5 | 2027-04-01 | ALP-EPC-00UQA-HS-GAD-0001 | 2027-05-04 | 23
G-CON-CWP | CWP-08-EL-01 | any:ewp-all IFC | 4 | 4 | 2027-04-15 | ALP-EPC-00UQA-EL-ELY-0001 | 2028-01-10 | 192
G-CON-CWP | CWP-08-IC-01 | any:ewp-all IFC | 6 | 6 | 2027-03-25 | ALP-EPC-00UQA-IC-ELY-0002 | 2028-02-21 | 237
G-CON-CWP | CWP-08-ME-01 | ewp-first? IFC | 1 | 1 | 2027-01-26 | ALP-EPC-00UQA-PI-LAY-0001 | 2027-11-01 | 199
G-CON-CWP | CWP-08-ME-01 | any:ewp-all IFC | 17 | 17 | 2027-01-26 | ALP-EPC-00UQA-PI-LAY-0001 | 2027-11-01 | 199
G-CON-CWP | CWP-08-ME-01 | rule:DL-V-ERC@mr? IFR | 9 | 9 | 2027-08-18 | ALP-M11-00QCA-ME-PRC-0001 | 2027-11-01 | 53
G-CON-CWP | CWP-08-PI-01 | any:ewp-all IFC | 25 | 25 | 2027-05-17 | ALP-EPC-00UQA-PI-PPL-0001 | 2027-12-13 | 150
G-CON-CWP | CWP-08-SS-01 | any:ewp-all IFC | 3 | 3 | 2027-03-03 | ALP-EPC-00UQA-CV-ARC-0001 | 2027-06-29 | 84
G-CON-CWP | CWP-09-CV-01 | any:ewp-all IFC | 8 | 8 | 2027-03-31 | ALP-S01-00UEK-SS-STL-0001 | 2027-08-04 | 90
G-CON-CWP | CWP-09-EL-01 | any:ewp-all IFC | 4 | 4 | 2027-03-31 | ALP-EPC-00UEK-EL-ELY-0001 | 2027-12-27 | 193
G-CON-CWP | CWP-09-IC-01 | any:ewp-all IFC | 5 | 5 | 2027-07-19 | ALP-EPC-00UEK-IC-ELY-0002 | 2028-01-24 | 135
G-CON-CWP | CWP-09-ME-01 | ewp-first? IFC | 1 | 1 | 2027-02-01 | ALP-EPC-00UEK-PI-LAY-0001 | 2027-11-01 | 195
G-CON-CWP | CWP-09-ME-01 | any:ewp-all IFC | 3 | 3 | 2027-02-01 | ALP-EPC-00UEK-PI-LAY-0001 | 2027-11-01 | 195
G-CON-CWP | CWP-09-ME-01 | rule:DL-V-ERC@mr? IFR | 1 | 1 | 2027-07-29 | ALP-M15-00EKA-ME-PRC-0001 | 2027-11-01 | 67
G-CON-CWP | CWP-09-PI-01 | any:ewp-all IFC | 5 | 5 | 2027-04-05 | ALP-EPC-00UEK-PI-PPL-0001 | 2027-11-29 | 170
G-CON-CWP | CWP-10-CV-01 | any:ewp-all IFC | 5 | 5 | 2027-03-31 | ALP-S01-00UEG-SS-STL-0001 | 2027-06-03 | 46
G-CON-CWP | CWP-10-EL-01 | any:ewp-all IFC | 4 | 4 | 2027-08-09 | ALP-EPC-00UEG-EL-ELY-0001 | 2028-01-24 | 120
G-CON-CWP | CWP-10-IC-01 | any:ewp-all IFC | 4 | 4 | 2027-07-23 | ALP-EPC-00UEG-IC-HUP-0001 | 2028-02-21 | 151
G-CON-CWP | CWP-10-ME-01 | ewp-first? IFC | 1 | 1 | 2027-01-27 | ALP-EPC-00UEG-PI-LAY-0001 | 2027-10-04 | 178
G-CON-CWP | CWP-10-ME-01 | any:ewp-all IFC | 3 | 3 | 2027-01-27 | ALP-EPC-00UEG-PI-LAY-0001 | 2027-10-04 | 178
G-CON-CWP | CWP-10-ME-01 | rule:DL-V-ERC@mr? IFR | 1 | 1 | 2027-07-01 | ALP-M16-00EGA-ME-PRC-0001 | 2027-10-04 | 67
G-CON-CWP | CWP-10-PI-01 | any:ewp-all IFC | 7 | 7 | 2027-03-31 | ALP-EPC-00UEG-PI-PPL-0001 | 2027-12-27 | 193
G-CON-CWP | CWP-11-CV-01 | ewp-first? IFC | 1 | 1 | 2027-01-19 | ALP-EPC-00UCA-PI-LAY-0001 | 2027-03-29 | 49
G-CON-CWP | CWP-11-CV-01 | any:ewp-all IFC | 13 | 13 | 2027-01-19 | ALP-EPC-00UCA-PI-LAY-0001 | 2027-03-29 | 49
G-CON-CWP | CWP-11-EL-01 | any:ewp-all IFC | 6 | 6 | 2027-03-01 | ALP-EPC-00UCA-EL-ELY-0001 | 2027-11-08 | 180
G-CON-CWP | CWP-11-HV-01 | any:ewp-all IFC | 2 | 2 | 2027-05-27 | ALP-EPC-00UCA-HV-GAD-0001 | 2027-11-08 | 117
G-CON-CWP | CWP-11-HV-01 | rule:DL-V-ERC@mr? IFR | 1 | 1 | 2027-06-03 | ALP-H01-00SAA-ME-PRC-0001 | 2027-11-08 | 112
G-CON-CWP | CWP-11-IC-01 | any:ewp-all IFC | 17 | 17 | 2027-03-25 | ALP-EPC-00USA-IC-ELY-0001 | 2027-11-22 | 172
G-CON-CWP | CWP-11-IC-01 | rule:DL-V-ERC@mr? IFR | 4 | 4 | 2027-08-05 | ALP-I08-00CJG-ME-PRC-0001 | 2027-11-22 | 77
G-CON-CWP | CWP-11-SS-01 | any:ewp-all IFC | 12 | 12 | 2027-03-01 | ALP-EPC-00USA-CV-ARC-0001 | 2027-05-24 | 60
G-CON-CWP | CWP-12-CV-01 | ewp-first? IFC | 1 | 1 | 2027-01-05 | ALP-EPC-00UZA-PI-LAY-0001 | 2027-01-18 | 9
G-CON-CWP | CWP-12-CV-01 | any:ewp-all IFC | 3 | 3 | 2026-12-15 | ALP-EPC-00UZA-CV-CVL-0001 | 2027-01-18 | 24
G-CON-CWP | CWP-12-CV-01 | rule:DL-V-ERC@mr? IFR | 1 | 1 | 2026-11-02 | ALP-E11-00000-ME-PRC-0001 | 2027-01-18 | 55
G-CON-CWP | CWP-12-CV-02 | any:ewp-all IFC | 10 | 10 | 2027-03-16 | ALP-EPC-00UZA-CV-CVL-0002 | 2027-03-22 | 4
G-CON-CWP | CWP-12-EL-01 | any:ewp-all IFC | 8 | 8 | 2027-02-24 | ALP-EPC-00UZB-EL-ELY-0001 | 2027-05-17 | 58
G-CON-CWP | CWP-12-PI-01 | any:ewp-all IFC | 12 | 12 | 2027-03-15 | ALP-EPC-00UZA-PI-PPL-0001 | 2027-07-12 | 85
G-CON-IWP | CWP-01-CV-01 | ewp-all IFC | 4 | 4 | 2027-03-04 | ALP-EPC-10UMA-CV-FND-0001 | 2027-05-03 | 42
G-CON-IWP | CWP-01-CV-02 | ewp-all IFC | 14 | 14 | 2027-06-21 | ALP-EPC-00UBF-CV-EFD-0001 | 2027-07-19 | 20
G-CON-IWP | CWP-01-EL-01 | ewp-all IFC | 11 | 11 | 2027-10-07 | ALP-EPC-10UMA-EL-ELY-0003 | 2028-04-10 | 132
G-CON-IWP | CWP-01-HV-01 | ewp-all IFC | 1 | 1 | 2027-05-27 | ALP-EPC-10UMA-HV-GAD-0001 | 2027-12-27 | 152
G-CON-IWP | CWP-01-IC-01 | ewp-all IFC | 13 | 13 | 2027-09-29 | ALP-EPC-10UMA-IC-LOP-0002 | 2028-05-01 | 153
G-CON-IWP | CWP-01-ME-01 | ewp-all IFC | 14 | 14 | 2027-09-06 | ALP-IEC-10MBA-ME-PRC-0001 | 2028-02-14 | 115
G-CON-IWP | CWP-01-PI-01 | ewp-all IFC | 19 | 19 | 2028-03-01 | ALP-EPC-10LAF-PI-SUP-0001 | 2028-03-27 | 18
G-CON-IWP | CWP-01-SS-01 | ewp-all IFC | 5 | 5 | 2027-07-06 | ALP-EPC-00UBF-SS-STL-0001 | 2027-09-27 | 59
G-CON-IWP | CWP-02-CV-01 | ewp-all IFC | 1 | 1 | 2027-03-08 | ALP-EPC-20UMB-CV-FND-0001 | 2027-04-26 | 35
G-CON-IWP | CWP-02-CV-02 | ewp-all IFC | 5 | 5 | 2027-06-28 | ALP-EPC-20UMB-CV-EFD-0001 | 2027-07-26 | 20
G-CON-IWP | CWP-02-EL-01 | ewp-all IFC | 4 | 4 | 2027-11-04 | ALP-EPC-20UMB-EL-ELY-0002 | 2028-05-15 | 137
G-CON-IWP | CWP-02-IC-01 | ewp-all IFC | 5 | 5 | 2027-09-27 | ALP-EPC-20UMB-IC-LOP-0001 | 2028-06-12 | 185
G-CON-IWP | CWP-02-ME-01 | ewp-all IFC | 5 | 5 | 2027-06-15 | ALP-M02-20LCB-EL-WIR-0001 | 2028-04-03 | 209
G-CON-IWP | CWP-02-PI-01 | ewp-all IFC | 11 | 11 | 2028-04-27 | ALP-EPC-20LCA-PI-SUP-0001 | 2028-05-15 | 12
G-CON-IWP | CWP-02-SS-01 | ewp-all IFC | 3 | 3 | 2027-07-06 | ALP-EPC-20UMB-SS-STL-0001 | 2027-09-27 | 59
G-CON-IWP | CWP-03-CV-01 | ewp-all IFC | 6 | 6 | 2027-04-20 | ALP-EPC-00UBA-CV-EFD-0001 | 2027-05-17 | 19
G-CON-IWP | CWP-03-EL-01 | ewp-all IFC | 31 | 31 | 2027-09-15 | ALP-EPC-00UBA-IC-LOP-0001 | 2027-12-27 | 73
G-CON-IWP | CWP-03-HV-01 | ewp-all IFC | 7 | 7 | 2027-10-22 | ALP-EPC-00SAA-PI-SUP-0001 | 2027-11-29 | 26
G-CON-IWP | CWP-03-SS-01 | ewp-all IFC | 4 | 4 | 2027-05-13 | ALP-EPC-00UBA-SS-STL-0002 | 2027-09-06 | 82
G-CON-IWP | CWP-04-CV-01 | ewp-all IFC | 6 | 6 | 2027-04-16 | ALP-EPC-00UAC-CV-EFD-0001 | 2027-05-17 | 21
G-CON-IWP | CWP-04-EL-01 | ewp-all IFC | 11 | 11 | 2027-09-16 | ALP-EPC-00UAC-EL-CBL-0001 | 2028-03-14 | 128
G-CON-IWP | CWP-04-SS-01 | ewp-all IFC | 4 | 4 | 2027-04-23 | ALP-EPC-00UAC-SS-STL-0002 | 2027-08-09 | 76
G-CON-IWP | CWP-05-CV-01 | ewp-all IFC | 9 | 9 | 2027-06-04 | ALP-EPC-00UPC-CV-EFD-0001 | 2027-07-08 | 24
G-CON-IWP | CWP-05-EL-01 | ewp-all IFC | 4 | 4 | 2027-10-08 | ALP-EPC-00UPC-EL-ELY-0003 | 2028-03-20 | 116
G-CON-IWP | CWP-05-IC-01 | ewp-all IFC | 5 | 5 | 2027-09-08 | ALP-EPC-00UPC-IC-LOP-0002 | 2028-04-10 | 153
G-CON-IWP | CWP-05-ME-01 | ewp-all IFC | 7 | 7 | 2027-06-08 | ALP-M05-00PBA-EL-WIR-0001 | 2028-02-14 | 179
G-CON-IWP | CWP-05-PI-01 | ewp-all IFC | 10 | 10 | 2027-10-08 | ALP-EPC-00PBA-PI-SUP-0001 | 2027-12-13 | 46
G-CON-IWP | CWP-06-CV-01 | ewp-all IFC | 11 | 11 | 2027-09-06 | ALP-EPC-00UPA-EL-ELY-0001 | 2027-12-03 | 64
G-CON-IWP | CWP-07-CV-01 | ewp-all IFC | 5 | 5 | 2027-06-01 | ALP-EPC-00UGA-CV-EFD-0001 | 2027-06-21 | 14
G-CON-IWP | CWP-07-EL-01 | ewp-all IFC | 4 | 4 | 2027-10-19 | ALP-EPC-00UGA-EL-ELY-0002 | 2028-04-17 | 129
G-CON-IWP | CWP-07-IC-01 | ewp-all IFC | 5 | 5 | 2027-09-20 | ALP-EPC-00UGA-IC-LOP-0002 | 2028-05-08 | 165
G-CON-IWP | CWP-07-ME-01 | ewp-all IFC | 7 | 7 | 2027-06-03 | ALP-M12-00GBA-EL-WIR-0001 | 2028-03-06 | 197
G-CON-IWP | CWP-07-PI-01 | ewp-all IFC | 13 | 13 | 2028-03-10 | ALP-EPC-00GUA-PI-SUP-0001 | 2028-04-03 | 16
G-CON-IWP | CWP-07-SS-01 | ewp-all IFC | 4 | 4 | 2027-05-14 | ALP-EPC-00UGA-SS-STL-0002 | 2027-08-23 | 71
G-CON-IWP | CWP-08-CV-01 | ewp-all IFC | 5 | 5 | 2027-06-07 | ALP-EPC-00UQA-CV-EFD-0001 | 2027-07-13 | 26
G-CON-IWP | CWP-08-EL-01 | ewp-all IFC | 4 | 4 | 2027-09-28 | ALP-EPC-00UQA-EL-CBL-0001 | 2028-03-20 | 124
G-CON-IWP | CWP-08-IC-01 | ewp-all IFC | 6 | 6 | 2027-10-04 | ALP-EPC-00UQA-IC-LOP-0002 | 2028-04-24 | 145
G-CON-IWP | CWP-08-ME-01 | ewp-all IFC | 17 | 17 | 2027-08-03 | ALP-M11-00QCA-EL-WIR-0001 | 2028-01-24 | 124
G-CON-IWP | CWP-08-PI-01 | ewp-all IFC | 25 | 25 | 2028-01-27 | ALP-EPC-10LAB-PI-SUP-0001 | 2028-03-06 | 27
G-CON-IWP | CWP-08-SS-01 | ewp-all IFC | 3 | 3 | 2027-06-15 | ALP-EPC-00UQA-SS-STL-0001 | 2027-09-07 | 60
G-CON-IWP | CWP-09-CV-01 | ewp-all IFC | 8 | 8 | 2027-07-27 | ALP-EPC-00UEK-CV-EFD-0001 | 2027-09-15 | 36
G-CON-IWP | CWP-09-EL-01 | ewp-all IFC | 4 | 4 | 2027-08-25 | ALP-EPC-00UEK-EL-CBL-0001 | 2028-01-31 | 113
G-CON-IWP | CWP-09-IC-01 | ewp-all IFC | 5 | 5 | 2027-09-09 | ALP-EPC-00UEK-IC-LOP-0002 | 2028-02-28 | 122
G-CON-IWP | CWP-09-ME-01 | ewp-all IFC | 3 | 3 | 2027-05-20 | ALP-M15-00EKA-EL-WIR-0001 | 2027-12-13 | 147
G-CON-IWP | CWP-09-PI-01 | ewp-all IFC | 5 | 5 | 2027-12-10 | ALP-EPC-00EKC-PI-SUP-0001 | 2028-01-24 | 31
G-CON-IWP | CWP-10-CV-01 | ewp-all IFC | 5 | 5 | 2027-06-23 | ALP-EPC-00UEG-CV-EFD-0001 | 2027-08-05 | 31
G-CON-IWP | CWP-10-EL-01 | ewp-all IFC | 4 | 4 | 2027-09-27 | ALP-EPC-00UEG-EL-ELY-0003 | 2028-03-06 | 115
G-CON-IWP | CWP-10-IC-01 | ewp-all IFC | 4 | 4 | 2027-09-08 | ALP-EPC-00UEG-IC-LOP-0002 | 2028-04-03 | 148
G-CON-IWP | CWP-10-ME-01 | ewp-all IFC | 3 | 3 | 2027-05-07 | ALP-M16-00EGA-EL-WIR-0001 | 2028-01-10 | 176
G-CON-IWP | CWP-10-PI-01 | ewp-all IFC | 7 | 7 | 2028-01-26 | ALP-EPC-00EGC-PI-SUP-0001 | 2028-03-06 | 28
G-CON-IWP | CWP-11-CV-01 | ewp-all IFC | 13 | 13 | 2027-04-26 | ALP-EPC-00UYA-HV-GAD-0001 | 2027-05-24 | 20
G-CON-IWP | CWP-11-EL-01 | ewp-all IFC | 6 | 6 | 2027-09-07 | ALP-EPC-00UCA-EL-ELY-0002 | 2028-01-03 | 84
G-CON-IWP | CWP-11-HV-01 | ewp-all IFC | 2 | 2 | 2027-08-06 | ALP-EPC-00UCA-PI-PPL-0001 | 2027-12-27 | 101
G-CON-IWP | CWP-11-IC-01 | ewp-all IFC | 17 | 17 | 2027-09-16 | ALP-I09-00CKA-EL-WIR-0001 | 2028-01-31 | 97
G-CON-IWP | CWP-11-SS-01 | ewp-all IFC | 12 | 12 | 2027-06-21 | ALP-EPC-00UYA-SS-STL-0001 | 2027-09-27 | 70
G-CON-IWP | CWP-12-CV-01 | ewp-all IFC | 3 | 3 | 2027-01-11 | ALP-EPC-00UZB-CV-CVL-0001 | 2027-03-01 | 35
G-CON-IWP | CWP-12-CV-02 | ewp-all IFC | 10 | 10 | 2027-06-17 | ALP-EPC-00UZE-CV-RBR-0001 | 2027-10-18 | 87
G-CON-IWP | CWP-12-EL-01 | ewp-all IFC | 8 | 8 | 2027-06-10 | ALP-EPC-00UZD-EL-ELY-0001 | 2027-11-08 | 107
G-CON-IWP | CWP-12-PI-01 | ewp-all IFC | 12 | 12 | 2027-10-20 | ALP-EPC-00SGA-PI-ISO-0001 | 2027-11-29 | 28
G-OPS-AB | 00000 | type:PID AB | 67 | 67 |  |  | 2029-07-18
G-OPS-AB | 00000 | type:SLD AB | 9 | 9 |  |  | 2029-07-18
G-OPS-AB | 00000 | type:ISO AB | 42 | 42 |  |  | 2029-07-18
G-OPS-AB | 00000 | rule:DL-PI-LAY AB | 12 | 12 |  |  | 2029-07-18
G-OPS-AB | 00000 | type:M3D@plant AB | 4 | 4 |  |  | 2029-07-18
G-OPS-HO-EL | 00ACA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-03-07 | ALP-E01-00ACA-ME-OMM-0001 | 2029-04-18 | 291
G-OPS-HO-EL | 00ACA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00ACA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00BBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-16 | ALP-E03-00BBA-ME-OMM-0001 | 2029-04-18 | 349
G-OPS-HO-EL | 00BBA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00BBA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00BFA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-11-25 | ALP-E05-00BFA-ME-OMM-0001 | 2029-04-18 | 364
G-OPS-HO-EL | 00BFA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00BFA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00BFT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-11-23 | ALP-E04-00BFT-ME-OMM-0001 | 2029-04-18 | 366
G-OPS-HO-EL | 00BFT | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00BFT-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00BLA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-03-09 | ALP-EPC-00BLA-CM-OMM-0001 | 2029-04-18 | 551
G-OPS-HO-EL | 00BLA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00BLA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00BMA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-11-25 | ALP-E05-00BFA-ME-OMM-0001 | 2029-04-18 | 364
G-OPS-HO-EL | 00BMA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00BMA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00BRA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-01 | ALP-E07-00BRA-ME-OMM-0001 | 2029-04-18 | 360
G-OPS-HO-EL | 00BRA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00BRA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00BTA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-01 | ALP-E07-00BRA-ME-OMM-0001 | 2029-04-18 | 360
G-OPS-HO-EL | 00BTA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00BTA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00BXA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-23 | ALP-E10-00BXA-ME-OMM-0001 | 2029-04-18 | 366
G-OPS-HO-EL | 00BXA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00BXA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 00XJA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-16 | ALP-E06-00XJA-ME-OMM-0001 | 2029-04-18 | 349
G-OPS-HO-EL | 00XJA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-00XJA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 10BAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-EL | 10BAA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-10BAA-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 10BAC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-EL | 10BAC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-10BAC-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 10BAT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-10 | ALP-IEC-10BAT-ME-OMM-0001 | 2029-04-18 | 332
G-OPS-HO-EL | 10BAT | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-10BAT-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 10BBT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-02-17 | ALP-E02-10BBT-ME-OMM-0001 | 2029-04-18 | 304
G-OPS-HO-EL | 10BBT | rule:DL-CM-TOD IFC | 1 | 1 | 2028-01-25 | ALP-EPC-10BBT-CM-MDB-0001 | 2029-04-18 | 321
G-OPS-HO-EL | 20BAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-EL | 20BAA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-02-08 | ALP-EPC-20BAA-CM-MDB-0001 | 2029-04-18 | 311
G-OPS-HO-EL | 20BAC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-EL | 20BAC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-02-08 | ALP-EPC-20BAC-CM-MDB-0001 | 2029-04-18 | 311
G-OPS-HO-EL | 20BAT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-10 | ALP-IEC-10BAT-ME-OMM-0001 | 2029-04-18 | 332
G-OPS-HO-EL | 20BAT | rule:DL-CM-TOD IFC | 1 | 1 | 2028-02-08 | ALP-EPC-20BAT-CM-MDB-0001 | 2029-04-18 | 311
G-OPS-HO-EL | 20BBT | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-02-17 | ALP-E02-10BBT-ME-OMM-0001 | 2029-04-18 | 304
G-OPS-HO-EL | 20BBT | rule:DL-CM-TOD IFC | 1 | 1 | 2028-02-08 | ALP-EPC-20BBT-CM-MDB-0001 | 2029-04-18 | 311
G-OPS-HO-FF | 00CJA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-20 | ALP-I01-00CJA-ME-OMM-0001 | 2029-04-18 | 324
G-OPS-HO-FF | 00CJA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00CJA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00CJG | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-20 | ALP-I08-00CJG-ME-OMM-0001 | 2029-04-18 | 324
G-OPS-HO-FF | 00CJG | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00CJG-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00CKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-05-11 | ALP-I09-00CKA-ME-OMM-0001 | 2029-04-18 | 244
G-OPS-HO-FF | 00CKA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00CKA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00CQA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-07 | ALP-I02-00CQA-ME-OMM-0001 | 2029-04-18 | 333
G-OPS-HO-FF | 00CQA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00CQA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00CYA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-03 | ALP-I07-00CYA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-FF | 00CYA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00CYA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00EGA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-16 | ALP-M16-00EGA-ME-OMM-0001 | 2029-04-18 | 349
G-OPS-HO-FF | 00EGA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00EGA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00EGB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-08-03 | ALP-EPC-00EGB-CM-OMM-0001 | 2029-04-18 | 446
G-OPS-HO-FF | 00EGB | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00EGB-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00EGC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-16 | ALP-M16-00EGA-ME-OMM-0001 | 2029-04-18 | 349
G-OPS-HO-FF | 00EGC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00EGC-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00EKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-13 | ALP-M15-00EKA-ME-OMM-0001 | 2029-04-18 | 329
G-OPS-HO-FF | 00EKA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00EKA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00EKC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-08-06 | ALP-EPC-00EKC-CM-OMM-0001 | 2029-04-18 | 443
G-OPS-HO-FF | 00EKC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00EKC-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00GBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-02-24 | ALP-M12-00GBA-ME-OMM-0001 | 2029-04-18 | 299
G-OPS-HO-FF | 00GBA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00GBA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00GCA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-02-24 | ALP-M12-00GBA-ME-OMM-0001 | 2029-04-18 | 299
G-OPS-HO-FF | 00GCA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00GCA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00GHA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-10-15 | ALP-M13-00GHA-ME-OMM-0001 | 2029-04-18 | 393
G-OPS-HO-FF | 00GHA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00GHA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00GKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-10-15 | ALP-M13-00GHA-ME-OMM-0001 | 2029-04-18 | 393
G-OPS-HO-FF | 00GKA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-10 | ALP-EPC-00GKA-CM-MDB-0001 | 2029-04-18 | 267
G-OPS-HO-FF | 00GMA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-11-18 | ALP-M14-00GNA-ME-OMM-0001 | 2029-04-18 | 369
G-OPS-HO-FF | 00GMA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00GMA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00GNA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-11-18 | ALP-M14-00GNA-ME-OMM-0001 | 2029-04-18 | 369
G-OPS-HO-FF | 00GNA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00GNA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00GUA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-11-18 | ALP-M14-00GNA-ME-OMM-0001 | 2029-04-18 | 369
G-OPS-HO-FF | 00GUA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00GUA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00LDA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-02-24 | ALP-M12-00GBA-ME-OMM-0001 | 2029-04-18 | 299
G-OPS-HO-FF | 00LDA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00LDA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00PAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-14 | ALP-M04-00PAA-ME-OMM-0001 | 2029-04-18 | 328
G-OPS-HO-FF | 00PAA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00PAA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00PAB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-08-09 | ALP-EPC-00PAB-CM-OMM-0001 | 2029-04-18 | 442
G-OPS-HO-FF | 00PAB | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00PAB-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00PAC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-02-10 | ALP-M03-00PAC-ME-OMM-0001 | 2029-04-18 | 309
G-OPS-HO-FF | 00PAC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00PAC-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00PAH | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-05 | ALP-M06-00PAH-ME-OMM-0001 | 2029-04-18 | 335
G-OPS-HO-FF | 00PAH | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00PAH-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00PBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-17 | ALP-M05-00PBA-ME-OMM-0001 | 2029-04-18 | 327
G-OPS-HO-FF | 00PBA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00PBA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00PGA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-09 | ALP-M07-00PGA-ME-OMM-0001 | 2029-04-18 | 354
G-OPS-HO-FF | 00PGA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00PGA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00QCA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-02-02 | ALP-M11-00QCA-ME-OMM-0001 | 2029-04-18 | 315
G-OPS-HO-FF | 00QCA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00QCA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00QEA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-09 | ALP-M08-00QEA-ME-OMM-0001 | 2029-04-18 | 354
G-OPS-HO-FF | 00QEA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00QEA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00QHA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-13 | ALP-M09-00QHA-ME-OMM-0001 | 2029-04-18 | 329
G-OPS-HO-FF | 00QHA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00QHA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00QJA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-28 | ALP-M10-00QJA-ME-OMM-0001 | 2029-04-18 | 341
G-OPS-HO-FF | 00QJA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-04-24 | ALP-EPC-00QJA-CM-MDB-0001 | 2029-04-18 | 257
G-OPS-HO-FF | 00QJB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-28 | ALP-M10-00QJA-ME-OMM-0001 | 2029-04-18 | 341
G-OPS-HO-FF | 00QJB | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-00QJB-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 00QUA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-11 | ALP-I03-00QUA-ME-OMM-0001 | 2029-04-18 | 331
G-OPS-HO-FF | 00QUA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-00QUA-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 00SAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-11-18 | ALP-H01-00SAA-ME-OMM-0001 | 2029-04-18 | 369
G-OPS-HO-FF | 00SAA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-00SAA-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 00SGA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-02 | ALP-M20-00SGA-ME-OMM-0001 | 2029-04-18 | 359
G-OPS-HO-FF | 00SGA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-00SGA-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 00SGC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-02 | ALP-M20-00SGA-ME-OMM-0001 | 2029-04-18 | 359
G-OPS-HO-FF | 00SGC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-00SGC-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 00SGY | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-10 | ALP-I06-00SGY-ME-OMM-0001 | 2029-04-18 | 332
G-OPS-HO-FF | 00SGY | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-00SGY-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 00SMA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-12-16 | ALP-M21-00SMA-ME-OMM-0001 | 2029-04-18 | 349
G-OPS-HO-FF | 00SMA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-00SMA-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 10HAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-12-27 | ALP-IEC-10HAA-ME-OMM-0001 | 2029-04-18 | 342
G-OPS-HO-FF | 10HAA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-10HAA-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 10HNA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-12-27 | ALP-IEC-10HAA-ME-OMM-0001 | 2029-04-18 | 342
G-OPS-HO-FF | 10HNA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-10HNA-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 10HNE | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-10HNE-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 10HSA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-12-27 | ALP-IEC-10HAA-ME-OMM-0001 | 2029-04-18 | 342
G-OPS-HO-FF | 10HSA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-10HSA-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 10HSB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-12-13 | ALP-M18-10HSB-ME-OMM-0001 | 2029-04-18 | 352
G-OPS-HO-FF | 10HSB | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-10HSB-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 10MBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-07-24 | ALP-IEC-10MBA-ME-OMM-0001 | 2029-04-18 | 192
G-OPS-HO-FF | 10MBA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-10MBA-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 10MBL | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-07-24 | ALP-IEC-10MBA-ME-OMM-0001 | 2029-04-18 | 192
G-OPS-HO-FF | 10MBL | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-08 | ALP-EPC-10MBL-CM-MDB-0001 | 2029-04-18 | 247
G-OPS-HO-FF | 10MBN | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-07-24 | ALP-IEC-10MBA-ME-OMM-0001 | 2029-04-18 | 192
G-OPS-HO-FF | 10MBN | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-10MBN-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 10MBP | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-07-24 | ALP-IEC-10MBA-ME-OMM-0001 | 2029-04-18 | 192
G-OPS-HO-FF | 10MBP | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-10MBP-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 10MBU | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-07-24 | ALP-IEC-10MBA-ME-OMM-0001 | 2029-04-18 | 192
G-OPS-HO-FF | 10MBU | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-10MBU-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 10MBV | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-07-24 | ALP-IEC-10MBA-ME-OMM-0001 | 2029-04-18 | 192
G-OPS-HO-FF | 10MBV | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-10MBV-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 10MBY | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-01 | ALP-IEC-10MBY-ME-OMM-0001 | 2029-04-18 | 382
G-OPS-HO-FF | 10MBY | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-10MBY-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 10MKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-FF | 10MKA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-10MKA-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 10MKC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-FF | 10MKC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-10MKC-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 10MKG | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-FF | 10MKG | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-10MKG-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 20MAY | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-01 | ALP-IEC-10MBY-ME-OMM-0001 | 2029-04-18 | 382
G-OPS-HO-FF | 20MAY | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-20MAY-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 20MKA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-FF | 20MKA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-20MKA-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-FF | 20MKC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-01-03 | ALP-IEC-10MKA-ME-OMM-0001 | 2029-04-18 | 337
G-OPS-HO-FF | 20MKC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-05-22 | ALP-EPC-20MKC-CM-MDB-0001 | 2029-04-18 | 237
G-OPS-HO-WS | 00LBG | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-10 | ALP-EPC-00LBG-CM-OMM-0001 | 2029-04-18 | 375
G-OPS-HO-WS | 00LBG | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-00LBG-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10HAN | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2027-11-10 | ALP-EPC-10HAN-CM-OMM-0001 | 2029-04-18 | 375
G-OPS-HO-WS | 10HAN | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10HAN-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10LAB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-12 | ALP-EPC-10LAB-CM-OMM-0001 | 2029-04-18 | 373
G-OPS-HO-WS | 10LAB | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10LAB-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10LAC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-13 | ALP-M01-10LAC-ME-OMM-0001 | 2029-04-18 | 329
G-OPS-HO-WS | 10LAC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10LAC-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10LAE | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-12 | ALP-EPC-10LAE-CM-OMM-0001 | 2029-04-18 | 373
G-OPS-HO-WS | 10LAE | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10LAE-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10LAF | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-12 | ALP-EPC-10LAF-CM-OMM-0001 | 2029-04-18 | 373
G-OPS-HO-WS | 10LAF | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10LAF-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10LBA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-22 | ALP-EPC-10LBA-CM-OMM-0001 | 2029-04-18 | 367
G-OPS-HO-WS | 10LBA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10LBA-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10LBB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-23 | ALP-EPC-10LBB-CM-OMM-0001 | 2029-04-18 | 366
G-OPS-HO-WS | 10LBB | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10LBB-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10LBC | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-23 | ALP-EPC-10LBC-CM-OMM-0001 | 2029-04-18 | 366
G-OPS-HO-WS | 10LBC | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10LBC-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 10LBD | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-25 | ALP-EPC-10LBD-CM-OMM-0001 | 2029-04-18 | 364
G-OPS-HO-WS | 10LBD | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-10LBD-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 20LCA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-11-25 | ALP-EPC-20LCA-CM-OMM-0001 | 2029-04-18 | 364
G-OPS-HO-WS | 20LCA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-20LCA-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 20LCB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 2 | 2 | 2028-01-24 | ALP-M02-20LCB-ME-OMM-0001 | 2029-04-18 | 322
G-OPS-HO-WS | 20LCB | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-20LCB-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 20MAA | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-02-21 | ALP-IEC-20MAA-ME-OMM-0001 | 2029-04-18 | 302
G-OPS-HO-WS | 20MAA | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-20MAA-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 20MAB | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-02-21 | ALP-IEC-20MAA-ME-OMM-0001 | 2029-04-18 | 302
G-OPS-HO-WS | 20MAB | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-12 | ALP-EPC-20MAB-CM-MDB-0001 | 2029-04-18 | 222
G-OPS-HO-WS | 20MAG | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-02-21 | ALP-IEC-20MAA-ME-OMM-0001 | 2029-04-18 | 302
G-OPS-HO-WS | 20MAG | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-26 | ALP-EPC-20MAG-CM-MDB-0001 | 2029-04-18 | 212
G-OPS-HO-WS | 20MAJ | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-02-21 | ALP-IEC-20MAA-ME-OMM-0001 | 2029-04-18 | 302
G-OPS-HO-WS | 20MAJ | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-26 | ALP-EPC-20MAJ-CM-MDB-0001 | 2029-04-18 | 212
G-OPS-HO-WS | 20MAN | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2027-12-08 | ALP-EPC-20MAN-CM-OMM-0001 | 2029-04-18 | 355
G-OPS-HO-WS | 20MAN | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-26 | ALP-EPC-20MAN-CM-MDB-0001 | 2029-04-18 | 212
G-OPS-HO-WS | 20MAV | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-02-21 | ALP-IEC-20MAA-ME-OMM-0001 | 2029-04-18 | 302
G-OPS-HO-WS | 20MAV | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-26 | ALP-EPC-20MAV-CM-MDB-0001 | 2029-04-18 | 212
G-OPS-HO-WS | 20MAW | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-02-21 | ALP-IEC-20MAA-ME-OMM-0001 | 2029-04-18 | 302
G-OPS-HO-WS | 20MAW | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-26 | ALP-EPC-20MAW-CM-MDB-0001 | 2029-04-18 | 212
G-OPS-HO-WS | 20MAX | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC | 1 | 1 | 2028-02-21 | ALP-IEC-20MAA-ME-OMM-0001 | 2029-04-18 | 302
G-OPS-HO-WS | 20MAX | rule:DL-CM-TOD IFC | 1 | 1 | 2028-06-26 | ALP-EPC-20MAX-CM-MDB-0001 | 2029-04-18 | 212
G-OWN-BDP | 00000 | bdp:1 ACCEPTED | 15 | 15 | 2027-03-08 | ALP-EPC-00CJA-IC-BLK-0001 | 2027-04-02 | 19
G-OWN-BDP2 | 00000 | bdp:2 ACCEPTED | 10 | 10 | 2027-07-21 | ALP-EPC-20LCB-PR-PID-0001 | 2027-08-02 | 8
G-OWN-TO | 00000 | type:TRP@plant ACCEPTED | 11 | 11 | 2029-04-18 | ALP-EPC-00000-CM-TRP-0004 | 2029-04-18 | 0
G-OWN-TO | 00000 | id:ALP-EPC-00000-CM-OMM-0001 IFC | 1 | 1 | 2027-11-26 | ALP-EPC-00000-CM-OMM-0001 | 2029-04-18 | 363
G-OWN-TO | 00000 | id:ALP-EPC-00000-CM-LST-0002 IFC | 1 | 1 | 2027-12-01 | ALP-EPC-00000-CM-LST-0002 | 2029-04-18 | 360
G-OWN-TO | 00000 | type:LST@plant IFR | 24 | 23 | 2028-01-13 | ALP-EPC-00000-PI-LST-0001 | 2029-04-18 | 329
G-OWN-TOC | 00000 | id:ALP-EPC-00000-CM-CMP-0001 ACCEPTED | 1 | 1 | 2027-09-03 | ALP-EPC-00000-CM-CMP-0001 | 2028-08-21 | 251
G-OWN-TOC | 00000 | id:ALP-EPC-00000-CM-CMP-0002 ACCEPTED | 1 | 1 | 2027-08-11 | ALP-EPC-00000-CM-CMP-0002 | 2028-08-21 | 268
G-OWN-TOC | 00000 | id:ALP-EPC-00000-CM-CMP-0003 ACCEPTED | 1 | 1 | 2027-11-24 | ALP-EPC-00000-CM-CMP-0003 | 2028-08-21 | 193
G-OWN-TOC | 00000 | id:ALP-EPC-00000-CM-CMP-0004 ACCEPTED | 1 | 1 | 2027-09-01 | ALP-EPC-00000-CM-CMP-0004 | 2028-08-21 | 253
G-OWN-TOC | 00000 | id:ALP-EPC-00000-CM-CMP-0005 ACCEPTED | 1 | 1 | 2027-09-14 | ALP-EPC-00000-CM-CMP-0005 | 2028-08-21 | 244
G-OWN-TOC | 00000 | id:ALP-EPC-00000-CM-CMP-0006 ACCEPTED | 1 | 1 | 2027-09-16 | ALP-EPC-00000-CM-CMP-0006 | 2028-08-21 | 242
G-PRC-ENQ | MR-CV-001 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-CV-SPC-0003 | 2027-02-01 | 65
G-PRC-ENQ | MR-CV-001 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-CV-MRQ-0001 | 2027-02-01 | 65
G-PRC-ENQ | MR-CV-002 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-CV-SPC-0004 | 2026-11-23 | 15
G-PRC-ENQ | MR-CV-002 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-CV-MRQ-0002 | 2026-11-23 | 15
G-PRC-ENQ | MR-CV-003 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-CV-SPC-0005 | 2027-03-05 | 89
G-PRC-ENQ | MR-CV-003 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-CV-MRQ-0003 | 2027-03-05 | 89
G-PRC-ENQ | MR-EL-001 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00ACA-EL-SPC-0001 | 2026-12-15 | 31
G-PRC-ENQ | MR-EL-001 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00ACA-EL-MRQ-0001 | 2026-12-15 | 31
G-PRC-ENQ | MR-EL-002 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10BBT-EL-SPC-0001 | 2027-01-25 | 60
G-PRC-ENQ | MR-EL-002 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10BBT-EL-MRQ-0001 | 2027-01-25 | 60
G-PRC-ENQ | MR-EL-003 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00BBA-EL-SPC-0001 | 2026-12-07 | 25
G-PRC-ENQ | MR-EL-003 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00BBA-EL-MRQ-0001 | 2026-12-07 | 25
G-PRC-ENQ | MR-EL-004 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00BFT-EL-SPC-0001 | 2027-03-22 | 100
G-PRC-ENQ | MR-EL-004 | type:MRQ@epc IFR | 1 | 1 | 2026-11-23 | ALP-EPC-00BFT-EL-MRQ-0001 | 2027-03-22 | 85
G-PRC-ENQ | MR-EL-005 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00BFA-EL-SPC-0001 | 2027-01-18 | 55
G-PRC-ENQ | MR-EL-005 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00BFA-EL-MRQ-0001 | 2027-01-18 | 55
G-PRC-ENQ | MR-EL-006 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00XJA-EL-SPC-0001 | 2026-12-07 | 25
G-PRC-ENQ | MR-EL-006 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00XJA-EL-MRQ-0001 | 2026-12-07 | 25
G-PRC-ENQ | MR-EL-007 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00BRA-EL-SPC-0001 | 2027-03-22 | 100
G-PRC-ENQ | MR-EL-007 | type:MRQ@epc IFR | 1 | 1 | 2026-11-23 | ALP-EPC-00BRA-EL-MRQ-0001 | 2027-03-22 | 85
G-PRC-ENQ | MR-EL-008 | type:SPC@epc IFR | 1 | 1 | 2027-01-01 | ALP-EPC-00000-EL-SPC-0004 | 2027-05-03 | 86
G-PRC-ENQ | MR-EL-008 | type:MRQ@epc IFR | 1 | 1 | 2027-01-08 | ALP-EPC-00000-EL-MRQ-0001 | 2027-05-03 | 81
G-PRC-ENQ | MR-EL-009 | type:SPC@epc IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00000-EL-SPC-0005 | 2026-12-21 | 15
G-PRC-ENQ | MR-EL-009 | type:MRQ@epc IFR | 1 | 1 | 2026-12-07 | ALP-EPC-00000-EL-MRQ-0002 | 2026-12-21 | 10
G-PRC-ENQ | MR-EL-010 | type:SPC@epc IFR | 1 | 1 | 2027-02-25 | ALP-EPC-00BXA-GE-SPC-0001 | 2027-04-26 | 42
G-PRC-ENQ | MR-EL-010 | type:MRQ@epc IFR | 1 | 1 | 2027-03-04 | ALP-EPC-00BXA-GE-MRQ-0001 | 2027-04-26 | 37
G-PRC-ENQ | MR-EL-011 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-GE-SPC-0001 | 2026-11-09 | 5
G-PRC-ENQ | MR-EL-011 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-GE-MRQ-0001 | 2026-11-09 | 5
G-PRC-ENQ | MR-EL-012 | type:SPC@epc IFR | 1 | 1 | 2026-12-11 | ALP-EPC-00000-GE-SPC-0002 | 2027-09-06 | 191
G-PRC-ENQ | MR-EL-012 | type:MRQ@epc IFR | 1 | 1 | 2027-03-19 | ALP-EPC-00000-GE-MRQ-0002 | 2027-09-06 | 121
G-PRC-ENQ | MR-HV-001 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00SAA-HV-SPC-0001 | 2027-01-04 | 45
G-PRC-ENQ | MR-HV-001 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00SAA-HV-MRQ-0001 | 2027-01-04 | 45
G-PRC-ENQ | MR-IC-001 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00CJA-IC-SPC-0001 | 2026-11-30 | 20
G-PRC-ENQ | MR-IC-001 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00CJA-IC-MRQ-0001 | 2026-11-30 | 20
G-PRC-ENQ | MR-IC-002 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00CQA-IC-SPC-0001 | 2027-05-03 | 130
G-PRC-ENQ | MR-IC-002 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00CQA-IC-MRQ-0001 | 2027-05-03 | 130
G-PRC-ENQ | MR-IC-003 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00QUA-IC-SPC-0001 | 2027-05-03 | 130
G-PRC-ENQ | MR-IC-003 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00QUA-IC-MRQ-0001 | 2027-05-03 | 130
G-PRC-ENQ | MR-IC-004 | type:SPC@epc IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00000-IC-SPC-0003 | 2027-05-24 | 125
G-PRC-ENQ | MR-IC-004 | type:MRQ@epc IFR | 1 | 1 | 2026-12-07 | ALP-EPC-00000-IC-MRQ-0001 | 2027-05-24 | 120
G-PRC-ENQ | MR-IC-005 | type:SPC@epc IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00000-IC-SPC-0004 | 2027-03-15 | 75
G-PRC-ENQ | MR-IC-005 | type:MRQ@epc IFR | 1 | 1 | 2026-12-07 | ALP-EPC-00000-IC-MRQ-0002 | 2027-03-15 | 70
G-PRC-ENQ | MR-IC-006 | type:SPC@epc IFR | 1 | 1 | 2027-03-03 | ALP-EPC-00SGY-GE-SPC-0001 | 2027-05-24 | 58
G-PRC-ENQ | MR-IC-006 | type:MRQ@epc IFR | 1 | 1 | 2027-03-24 | ALP-EPC-00SGY-GE-MRQ-0001 | 2027-05-24 | 43
G-PRC-ENQ | MR-IC-007 | type:SPC@epc IFR | 1 | 1 | 2027-02-24 | ALP-EPC-00CYA-GE-SPC-0001 | 2027-05-24 | 63
G-PRC-ENQ | MR-IC-007 | type:MRQ@epc IFR | 1 | 1 | 2027-03-17 | ALP-EPC-00CYA-GE-MRQ-0001 | 2027-05-24 | 48
G-PRC-ENQ | MR-IC-008 | type:SPC@epc IFR | 1 | 1 | 2027-02-01 | ALP-EPC-00CJG-GE-SPC-0001 | 2027-04-12 | 50
G-PRC-ENQ | MR-IC-008 | type:MRQ@epc IFR | 1 | 1 | 2027-02-22 | ALP-EPC-00CJG-GE-MRQ-0001 | 2027-04-12 | 35
G-PRC-ENQ | MR-IC-009 | type:SPC@epc IFR | 1 | 1 | 2027-02-01 | ALP-EPC-00CKA-GE-SPC-0001 | 2027-04-12 | 50
G-PRC-ENQ | MR-IC-009 | type:MRQ@epc IFR | 1 | 1 | 2027-02-22 | ALP-EPC-00CKA-GE-MRQ-0001 | 2027-04-12 | 35
G-PRC-ENQ | MR-IC-010 | type:SPC@epc IFR | 1 | 1 | 2027-04-02 | ALP-EPC-00000-GE-SPC-0003 | 2027-10-25 | 146
G-PRC-ENQ | MR-IC-010 | type:MRQ@epc IFR | 1 | 1 | 2027-04-09 | ALP-EPC-00000-GE-MRQ-0003 | 2027-10-25 | 141
G-PRC-ENQ | MR-ME-001 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10LAC-ME-SPC-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-001 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10LAC-ME-MRQ-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-002 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-20LCB-ME-SPC-0001 | 2027-02-01 | 65
G-PRC-ENQ | MR-ME-002 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-20LCB-ME-MRQ-0001 | 2027-02-01 | 65
G-PRC-ENQ | MR-ME-003 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PAC-ME-SPC-0001 | 2026-11-23 | 15
G-PRC-ENQ | MR-ME-003 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PAC-ME-MRQ-0001 | 2026-11-23 | 15
G-PRC-ENQ | MR-ME-004 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PAA-ME-SPC-0001 | 2027-02-01 | 65
G-PRC-ENQ | MR-ME-004 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PAA-ME-MRQ-0001 | 2027-02-01 | 65
G-PRC-ENQ | MR-ME-005 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PBA-ME-SPC-0001 | 2027-02-01 | 65
G-PRC-ENQ | MR-ME-005 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PBA-ME-MRQ-0001 | 2027-02-01 | 65
G-PRC-ENQ | MR-ME-006 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PAH-ME-SPC-0001 | 2027-04-26 | 125
G-PRC-ENQ | MR-ME-006 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PAH-ME-MRQ-0001 | 2027-04-26 | 125
G-PRC-ENQ | MR-ME-007 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PGA-ME-SPC-0001 | 2027-01-25 | 60
G-PRC-ENQ | MR-ME-007 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00PGA-ME-MRQ-0001 | 2027-01-25 | 60
G-PRC-ENQ | MR-ME-008 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00QEA-ME-SPC-0001 | 2027-01-25 | 60
G-PRC-ENQ | MR-ME-008 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00QEA-ME-MRQ-0001 | 2027-01-25 | 60
G-PRC-ENQ | MR-ME-009 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00QHA-ME-SPC-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-009 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00QHA-ME-MRQ-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-010 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00QJA-ME-SPC-0001 | 2027-05-10 | 135
G-PRC-ENQ | MR-ME-010 | type:MRQ@epc IFR | 1 | 1 | 2027-03-25 | ALP-EPC-00QJA-ME-MRQ-0001 | 2027-05-10 | 32
G-PRC-ENQ | MR-ME-011 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00QCA-ME-SPC-0001 | 2027-04-05 | 110
G-PRC-ENQ | MR-ME-011 | type:MRQ@epc IFR | 1 | 1 | 2027-03-26 | ALP-EPC-00QCA-ME-MRQ-0001 | 2027-04-05 | 6
G-PRC-ENQ | MR-ME-012 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00LDA-ME-SPC-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-012 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00LDA-ME-MRQ-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-013 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00GHA-ME-SPC-0001 | 2027-03-29 | 105
G-PRC-ENQ | MR-ME-013 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00GHA-ME-MRQ-0001 | 2027-03-29 | 105
G-PRC-ENQ | MR-ME-014 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00GNA-ME-SPC-0001 | 2027-03-22 | 100
G-PRC-ENQ | MR-ME-014 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00GNA-ME-MRQ-0001 | 2027-03-22 | 100
G-PRC-ENQ | MR-ME-015 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00EKA-ME-SPC-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-015 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00EKA-ME-MRQ-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-016 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00EGA-ME-SPC-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-016 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00EGA-ME-MRQ-0001 | 2026-11-16 | 10
G-PRC-ENQ | MR-ME-017 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00EGB-ME-SPC-0001 | 2027-05-17 | 140
G-PRC-ENQ | MR-ME-017 | type:MRQ@epc IFR | 1 | 1 | 2026-11-23 | ALP-EPC-00EGB-ME-MRQ-0001 | 2027-05-17 | 125
G-PRC-ENQ | MR-ME-018 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10HSB-ME-SPC-0001 | 2027-01-25 | 60
G-PRC-ENQ | MR-ME-018 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10HSB-ME-MRQ-0001 | 2027-01-25 | 60
G-PRC-ENQ | MR-ME-019 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10HAN-ME-SPC-0001 | 2027-03-15 | 95
G-PRC-ENQ | MR-ME-019 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10HAN-ME-MRQ-0001 | 2027-03-15 | 95
G-PRC-ENQ | MR-ME-020 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00SGA-ME-SPC-0001 | 2027-01-11 | 50
G-PRC-ENQ | MR-ME-020 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00SGA-ME-MRQ-0001 | 2027-01-11 | 50
G-PRC-ENQ | MR-ME-021 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00SMA-ME-SPC-0001 | 2026-11-30 | 20
G-PRC-ENQ | MR-ME-021 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00SMA-ME-MRQ-0001 | 2026-11-30 | 20
G-PRC-ENQ | MR-ME-022 | type:SPC@epc IFR | 1 | 1 | 2027-04-16 | ALP-EPC-00000-GE-SPC-0004 | 2027-11-15 | 151
G-PRC-ENQ | MR-ME-022 | type:MRQ@epc IFR | 1 | 1 | 2027-04-23 | ALP-EPC-00000-GE-MRQ-0004 | 2027-11-15 | 146
G-PRC-ENQ | MR-ME-023 | type:SPC@epc IFR | 1 | 1 | 2027-06-18 | ALP-EPC-00000-GE-SPC-0005 | 2027-08-30 | 51
G-PRC-ENQ | MR-ME-023 | type:MRQ@epc IFR | 1 | 1 | 2027-06-25 | ALP-EPC-00000-GE-MRQ-0005 | 2027-08-30 | 46
G-PRC-ENQ | MR-ME-024 | type:SPC@epc IFR | 1 | 1 | 2027-06-16 | ALP-EPC-00UZF-GE-SPC-0001 | 2027-09-20 | 68
G-PRC-ENQ | MR-ME-024 | type:MRQ@epc IFR | 1 | 1 | 2027-06-23 | ALP-EPC-00UZF-GE-MRQ-0001 | 2027-09-20 | 63
G-PRC-ENQ | MR-PI-001 | type:SPC@epc IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00000-PI-SPC-0004 | 2027-01-04 | 25
G-PRC-ENQ | MR-PI-001 | type:MRQ@epc IFR | 1 | 1 | 2026-12-07 | ALP-EPC-00000-PI-MRQ-0001 | 2027-01-04 | 20
G-PRC-ENQ | MR-PI-002 | type:SPC@epc IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00000-PI-SPC-0005 | 2026-12-21 | 15
G-PRC-ENQ | MR-PI-002 | type:MRQ@epc IFR | 1 | 1 | 2026-12-07 | ALP-EPC-00000-PI-MRQ-0002 | 2026-12-21 | 10
G-PRC-ENQ | MR-PI-003 | type:SPC@epc IFR | 1 | 1 | 2026-12-17 | ALP-EPC-00000-PI-SPC-0006 | 2027-04-12 | 82
G-PRC-ENQ | MR-PI-003 | type:MRQ@epc IFR | 1 | 1 | 2026-12-24 | ALP-EPC-00000-PI-MRQ-0003 | 2027-04-12 | 77
G-PRC-ENQ | MR-PI-004 | type:SPC@epc IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00000-PI-SPC-0007 | 2026-12-21 | 15
G-PRC-ENQ | MR-PI-004 | type:MRQ@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-PI-MRQ-0004 | 2026-12-21 | 35
G-PRC-ENQ | MR-PI-005 | type:SPC@epc IFR | 1 | 1 | 2027-03-22 | ALP-EPC-00000-GE-SPC-0006 | 2027-07-12 | 80
G-PRC-ENQ | MR-PI-005 | type:MRQ@epc IFR | 1 | 1 | 2027-03-29 | ALP-EPC-00000-GE-MRQ-0006 | 2027-07-12 | 75
G-PRC-ENQ | MR-PI-006 | type:SPC@epc IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00000-GE-SPC-0007 | 2027-07-12 | 160
G-PRC-ENQ | MR-PI-006 | type:MRQ@epc IFR | 1 | 1 | 2026-12-07 | ALP-EPC-00000-GE-MRQ-0007 | 2027-07-12 | 155
G-PRC-ENQ | MR-PI-007 | type:SPC@epc IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00000-GE-SPC-0008 | 2027-06-14 | 140
G-PRC-ENQ | MR-PI-007 | type:MRQ@epc IFR | 1 | 1 | 2026-12-07 | ALP-EPC-00000-GE-MRQ-0008 | 2027-06-14 | 135
G-PRC-ENQ | MR-SS-001 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-SS-SPC-0002 | 2027-01-19 | 56
G-PRC-ENQ | MR-SS-001 | type:MRQ@epc IFR | 1 | 1 | 2026-11-09 | ALP-EPC-00000-SS-MRQ-0001 | 2027-01-19 | 51
G-PRC-ENQ | MR-SS-002 | type:SPC@epc IFR | 1 | 1 | 2026-11-02 | ALP-EPC-10HNE-SS-SPC-0001 | 2027-01-11 | 50
G-PRC-ENQ | MR-SS-002 | type:MRQ@epc IFR | 1 | 1 | 2026-11-09 | ALP-EPC-10HNE-SS-MRQ-0001 | 2027-01-11 | 45
G-PRC-FAB | MR-EL-001 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-02-09 | ALP-E01-00ACA-ME-GAD-0001 | 2027-05-10 | 64
G-PRC-FAB | MR-EL-001 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-02-23 | ALP-E01-00ACA-ME-CAL-0001 | 2027-05-10 | 54
G-PRC-FAB | MR-EL-001 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-02-09 | ALP-E01-00ACA-CV-CAL-0001 | 2027-05-10 | 64
G-PRC-FAB | MR-EL-001 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-02-02 | ALP-E01-00ACA-ME-ITP-0001 | 2027-05-10 | 69
G-PRC-FAB | MR-EL-002 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-15 | ALP-E02-10BBT-ME-GAD-0001 | 2027-07-26 | 72
G-PRC-FAB | MR-EL-002 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-29 | ALP-E02-10BBT-ME-CAL-0001 | 2027-07-26 | 62
G-PRC-FAB | MR-EL-002 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-E02-10BBT-CV-CAL-0001 | 2027-07-26 | 72
G-PRC-FAB | MR-EL-002 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-08 | ALP-E02-10BBT-ME-ITP-0001 | 2027-07-26 | 77
G-PRC-FAB | MR-EL-003 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-08 | ALP-E03-00BBA-ME-GAD-0001 | 2027-05-26 | 57
G-PRC-FAB | MR-EL-003 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-19 | ALP-E03-00BBA-ME-CAL-0001 | 2027-05-26 | 48
G-PRC-FAB | MR-EL-003 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-02 | ALP-E03-00BBA-ME-ITP-0001 | 2027-05-26 | 61
G-PRC-FAB | MR-EL-004 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-13 | ALP-E04-00BFT-ME-GAD-0001 | 2027-07-21 | 71
G-PRC-FAB | MR-EL-004 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-21 | ALP-E04-00BFT-ME-CAL-0001 | 2027-07-21 | 65
G-PRC-FAB | MR-EL-004 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-07 | ALP-E04-00BFT-ME-ITP-0001 | 2027-07-21 | 75
G-PRC-FAB | MR-EL-005 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-22 | ALP-E05-00BFA-ME-GAD-0001 | 2027-06-21 | 65
G-PRC-FAB | MR-EL-005 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-01 | ALP-E05-00BFA-ME-CAL-0001 | 2027-06-21 | 57
G-PRC-FAB | MR-EL-005 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-18 | ALP-E05-00BFA-ME-ITP-0001 | 2027-06-21 | 67
G-PRC-FAB | MR-EL-006 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-08 | ALP-E06-00XJA-ME-GAD-0001 | 2027-05-26 | 57
G-PRC-FAB | MR-EL-006 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-19 | ALP-E06-00XJA-ME-CAL-0001 | 2027-05-26 | 48
G-PRC-FAB | MR-EL-006 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-08 | ALP-E06-00XJA-CV-CAL-0001 | 2027-05-26 | 57
G-PRC-FAB | MR-EL-006 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-02 | ALP-E06-00XJA-ME-ITP-0001 | 2027-05-26 | 61
G-PRC-FAB | MR-EL-007 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-21 | ALP-E07-00BRA-ME-GAD-0001 | 2027-07-21 | 65
G-PRC-FAB | MR-EL-007 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-29 | ALP-E07-00BRA-ME-CAL-0001 | 2027-07-21 | 59
G-PRC-FAB | MR-EL-007 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-E07-00BRA-ME-ITP-0001 | 2027-07-21 | 69
G-PRC-FAB | MR-EL-010 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-06-08 | ALP-E10-00BXA-ME-ITP-0001 | 2027-08-04 | 41
G-PRC-FAB | MR-EL-011 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2026-12-07 | ALP-E11-00000-ME-ITP-0001 | 2026-12-08 | 1
G-PRC-FAB | MR-EL-101 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 1 | 2026-12-28 | ALP-IEC-10MKA-ME-GAD-0001 | 2027-03-18 | 58
G-PRC-FAB | MR-EL-101 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-03-01 | ALP-IEC-10MKA-PR-PID-0001 | 2027-03-18 | 13
G-PRC-FAB | MR-EL-101 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-01-11 | ALP-IEC-10MKA-ME-CAL-0001 | 2027-03-18 | 48
G-PRC-FAB | MR-EL-101 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2026-12-28 | ALP-IEC-10MKA-CV-CAL-0001 | 2027-03-18 | 58
G-PRC-FAB | MR-EL-101 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2026-12-21 | ALP-IEC-10MKA-ME-ITP-0001 | 2027-03-18 | 63
G-PRC-FAB | MR-EL-102 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 0 | 2026-10-12 | ALP-IEC-10BAT-EL-GAD-0001 | 2027-03-22 | 115
G-PRC-FAB | MR-EL-102 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-01-11 | ALP-IEC-10BAT-ME-CAL-0001 | 2027-03-22 | 50
G-PRC-FAB | MR-EL-102 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2026-12-28 | ALP-IEC-10BAT-CV-CAL-0001 | 2027-03-22 | 60
G-PRC-FAB | MR-EL-102 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2026-12-21 | ALP-IEC-10BAT-ME-ITP-0001 | 2027-03-22 | 65
G-PRC-FAB | MR-HV-001 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-15 | ALP-H01-00SAA-ME-GAD-0001 | 2027-06-07 | 60
G-PRC-FAB | MR-HV-001 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-12 | ALP-H01-00SAA-PR-PID-0001 | 2027-06-07 | 40
G-PRC-FAB | MR-HV-001 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-25 | ALP-H01-00SAA-ME-CAL-0001 | 2027-06-07 | 52
G-PRC-FAB | MR-HV-001 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-11 | ALP-H01-00SAA-ME-ITP-0001 | 2027-06-07 | 62
G-PRC-FAB | MR-IC-001 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-18 | ALP-I01-00CJA-ME-GAD-0001 | 2027-06-07 | 57
G-PRC-FAB | MR-IC-001 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-01 | ALP-I01-00CJA-ME-CAL-0001 | 2027-06-07 | 47
G-PRC-FAB | MR-IC-001 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-11 | ALP-I01-00CJA-ME-ITP-0001 | 2027-06-07 | 62
G-PRC-FAB | MR-IC-002 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-05-04 | ALP-I02-00CQA-ME-GAD-0001 | 2027-10-04 | 109
G-PRC-FAB | MR-IC-002 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-05-14 | ALP-I02-00CQA-ME-CAL-0001 | 2027-10-04 | 101
G-PRC-FAB | MR-IC-002 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-30 | ALP-I02-00CQA-ME-ITP-0001 | 2027-10-04 | 111
G-PRC-FAB | MR-IC-003 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-05-06 | ALP-I03-00QUA-ME-GAD-0001 | 2027-10-04 | 107
G-PRC-FAB | MR-IC-003 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-06-03 | ALP-I03-00QUA-PR-PID-0001 | 2027-10-04 | 87
G-PRC-FAB | MR-IC-003 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-05-18 | ALP-I03-00QUA-ME-CAL-0001 | 2027-10-04 | 99
G-PRC-FAB | MR-IC-003 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-05-04 | ALP-I03-00QUA-ME-ITP-0001 | 2027-10-04 | 109
G-PRC-FAB | MR-IC-006 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-07-05 | ALP-I06-00SGY-ME-GAD-0001 | 2027-09-13 | 50
G-PRC-FAB | MR-IC-006 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-07-12 | ALP-I06-00SGY-ME-CAL-0001 | 2027-09-13 | 45
G-PRC-FAB | MR-IC-006 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-06-28 | ALP-I06-00SGY-ME-ITP-0001 | 2027-09-13 | 55
G-PRC-FAB | MR-IC-007 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-06-28 | ALP-I07-00CYA-ME-GAD-0001 | 2027-09-13 | 55
G-PRC-FAB | MR-IC-007 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-07-05 | ALP-I07-00CYA-ME-CAL-0001 | 2027-09-13 | 50
G-PRC-FAB | MR-IC-007 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-06-21 | ALP-I07-00CYA-ME-ITP-0001 | 2027-09-13 | 60
G-PRC-FAB | MR-IC-008 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-06-10 | ALP-I08-00CJG-ME-GAD-0001 | 2027-08-18 | 49
G-PRC-FAB | MR-IC-008 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-06-18 | ALP-I08-00CJG-ME-CAL-0001 | 2027-08-18 | 43
G-PRC-FAB | MR-IC-008 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-06-04 | ALP-I08-00CJG-ME-ITP-0001 | 2027-08-18 | 53
G-PRC-FAB | MR-IC-009 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-07-08 | ALP-I09-00CKA-ME-GAD-0001 | 2027-10-11 | 67
G-PRC-FAB | MR-IC-009 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-07-22 | ALP-I09-00CKA-ME-CAL-0001 | 2027-10-11 | 57
G-PRC-FAB | MR-IC-009 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-07-01 | ALP-I09-00CKA-ME-ITP-0001 | 2027-10-11 | 72
G-PRC-FAB | MR-IC-101 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2026-12-28 | ALP-IEC-10MBY-ME-GAD-0001 | 2027-02-22 | 40
G-PRC-FAB | MR-IC-101 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-01-11 | ALP-IEC-10MBY-ME-CAL-0001 | 2027-02-22 | 30
G-PRC-FAB | MR-IC-101 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2026-12-21 | ALP-IEC-10MBY-ME-ITP-0001 | 2027-02-22 | 45
G-PRC-FAB | MR-ME-001 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-11 | ALP-M01-10LAC-ME-GAD-0001 | 2027-05-17 | 47
G-PRC-FAB | MR-ME-001 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-M01-10LAC-PR-PID-0001 | 2027-05-17 | 22
G-PRC-FAB | MR-ME-001 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-25 | ALP-M01-10LAC-ME-CAL-0001 | 2027-05-17 | 37
G-PRC-FAB | MR-ME-001 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-11 | ALP-M01-10LAC-CV-CAL-0001 | 2027-05-17 | 47
G-PRC-FAB | MR-ME-001 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-04 | ALP-M01-10LAC-ME-ITP-0001 | 2027-05-17 | 52
G-PRC-FAB | MR-ME-002 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-14 | ALP-M02-20LCB-ME-GAD-0001 | 2027-07-21 | 70
G-PRC-FAB | MR-ME-002 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-05-18 | ALP-M02-20LCB-PR-PID-0001 | 2027-07-21 | 46
G-PRC-FAB | MR-ME-002 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-27 | ALP-M02-20LCB-ME-CAL-0001 | 2027-07-21 | 61
G-PRC-FAB | MR-ME-002 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-04-14 | ALP-M02-20LCB-CV-CAL-0001 | 2027-07-21 | 70
G-PRC-FAB | MR-ME-002 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-08 | ALP-M02-20LCB-ME-ITP-0001 | 2027-07-21 | 74
G-PRC-FAB | MR-ME-003 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-11 | ALP-M03-00PAC-ME-GAD-0001 | 2027-06-03 | 60
G-PRC-FAB | MR-ME-003 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-M03-00PAC-PR-PID-0001 | 2027-06-03 | 35
G-PRC-FAB | MR-ME-003 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-25 | ALP-M03-00PAC-ME-CAL-0001 | 2027-06-03 | 50
G-PRC-FAB | MR-ME-003 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-11 | ALP-M03-00PAC-CV-CAL-0001 | 2027-06-03 | 60
G-PRC-FAB | MR-ME-003 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-04 | ALP-M03-00PAC-ME-ITP-0001 | 2027-06-03 | 65
G-PRC-FAB | MR-ME-004 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-06 | ALP-M04-00PAA-ME-GAD-0001 | 2027-07-21 | 76
G-PRC-FAB | MR-ME-004 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-05-10 | ALP-M04-00PAA-PR-PID-0001 | 2027-07-21 | 52
G-PRC-FAB | MR-ME-004 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-19 | ALP-M04-00PAA-ME-CAL-0001 | 2027-07-21 | 67
G-PRC-FAB | MR-ME-004 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-04-06 | ALP-M04-00PAA-CV-CAL-0001 | 2027-07-21 | 76
G-PRC-FAB | MR-ME-004 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-31 | ALP-M04-00PAA-ME-ITP-0001 | 2027-07-21 | 80
G-PRC-FAB | MR-ME-005 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-07 | ALP-M05-00PBA-ME-GAD-0001 | 2027-07-21 | 75
G-PRC-FAB | MR-ME-005 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-05-11 | ALP-M05-00PBA-PR-PID-0001 | 2027-07-21 | 51
G-PRC-FAB | MR-ME-005 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-20 | ALP-M05-00PBA-ME-CAL-0001 | 2027-07-21 | 66
G-PRC-FAB | MR-ME-005 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-04-07 | ALP-M05-00PBA-CV-CAL-0001 | 2027-07-21 | 75
G-PRC-FAB | MR-ME-005 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-01 | ALP-M05-00PBA-ME-ITP-0001 | 2027-07-21 | 79
G-PRC-FAB | MR-ME-006 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-30 | ALP-M06-00PAH-ME-GAD-0001 | 2027-09-27 | 106
G-PRC-FAB | MR-ME-006 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-05-28 | ALP-M06-00PAH-PR-PID-0001 | 2027-09-27 | 86
G-PRC-FAB | MR-ME-006 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-05-12 | ALP-M06-00PAH-ME-CAL-0001 | 2027-09-27 | 98
G-PRC-FAB | MR-ME-006 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-28 | ALP-M06-00PAH-ME-ITP-0001 | 2027-09-27 | 108
G-PRC-FAB | MR-ME-007 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-05 | ALP-M07-00PGA-ME-GAD-0001 | 2027-06-28 | 60
G-PRC-FAB | MR-ME-007 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-05-03 | ALP-M07-00PGA-PR-PID-0001 | 2027-06-28 | 40
G-PRC-FAB | MR-ME-007 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-M07-00PGA-ME-CAL-0001 | 2027-06-28 | 52
G-PRC-FAB | MR-ME-007 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-04-05 | ALP-M07-00PGA-CV-CAL-0001 | 2027-06-28 | 60
G-PRC-FAB | MR-ME-007 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-01 | ALP-M07-00PGA-ME-ITP-0001 | 2027-06-28 | 62
G-PRC-FAB | MR-ME-008 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-05 | ALP-M08-00QEA-ME-GAD-0001 | 2027-06-28 | 60
G-PRC-FAB | MR-ME-008 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-05-03 | ALP-M08-00QEA-PR-PID-0001 | 2027-06-28 | 40
G-PRC-FAB | MR-ME-008 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-M08-00QEA-ME-CAL-0001 | 2027-06-28 | 52
G-PRC-FAB | MR-ME-008 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-04-05 | ALP-M08-00QEA-CV-CAL-0001 | 2027-06-28 | 60
G-PRC-FAB | MR-ME-008 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-01 | ALP-M08-00QEA-ME-ITP-0001 | 2027-06-28 | 62
G-PRC-FAB | MR-ME-009 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-11 | ALP-M09-00QHA-ME-GAD-0001 | 2027-05-17 | 47
G-PRC-FAB | MR-ME-009 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-M09-00QHA-PR-PID-0001 | 2027-05-17 | 22
G-PRC-FAB | MR-ME-009 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-25 | ALP-M09-00QHA-ME-CAL-0001 | 2027-05-17 | 37
G-PRC-FAB | MR-ME-009 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-11 | ALP-M09-00QHA-CV-CAL-0001 | 2027-05-17 | 47
G-PRC-FAB | MR-ME-009 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-04 | ALP-M09-00QHA-ME-ITP-0001 | 2027-05-17 | 52
G-PRC-FAB | MR-ME-010 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-06-22 | ALP-M10-00QJA-ME-GAD-0001 | 2027-08-23 | 44
G-PRC-FAB | MR-ME-010 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-07-06 | ALP-M10-00QJA-PR-PID-0001 | 2027-08-23 | 34
G-PRC-FAB | MR-ME-010 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-06-29 | ALP-M10-00QJA-ME-CAL-0001 | 2027-08-23 | 39
G-PRC-FAB | MR-ME-010 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-06-15 | ALP-M10-00QJA-ME-ITP-0001 | 2027-08-23 | 49
G-PRC-FAB | MR-ME-011 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-06-23 | ALP-M11-00QCA-ME-GAD-0001 | 2027-07-28 | 25
G-PRC-FAB | MR-ME-011 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-07-15 | ALP-M11-00QCA-PR-PID-0001 | 2027-07-28 | 9
G-PRC-FAB | MR-ME-011 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-07-01 | ALP-M11-00QCA-ME-CAL-0001 | 2027-07-28 | 19
G-PRC-FAB | MR-ME-011 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-06-17 | ALP-M11-00QCA-ME-ITP-0001 | 2027-07-28 | 29
G-PRC-FAB | MR-ME-012 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-25 | ALP-M12-00GBA-ME-GAD-0001 | 2027-06-10 | 55
G-PRC-FAB | MR-ME-012 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-29 | ALP-M12-00GBA-PR-PID-0001 | 2027-06-10 | 30
G-PRC-FAB | MR-ME-012 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-08 | ALP-M12-00GBA-ME-CAL-0001 | 2027-06-10 | 45
G-PRC-FAB | MR-ME-012 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-25 | ALP-M12-00GBA-CV-CAL-0001 | 2027-06-10 | 55
G-PRC-FAB | MR-ME-012 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-18 | ALP-M12-00GBA-ME-ITP-0001 | 2027-06-10 | 60
G-PRC-FAB | MR-ME-013 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-05 | ALP-M13-00GHA-ME-GAD-0001 | 2027-07-28 | 103
G-PRC-FAB | MR-ME-013 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-03-29 | ALP-M13-00GHA-PR-PID-0001 | 2027-07-28 | 87
G-PRC-FAB | MR-ME-013 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-15 | ALP-M13-00GHA-ME-CAL-0001 | 2027-07-28 | 97
G-PRC-FAB | MR-ME-013 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-05 | ALP-M13-00GHA-CV-CAL-0001 | 2027-07-28 | 103
G-PRC-FAB | MR-ME-013 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-01 | ALP-M13-00GHA-ME-ITP-0001 | 2027-07-28 | 107
G-PRC-FAB | MR-ME-014 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-15 | ALP-M14-00GNA-ME-GAD-0001 | 2027-08-23 | 115
G-PRC-FAB | MR-ME-014 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-12 | ALP-M14-00GNA-PR-PID-0001 | 2027-08-23 | 95
G-PRC-FAB | MR-ME-014 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-25 | ALP-M14-00GNA-ME-CAL-0001 | 2027-08-23 | 107
G-PRC-FAB | MR-ME-014 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-15 | ALP-M14-00GNA-CV-CAL-0001 | 2027-08-23 | 115
G-PRC-FAB | MR-ME-014 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-11 | ALP-M14-00GNA-ME-ITP-0001 | 2027-08-23 | 117
G-PRC-FAB | MR-ME-015 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-11 | ALP-M15-00EKA-ME-GAD-0001 | 2027-05-17 | 47
G-PRC-FAB | MR-ME-015 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-15 | ALP-M15-00EKA-PR-PID-0001 | 2027-05-17 | 22
G-PRC-FAB | MR-ME-015 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-25 | ALP-M15-00EKA-ME-CAL-0001 | 2027-05-17 | 37
G-PRC-FAB | MR-ME-015 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-11 | ALP-M15-00EKA-CV-CAL-0001 | 2027-05-17 | 47
G-PRC-FAB | MR-ME-015 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-04 | ALP-M15-00EKA-ME-ITP-0001 | 2027-05-17 | 52
G-PRC-FAB | MR-ME-016 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-08 | ALP-M16-00EGA-ME-GAD-0001 | 2027-05-05 | 42
G-PRC-FAB | MR-ME-016 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-09 | ALP-M16-00EGA-PR-PID-0001 | 2027-05-05 | 18
G-PRC-FAB | MR-ME-016 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-19 | ALP-M16-00EGA-ME-CAL-0001 | 2027-05-05 | 33
G-PRC-FAB | MR-ME-016 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-08 | ALP-M16-00EGA-CV-CAL-0001 | 2027-05-05 | 42
G-PRC-FAB | MR-ME-016 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-02 | ALP-M16-00EGA-ME-ITP-0001 | 2027-05-05 | 46
G-PRC-FAB | MR-ME-018 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-04-07 | ALP-M18-10HSB-ME-GAD-0001 | 2027-06-28 | 58
G-PRC-FAB | MR-ME-018 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-05-05 | ALP-M18-10HSB-PR-PID-0001 | 2027-06-28 | 38
G-PRC-FAB | MR-ME-018 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-19 | ALP-M18-10HSB-ME-CAL-0001 | 2027-06-28 | 50
G-PRC-FAB | MR-ME-018 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-04-07 | ALP-M18-10HSB-CV-CAL-0001 | 2027-06-28 | 58
G-PRC-FAB | MR-ME-018 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-04-05 | ALP-M18-10HSB-ME-ITP-0001 | 2027-06-28 | 60
G-PRC-FAB | MR-ME-019 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-29 | ALP-M19-10HAN-ME-GAD-0001 | 2027-07-14 | 77
G-PRC-FAB | MR-ME-019 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-20 | ALP-M19-10HAN-PR-PID-0001 | 2027-07-14 | 61
G-PRC-FAB | MR-ME-019 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-04-06 | ALP-M19-10HAN-ME-CAL-0001 | 2027-07-14 | 71
G-PRC-FAB | MR-ME-019 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-29 | ALP-M19-10HAN-CV-CAL-0001 | 2027-07-14 | 77
G-PRC-FAB | MR-ME-019 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-23 | ALP-M19-10HAN-ME-ITP-0001 | 2027-07-14 | 81
G-PRC-FAB | MR-ME-020 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-17 | ALP-M20-00SGA-ME-GAD-0001 | 2027-06-18 | 67
G-PRC-FAB | MR-ME-020 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-04-16 | ALP-M20-00SGA-PR-PID-0001 | 2027-06-18 | 45
G-PRC-FAB | MR-ME-020 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-29 | ALP-M20-00SGA-ME-CAL-0001 | 2027-06-18 | 59
G-PRC-FAB | MR-ME-020 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-17 | ALP-M20-00SGA-CV-CAL-0001 | 2027-06-18 | 67
G-PRC-FAB | MR-ME-020 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-12 | ALP-M20-00SGA-ME-ITP-0001 | 2027-06-18 | 70
G-PRC-FAB | MR-ME-021 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 2 | 2027-03-08 | ALP-M21-00SMA-ME-GAD-0001 | 2027-05-19 | 52
G-PRC-FAB | MR-ME-021 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-03-19 | ALP-M21-00SMA-ME-CAL-0001 | 2027-05-19 | 43
G-PRC-FAB | MR-ME-021 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-03-08 | ALP-M21-00SMA-CV-CAL-0001 | 2027-05-19 | 52
G-PRC-FAB | MR-ME-021 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-03-02 | ALP-M21-00SMA-ME-ITP-0001 | 2027-05-19 | 56
G-PRC-FAB | MR-ME-101 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 0 | 2026-10-12 | ALP-IEC-10MBA-ME-GAD-0001 | 2027-03-22 | 115
G-PRC-FAB | MR-ME-101 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-02-15 | ALP-IEC-10MBA-PR-PID-0001 | 2027-03-22 | 25
G-PRC-FAB | MR-ME-101 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-01-11 | ALP-IEC-10MBA-ME-CAL-0001 | 2027-03-22 | 50
G-PRC-FAB | MR-ME-101 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2026-12-28 | ALP-IEC-10MBA-CV-CAL-0001 | 2027-03-22 | 60
G-PRC-FAB | MR-ME-101 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2027-02-15 | ALP-IEC-10MBA-ME-ITP-0001 | 2027-03-22 | 25
G-PRC-FAB | MR-ME-102 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 0 | 2026-10-12 | ALP-IEC-10HAA-ME-GAD-0001 | 2027-03-16 | 111
G-PRC-FAB | MR-ME-102 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-02-15 | ALP-IEC-10HAA-PR-PID-0001 | 2027-03-16 | 21
G-PRC-FAB | MR-ME-102 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-01-11 | ALP-IEC-10HAA-ME-CAL-0001 | 2027-03-16 | 46
G-PRC-FAB | MR-ME-102 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2026-12-28 | ALP-IEC-10HAA-CV-CAL-0001 | 2027-03-16 | 56
G-PRC-FAB | MR-ME-102 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2026-12-21 | ALP-IEC-10HAA-ME-ITP-0001 | 2027-03-16 | 61
G-PRC-FAB | MR-ME-103 | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED | 2 | 0 | 2026-10-12 | ALP-IEC-20MAA-ME-GAD-0001 | 2027-04-07 | 127
G-PRC-FAB | MR-ME-103 | rule:DL-V-PID? ACCEPTED | 1 | 1 | 2027-03-01 | ALP-IEC-20MAA-PR-PID-0001 | 2027-04-07 | 27
G-PRC-FAB | MR-ME-103 | rule:DL-V-CAL? ACCEPTED | 1 | 1 | 2027-01-11 | ALP-IEC-20MAA-ME-CAL-0001 | 2027-04-07 | 62
G-PRC-FAB | MR-ME-103 | rule:DL-V-FDL? ACCEPTED | 1 | 1 | 2027-01-11 | ALP-IEC-20MAA-CV-CAL-0001 | 2027-04-07 | 62
G-PRC-FAB | MR-ME-103 | rule:DL-V-ITP? ACCEPTED | 1 | 1 | 2026-12-21 | ALP-IEC-20MAA-ME-ITP-0001 | 2027-04-07 | 77
G-PRC-FAT | MR-EL-001 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-09-21 | ALP-E01-00ACA-ME-TST-0001 | 2027-11-16 | 40
G-PRC-FAT | MR-EL-002 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-09-02 | ALP-E02-10BBT-ME-TST-0001 | 2027-10-28 | 40
G-PRC-FAT | MR-EL-003 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-01 | ALP-E03-00BBA-ME-TST-0001 | 2027-08-26 | 40
G-PRC-FAT | MR-EL-004 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-08 | ALP-E04-00BFT-ME-TST-0001 | 2027-08-03 | 40
G-PRC-FAT | MR-EL-005 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-10 | ALP-E05-00BFA-ME-TST-0001 | 2027-08-05 | 40
G-PRC-FAT | MR-EL-006 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-01 | ALP-E06-00XJA-ME-TST-0001 | 2027-08-26 | 40
G-PRC-FAT | MR-EL-007 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-16 | ALP-E07-00BRA-ME-TST-0001 | 2027-08-11 | 40
G-PRC-FAT | MR-EL-010 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-08 | ALP-E10-00BXA-ME-TST-0001 | 2027-08-03 | 40
G-PRC-FAT | MR-EL-011 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2026-11-02 | ALP-E11-00000-ME-TST-0001 | 2026-12-14 | 30
G-PRC-FAT | MR-EL-101 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-19 | ALP-IEC-10MKA-ME-TST-0001 | 2027-09-13 | 40
G-PRC-FAT | MR-EL-102 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-26 | ALP-IEC-10BAT-ME-TST-0001 | 2027-09-20 | 40
G-PRC-FAT | MR-HV-001 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-03 | ALP-H01-00SAA-ME-TST-0001 | 2027-07-29 | 40
G-PRC-FAT | MR-IC-001 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-08-05 | ALP-I01-00CJA-ME-TST-0001 | 2027-09-30 | 40
G-PRC-FAT | MR-IC-002 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-23 | ALP-I02-00CQA-ME-TST-0001 | 2027-09-17 | 40
G-PRC-FAT | MR-IC-003 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-27 | ALP-I03-00QUA-ME-TST-0001 | 2027-09-21 | 40
G-PRC-FAT | MR-IC-006 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-26 | ALP-I06-00SGY-ME-TST-0001 | 2027-09-20 | 40
G-PRC-FAT | MR-IC-007 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-19 | ALP-I07-00CYA-ME-TST-0001 | 2027-09-13 | 40
G-PRC-FAT | MR-IC-008 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-08-05 | ALP-I08-00CJG-ME-TST-0001 | 2027-09-30 | 40
G-PRC-FAT | MR-IC-009 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-11-25 | ALP-I09-00CKA-ME-TST-0001 | 2028-01-20 | 40
G-PRC-FAT | MR-IC-101 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-05-17 | ALP-IEC-10MBY-ME-TST-0001 | 2027-07-12 | 40
G-PRC-FAT | MR-ME-001 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-29 | ALP-M01-10LAC-ME-TST-0001 | 2027-09-23 | 40
G-PRC-FAT | MR-ME-002 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-08-09 | ALP-M02-20LCB-ME-TST-0001 | 2027-10-04 | 40
G-PRC-FAT | MR-ME-003 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-08-26 | ALP-M03-00PAC-ME-TST-0001 | 2027-10-21 | 40
G-PRC-FAT | MR-ME-004 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-30 | ALP-M04-00PAA-ME-TST-0001 | 2027-09-24 | 40
G-PRC-FAT | MR-ME-005 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-08-02 | ALP-M05-00PBA-ME-TST-0001 | 2027-09-27 | 40
G-PRC-FAT | MR-ME-006 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-21 | ALP-M06-00PAH-ME-TST-0001 | 2027-09-15 | 40
G-PRC-FAT | MR-ME-007 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-24 | ALP-M07-00PGA-ME-TST-0001 | 2027-08-19 | 40
G-PRC-FAT | MR-ME-008 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-24 | ALP-M08-00QEA-ME-TST-0001 | 2027-08-19 | 40
G-PRC-FAT | MR-ME-009 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-29 | ALP-M09-00QHA-ME-TST-0001 | 2027-09-23 | 40
G-PRC-FAT | MR-ME-010 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-13 | ALP-M10-00QJA-ME-TST-0001 | 2027-09-07 | 40
G-PRC-FAT | MR-ME-011 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-08-18 | ALP-M11-00QCA-ME-TST-0001 | 2027-10-13 | 40
G-PRC-FAT | MR-ME-012 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-09-09 | ALP-M12-00GBA-ME-TST-0001 | 2027-11-04 | 40
G-PRC-FAT | MR-ME-013 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-04-30 | ALP-M13-00GHA-ME-TST-0001 | 2027-06-25 | 40
G-PRC-FAT | MR-ME-014 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-03 | ALP-M14-00GNA-ME-TST-0001 | 2027-07-29 | 40
G-PRC-FAT | MR-ME-015 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-29 | ALP-M15-00EKA-ME-TST-0001 | 2027-09-23 | 40
G-PRC-FAT | MR-ME-016 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-01 | ALP-M16-00EGA-ME-TST-0001 | 2027-08-26 | 40
G-PRC-FAT | MR-ME-018 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-28 | ALP-M18-10HSB-ME-TST-0001 | 2027-08-23 | 40
G-PRC-FAT | MR-ME-019 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-05-24 | ALP-M19-10HAN-ME-TST-0001 | 2027-07-19 | 40
G-PRC-FAT | MR-ME-020 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-06-17 | ALP-M20-00SGA-ME-TST-0001 | 2027-08-12 | 40
G-PRC-FAT | MR-ME-021 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-01 | ALP-M21-00SMA-ME-TST-0001 | 2027-08-26 | 40
G-PRC-FAT | MR-ME-101 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-26 | ALP-IEC-10MBA-ME-TST-0001 | 2027-09-20 | 40
G-PRC-FAT | MR-ME-102 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-07-12 | ALP-IEC-10HAA-ME-TST-0001 | 2027-09-06 | 40
G-PRC-FAT | MR-ME-103 | rule:DL-V-FAT ACCEPTED | 1 | 1 | 2027-09-06 | ALP-IEC-20MAA-ME-TST-0001 | 2027-11-01 | 40
G-PRC-PO | MR-CV-001 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00000-CV-SPC-0003 | 2027-03-22 | 75
G-PRC-PO | MR-CV-001 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00000-CV-MRQ-0001 | 2027-03-22 | 97
G-PRC-PO | MR-CV-001 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-14 | ALP-EPC-00000-GE-RPT-0001 | 2027-03-22 | 47
G-PRC-PO | MR-CV-002 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00000-CV-SPC-0004 | 2027-01-11 | 25
G-PRC-PO | MR-CV-002 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00000-CV-MRQ-0002 | 2027-01-11 | 47
G-PRC-PO | MR-CV-002 | rule:DL-MR-TBE IFR | 1 | 1 | 2026-12-24 | ALP-EPC-00000-GE-RPT-0002 | 2027-01-11 | 12
G-PRC-PO | MR-CV-003 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00000-CV-SPC-0005 | 2027-05-14 | 114
G-PRC-PO | MR-CV-003 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00000-CV-MRQ-0003 | 2027-05-14 | 136
G-PRC-PO | MR-CV-003 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-11 | ALP-EPC-00UPA-GE-RPT-0001 | 2027-05-14 | 46
G-PRC-PO | MR-EL-001 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00ACA-EL-SPC-0001 | 2026-12-15 | 6
G-PRC-PO | MR-EL-001 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00ACA-EL-MRQ-0001 | 2026-12-15 | 28
G-PRC-PO | MR-EL-001 | rule:DL-MR-TBE IFR | 1 | 1 | 2026-11-26 | ALP-EPC-00ACA-GE-RPT-0001 | 2026-12-15 | 13
G-PRC-PO | MR-EL-001 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00ACA-EL-ITP-0001 | 2026-12-15 | 21
G-PRC-PO | MR-EL-002 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-10BBT-EL-SPC-0001 | 2027-04-05 | 85
G-PRC-PO | MR-EL-002 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-10BBT-EL-MRQ-0001 | 2027-04-05 | 107
G-PRC-PO | MR-EL-002 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-18 | ALP-EPC-10BBT-GE-RPT-0001 | 2027-04-05 | 32
G-PRC-PO | MR-EL-002 | type:ITP@epc? IFR | 1 | 1 | 2026-12-02 | ALP-EPC-10BBT-EL-ITP-0001 | 2027-04-05 | 88
G-PRC-PO | MR-EL-003 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00BBA-EL-SPC-0001 | 2027-02-15 | 50
G-PRC-PO | MR-EL-003 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00BBA-EL-MRQ-0001 | 2027-02-15 | 72
G-PRC-PO | MR-EL-003 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-07 | ALP-EPC-00BBA-GE-RPT-0001 | 2027-02-15 | 27
G-PRC-PO | MR-EL-003 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00BBA-EL-ITP-0001 | 2027-02-15 | 65
G-PRC-PO | MR-EL-004 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00BFT-EL-SPC-0001 | 2027-05-10 | 110
G-PRC-PO | MR-EL-004 | type:MRQ@epc IFC | 1 | 1 | 2026-11-26 | ALP-EPC-00BFT-EL-MRQ-0001 | 2027-05-10 | 117
G-PRC-PO | MR-EL-004 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-02 | ALP-EPC-00BFT-GE-RPT-0001 | 2027-05-10 | 49
G-PRC-PO | MR-EL-004 | type:ITP@epc? IFR | 1 | 1 | 2026-12-10 | ALP-EPC-00BFT-EL-ITP-0001 | 2027-05-10 | 107
G-PRC-PO | MR-EL-005 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00BFA-EL-SPC-0001 | 2027-03-29 | 80
G-PRC-PO | MR-EL-005 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00BFA-EL-MRQ-0001 | 2027-03-29 | 102
G-PRC-PO | MR-EL-005 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-04 | ALP-EPC-00BFA-GE-RPT-0001 | 2027-03-29 | 37
G-PRC-PO | MR-EL-005 | type:ITP@epc? IFR | 1 | 1 | 2026-11-23 | ALP-EPC-00BFA-EL-ITP-0001 | 2027-03-29 | 90
G-PRC-PO | MR-EL-006 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00XJA-EL-SPC-0001 | 2027-02-15 | 50
G-PRC-PO | MR-EL-006 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00XJA-EL-MRQ-0001 | 2027-02-15 | 72
G-PRC-PO | MR-EL-006 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-07 | ALP-EPC-00XJA-GE-RPT-0001 | 2027-02-15 | 27
G-PRC-PO | MR-EL-006 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00XJA-EL-ITP-0001 | 2027-02-15 | 65
G-PRC-PO | MR-EL-007 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00BRA-EL-SPC-0001 | 2027-05-10 | 110
G-PRC-PO | MR-EL-007 | type:MRQ@epc IFC | 1 | 1 | 2026-11-26 | ALP-EPC-00BRA-EL-MRQ-0001 | 2027-05-10 | 117
G-PRC-PO | MR-EL-007 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-10 | ALP-EPC-00BRA-GE-RPT-0001 | 2027-05-10 | 43
G-PRC-PO | MR-EL-007 | type:ITP@epc? IFR | 1 | 1 | 2026-12-16 | ALP-EPC-00BRA-EL-ITP-0001 | 2027-05-10 | 103
G-PRC-PO | MR-EL-008 | type:SPC@epc IFC | 1 | 1 | 2027-02-05 | ALP-EPC-00000-EL-SPC-0004 | 2027-06-21 | 96
G-PRC-PO | MR-EL-008 | type:MRQ@epc IFC | 1 | 1 | 2027-01-13 | ALP-EPC-00000-EL-MRQ-0001 | 2027-06-21 | 113
G-PRC-PO | MR-EL-008 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-15 | ALP-EPC-00000-GE-RPT-0003 | 2027-06-21 | 70
G-PRC-PO | MR-EL-009 | type:SPC@epc IFC | 1 | 1 | 2027-01-04 | ALP-EPC-00000-EL-SPC-0005 | 2027-02-08 | 25
G-PRC-PO | MR-EL-009 | type:MRQ@epc IFC | 1 | 1 | 2026-12-10 | ALP-EPC-00000-EL-MRQ-0002 | 2027-02-08 | 42
G-PRC-PO | MR-EL-009 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-28 | ALP-EPC-00BLA-GE-RPT-0001 | 2027-02-08 | 7
G-PRC-PO | MR-EL-010 | type:SPC@epc IFC | 1 | 1 | 2027-04-01 | ALP-EPC-00BXA-GE-SPC-0001 | 2027-06-21 | 57
G-PRC-PO | MR-EL-010 | type:MRQ@epc IFC | 1 | 1 | 2027-03-09 | ALP-EPC-00BXA-GE-MRQ-0001 | 2027-06-21 | 74
G-PRC-PO | MR-EL-010 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-05-11 | ALP-EPC-00BXA-GE-RPT-0001 | 2027-06-21 | 29
G-PRC-PO | MR-EL-010 | type:ITP@epc? IFR | 1 | 1 | 2027-03-11 | ALP-EPC-00BXA-GE-ITP-0001 | 2027-06-21 | 72
G-PRC-PO | MR-EL-011 | type:SPC@epc IFC | 1 | 1 | 2026-11-16 | ALP-EPC-00000-GE-SPC-0001 | 2026-11-16 | 0
G-PRC-PO | MR-EL-011 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00000-GE-MRQ-0001 | 2026-11-16 | 7
G-PRC-PO | MR-EL-011 | rule:DL-MR-TBE IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-GE-RPT-0004 | 2026-11-16 | 10
G-PRC-PO | MR-EL-011 | type:ITP@epc? IFR | 1 | 1 | 2026-11-02 | ALP-EPC-00000-GE-ITP-0001 | 2026-11-16 | 10
G-PRC-PO | MR-EL-012 | type:SPC@epc IFC | 1 | 1 | 2027-01-15 | ALP-EPC-00000-GE-SPC-0002 | 2027-11-22 | 221
G-PRC-PO | MR-EL-012 | type:MRQ@epc IFC | 1 | 1 | 2027-03-24 | ALP-EPC-00000-GE-MRQ-0002 | 2027-11-22 | 173
G-PRC-PO | MR-EL-012 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-06-09 | ALP-EPC-00000-GE-RPT-0005 | 2027-11-22 | 118
G-PRC-PO | MR-HV-001 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00SAA-HV-SPC-0001 | 2027-03-15 | 70
G-PRC-PO | MR-HV-001 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00SAA-HV-MRQ-0001 | 2027-03-15 | 92
G-PRC-PO | MR-HV-001 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-28 | ALP-EPC-00SAA-GE-RPT-0001 | 2027-03-15 | 32
G-PRC-PO | MR-HV-001 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00SAA-HV-ITP-0001 | 2027-03-15 | 85
G-PRC-PO | MR-IC-001 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00CJA-IC-SPC-0001 | 2027-02-15 | 50
G-PRC-PO | MR-IC-001 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00CJA-IC-MRQ-0001 | 2027-02-15 | 72
G-PRC-PO | MR-IC-001 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-12 | ALP-EPC-00CJA-GE-RPT-0001 | 2027-02-15 | 24
G-PRC-PO | MR-IC-001 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00CJA-IC-ITP-0001 | 2027-02-15 | 65
G-PRC-PO | MR-IC-002 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00CQA-IC-SPC-0001 | 2027-07-12 | 155
G-PRC-PO | MR-IC-002 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00CQA-IC-MRQ-0001 | 2027-07-12 | 177
G-PRC-PO | MR-IC-002 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-19 | ALP-EPC-00CQA-GE-RPT-0001 | 2027-07-12 | 81
G-PRC-PO | MR-IC-002 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00CQA-IC-ITP-0001 | 2027-07-12 | 170
G-PRC-PO | MR-IC-003 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00QUA-IC-SPC-0001 | 2027-07-12 | 155
G-PRC-PO | MR-IC-003 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00QUA-IC-MRQ-0001 | 2027-07-12 | 177
G-PRC-PO | MR-IC-003 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-23 | ALP-EPC-00QUA-GE-RPT-0001 | 2027-07-12 | 79
G-PRC-PO | MR-IC-003 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00QUA-IC-ITP-0001 | 2027-07-12 | 170
G-PRC-PO | MR-IC-004 | type:SPC@epc IFC | 1 | 1 | 2027-01-04 | ALP-EPC-00000-IC-SPC-0003 | 2027-07-26 | 145
G-PRC-PO | MR-IC-004 | type:MRQ@epc IFC | 1 | 1 | 2026-12-10 | ALP-EPC-00000-IC-MRQ-0001 | 2027-07-26 | 162
G-PRC-PO | MR-IC-004 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-24 | ALP-EPC-00000-GE-RPT-0006 | 2027-07-26 | 88
G-PRC-PO | MR-IC-005 | type:SPC@epc IFC | 1 | 1 | 2027-01-04 | ALP-EPC-00000-IC-SPC-0004 | 2027-05-17 | 95
G-PRC-PO | MR-IC-005 | type:MRQ@epc IFC | 1 | 1 | 2026-12-10 | ALP-EPC-00000-IC-MRQ-0002 | 2027-05-17 | 112
G-PRC-PO | MR-IC-005 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-15 | ALP-EPC-00000-GE-RPT-0007 | 2027-05-17 | 45
G-PRC-PO | MR-IC-006 | type:SPC@epc IFC | 1 | 1 | 2027-04-07 | ALP-EPC-00SGY-GE-SPC-0001 | 2027-07-19 | 73
G-PRC-PO | MR-IC-006 | type:MRQ@epc IFC | 1 | 1 | 2027-03-29 | ALP-EPC-00SGY-GE-MRQ-0001 | 2027-07-19 | 80
G-PRC-PO | MR-IC-006 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-05-31 | ALP-EPC-00SGY-GE-RPT-0001 | 2027-07-19 | 35
G-PRC-PO | MR-IC-006 | type:ITP@epc? IFR | 1 | 1 | 2027-03-19 | ALP-EPC-00SGY-GE-ITP-0001 | 2027-07-19 | 86
G-PRC-PO | MR-IC-007 | type:SPC@epc IFC | 1 | 1 | 2027-03-31 | ALP-EPC-00CYA-GE-SPC-0001 | 2027-07-19 | 78
G-PRC-PO | MR-IC-007 | type:MRQ@epc IFC | 1 | 1 | 2027-03-22 | ALP-EPC-00CYA-GE-MRQ-0001 | 2027-07-19 | 85
G-PRC-PO | MR-IC-007 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-05-24 | ALP-EPC-00CYA-GE-RPT-0001 | 2027-07-19 | 40
G-PRC-PO | MR-IC-007 | type:ITP@epc? IFR | 1 | 1 | 2027-03-18 | ALP-EPC-00CYA-GE-ITP-0001 | 2027-07-19 | 87
G-PRC-PO | MR-IC-008 | type:SPC@epc IFC | 1 | 1 | 2027-03-08 | ALP-EPC-00CJG-GE-SPC-0001 | 2027-06-07 | 65
G-PRC-PO | MR-IC-008 | type:MRQ@epc IFC | 1 | 1 | 2027-02-25 | ALP-EPC-00CJG-GE-MRQ-0001 | 2027-06-07 | 72
G-PRC-PO | MR-IC-008 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-04-29 | ALP-EPC-00CJG-GE-RPT-0001 | 2027-06-07 | 27
G-PRC-PO | MR-IC-008 | type:ITP@epc? IFR | 1 | 1 | 2027-03-01 | ALP-EPC-00CJG-GE-ITP-0001 | 2027-06-07 | 70
G-PRC-PO | MR-IC-009 | type:SPC@epc IFC | 1 | 1 | 2027-03-08 | ALP-EPC-00CKA-GE-SPC-0001 | 2027-06-21 | 75
G-PRC-PO | MR-IC-009 | type:MRQ@epc IFC | 1 | 1 | 2027-02-25 | ALP-EPC-00CKA-GE-MRQ-0001 | 2027-06-21 | 82
G-PRC-PO | MR-IC-009 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-05-13 | ALP-EPC-00CKA-GE-RPT-0001 | 2027-06-21 | 27
G-PRC-PO | MR-IC-009 | type:ITP@epc? IFR | 1 | 1 | 2027-03-08 | ALP-EPC-00CKA-GE-ITP-0001 | 2027-06-21 | 75
G-PRC-PO | MR-IC-010 | type:SPC@epc IFC | 1 | 1 | 2027-05-07 | ALP-EPC-00000-GE-SPC-0003 | 2027-11-29 | 146
G-PRC-PO | MR-IC-010 | type:MRQ@epc IFC | 1 | 1 | 2027-04-14 | ALP-EPC-00000-GE-MRQ-0003 | 2027-11-29 | 163
G-PRC-PO | MR-IC-010 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-06-02 | ALP-EPC-00000-GE-RPT-0008 | 2027-11-29 | 128
G-PRC-PO | MR-ME-001 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-10LAC-ME-SPC-0001 | 2027-01-25 | 35
G-PRC-PO | MR-ME-001 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-10LAC-ME-MRQ-0001 | 2027-01-25 | 57
G-PRC-PO | MR-ME-001 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-07 | ALP-EPC-10LAC-GE-RPT-0001 | 2027-01-25 | 12
G-PRC-PO | MR-ME-001 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-10LAC-ME-ITP-0001 | 2027-01-25 | 50
G-PRC-PO | MR-ME-002 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-20LCB-ME-SPC-0001 | 2027-04-12 | 90
G-PRC-PO | MR-ME-002 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-20LCB-ME-MRQ-0001 | 2027-04-12 | 112
G-PRC-PO | MR-ME-002 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-22 | ALP-EPC-20LCB-GE-RPT-0001 | 2027-04-12 | 35
G-PRC-PO | MR-ME-002 | type:ITP@epc? IFR | 1 | 1 | 2026-11-23 | ALP-EPC-20LCB-ME-ITP-0001 | 2027-04-12 | 100
G-PRC-PO | MR-ME-003 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00PAC-ME-SPC-0001 | 2027-02-01 | 40
G-PRC-PO | MR-ME-003 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00PAC-ME-MRQ-0001 | 2027-02-01 | 62
G-PRC-PO | MR-ME-003 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-07 | ALP-EPC-00PAC-GE-RPT-0001 | 2027-02-01 | 17
G-PRC-PO | MR-ME-003 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00PAC-ME-ITP-0001 | 2027-02-01 | 55
G-PRC-PO | MR-ME-004 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00PAA-ME-SPC-0001 | 2027-04-12 | 90
G-PRC-PO | MR-ME-004 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00PAA-ME-MRQ-0001 | 2027-04-12 | 112
G-PRC-PO | MR-ME-004 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-12 | ALP-EPC-00PAA-GE-RPT-0001 | 2027-04-12 | 41
G-PRC-PO | MR-ME-004 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00PAA-ME-ITP-0001 | 2027-04-12 | 105
G-PRC-PO | MR-ME-005 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00PBA-ME-SPC-0001 | 2027-04-12 | 90
G-PRC-PO | MR-ME-005 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00PBA-ME-MRQ-0001 | 2027-04-12 | 112
G-PRC-PO | MR-ME-005 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-15 | ALP-EPC-00PBA-GE-RPT-0001 | 2027-04-12 | 40
G-PRC-PO | MR-ME-005 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00PBA-ME-ITP-0001 | 2027-04-12 | 105
G-PRC-PO | MR-ME-006 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00PAH-ME-SPC-0001 | 2027-07-05 | 150
G-PRC-PO | MR-ME-006 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00PAH-ME-MRQ-0001 | 2027-07-05 | 172
G-PRC-PO | MR-ME-006 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-17 | ALP-EPC-00PAH-GE-RPT-0001 | 2027-07-05 | 78
G-PRC-PO | MR-ME-006 | type:ITP@epc? IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00PAH-ME-ITP-0001 | 2027-07-05 | 155
G-PRC-PO | MR-ME-007 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00PGA-ME-SPC-0001 | 2027-04-05 | 85
G-PRC-PO | MR-ME-007 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00PGA-ME-MRQ-0001 | 2027-04-05 | 107
G-PRC-PO | MR-ME-007 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-18 | ALP-EPC-00PGA-GE-RPT-0001 | 2027-04-05 | 32
G-PRC-PO | MR-ME-007 | type:ITP@epc? IFR | 1 | 1 | 2026-11-17 | ALP-EPC-00PGA-ME-ITP-0001 | 2027-04-05 | 99
G-PRC-PO | MR-ME-008 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00QEA-ME-SPC-0001 | 2027-04-05 | 85
G-PRC-PO | MR-ME-008 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00QEA-ME-MRQ-0001 | 2027-04-05 | 107
G-PRC-PO | MR-ME-008 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-18 | ALP-EPC-00QEA-GE-RPT-0001 | 2027-04-05 | 32
G-PRC-PO | MR-ME-008 | type:ITP@epc? IFR | 1 | 1 | 2026-11-18 | ALP-EPC-00QEA-ME-ITP-0001 | 2027-04-05 | 98
G-PRC-PO | MR-ME-009 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00QHA-ME-SPC-0001 | 2027-01-25 | 35
G-PRC-PO | MR-ME-009 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00QHA-ME-MRQ-0001 | 2027-01-25 | 57
G-PRC-PO | MR-ME-009 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-07 | ALP-EPC-00QHA-GE-RPT-0001 | 2027-01-25 | 12
G-PRC-PO | MR-ME-009 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00QHA-ME-ITP-0001 | 2027-01-25 | 50
G-PRC-PO | MR-ME-010 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00QJA-ME-SPC-0001 | 2027-06-28 | 145
G-PRC-PO | MR-ME-010 | type:MRQ@epc IFC | 1 | 1 | 2027-03-30 | ALP-EPC-00QJA-ME-MRQ-0001 | 2027-06-28 | 64
G-PRC-PO | MR-ME-010 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-05-18 | ALP-EPC-00QJA-GE-RPT-0001 | 2027-06-28 | 29
G-PRC-PO | MR-ME-010 | type:ITP@epc? IFR | 1 | 1 | 2026-11-30 | ALP-EPC-00QJA-ME-ITP-0001 | 2027-06-28 | 150
G-PRC-PO | MR-ME-011 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00QCA-ME-SPC-0001 | 2027-05-17 | 115
G-PRC-PO | MR-ME-011 | type:MRQ@epc IFC | 1 | 1 | 2027-03-31 | ALP-EPC-00QCA-ME-MRQ-0001 | 2027-05-17 | 33
G-PRC-PO | MR-ME-011 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-05-12 | ALP-EPC-00QCA-GE-RPT-0001 | 2027-05-17 | 3
G-PRC-PO | MR-ME-011 | type:ITP@epc? IFR | 1 | 1 | 2026-11-26 | ALP-EPC-00QCA-ME-ITP-0001 | 2027-05-17 | 122
G-PRC-PO | MR-ME-012 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00LDA-ME-SPC-0001 | 2027-02-08 | 45
G-PRC-PO | MR-ME-012 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00LDA-ME-MRQ-0001 | 2027-02-08 | 67
G-PRC-PO | MR-ME-012 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-14 | ALP-EPC-00GBA-GE-RPT-0001 | 2027-02-08 | 17
G-PRC-PO | MR-ME-012 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00LDA-ME-ITP-0001 | 2027-02-08 | 60
G-PRC-PO | MR-ME-013 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00GHA-ME-SPC-0001 | 2027-05-17 | 115
G-PRC-PO | MR-ME-013 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00GHA-ME-MRQ-0001 | 2027-05-17 | 137
G-PRC-PO | MR-ME-013 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-22 | ALP-EPC-00GHA-GE-RPT-0001 | 2027-05-17 | 81
G-PRC-PO | MR-ME-013 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00GHA-ME-ITP-0001 | 2027-05-17 | 130
G-PRC-PO | MR-ME-014 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00GNA-ME-SPC-0001 | 2027-05-31 | 125
G-PRC-PO | MR-ME-014 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00GNA-ME-MRQ-0001 | 2027-05-31 | 147
G-PRC-PO | MR-ME-014 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-28 | ALP-EPC-00GNA-GE-RPT-0001 | 2027-05-31 | 87
G-PRC-PO | MR-ME-014 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00GNA-ME-ITP-0001 | 2027-05-31 | 140
G-PRC-PO | MR-ME-015 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00EKA-ME-SPC-0001 | 2027-01-25 | 35
G-PRC-PO | MR-ME-015 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00EKA-ME-MRQ-0001 | 2027-01-25 | 57
G-PRC-PO | MR-ME-015 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-07 | ALP-EPC-00EKA-GE-RPT-0001 | 2027-01-25 | 12
G-PRC-PO | MR-ME-015 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00EKA-ME-ITP-0001 | 2027-01-25 | 50
G-PRC-PO | MR-ME-016 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00EGA-ME-SPC-0001 | 2027-01-25 | 35
G-PRC-PO | MR-ME-016 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00EGA-ME-MRQ-0001 | 2027-01-25 | 57
G-PRC-PO | MR-ME-016 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-07 | ALP-EPC-00EGA-GE-RPT-0001 | 2027-01-25 | 12
G-PRC-PO | MR-ME-016 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00EGA-ME-ITP-0001 | 2027-01-25 | 50
G-PRC-PO | MR-ME-017 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00EGB-ME-SPC-0001 | 2027-07-26 | 165
G-PRC-PO | MR-ME-017 | type:MRQ@epc IFC | 1 | 1 | 2026-11-26 | ALP-EPC-00EGB-ME-MRQ-0001 | 2027-07-26 | 172
G-PRC-PO | MR-ME-017 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-25 | ALP-EPC-00EGB-GE-RPT-0001 | 2027-07-26 | 87
G-PRC-PO | MR-ME-018 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-10HSB-ME-SPC-0001 | 2027-04-05 | 85
G-PRC-PO | MR-ME-018 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-10HSB-ME-MRQ-0001 | 2027-04-05 | 107
G-PRC-PO | MR-ME-018 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-22 | ALP-EPC-10HSB-GE-RPT-0001 | 2027-04-05 | 30
G-PRC-PO | MR-ME-018 | type:ITP@epc? IFR | 1 | 1 | 2026-11-20 | ALP-EPC-10HSB-ME-ITP-0001 | 2027-04-05 | 96
G-PRC-PO | MR-ME-019 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-10HAN-ME-SPC-0001 | 2027-05-03 | 105
G-PRC-PO | MR-ME-019 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-10HAN-ME-MRQ-0001 | 2027-05-03 | 127
G-PRC-PO | MR-ME-019 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-15 | ALP-EPC-10HAN-GE-RPT-0001 | 2027-05-03 | 55
G-PRC-PO | MR-ME-019 | type:ITP@epc? IFR | 1 | 1 | 2026-11-25 | ALP-EPC-10HAN-ME-ITP-0001 | 2027-05-03 | 113
G-PRC-PO | MR-ME-020 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00SGA-ME-SPC-0001 | 2027-03-22 | 75
G-PRC-PO | MR-ME-020 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00SGA-ME-MRQ-0001 | 2027-03-22 | 97
G-PRC-PO | MR-ME-020 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-28 | ALP-EPC-00SGA-GE-RPT-0001 | 2027-03-22 | 37
G-PRC-PO | MR-ME-020 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00SGA-ME-ITP-0001 | 2027-03-22 | 90
G-PRC-PO | MR-ME-021 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00SMA-ME-SPC-0001 | 2027-02-08 | 45
G-PRC-PO | MR-ME-021 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00SMA-ME-MRQ-0001 | 2027-02-08 | 67
G-PRC-PO | MR-ME-021 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-07 | ALP-EPC-00SMA-GE-RPT-0001 | 2027-02-08 | 22
G-PRC-PO | MR-ME-021 | type:ITP@epc? IFR | 1 | 1 | 2026-11-16 | ALP-EPC-00SMA-ME-ITP-0001 | 2027-02-08 | 60
G-PRC-PO | MR-ME-022 | type:SPC@epc IFC | 1 | 1 | 2027-05-21 | ALP-EPC-00000-GE-SPC-0004 | 2028-01-10 | 166
G-PRC-PO | MR-ME-022 | type:MRQ@epc IFC | 1 | 1 | 2027-04-28 | ALP-EPC-00000-GE-MRQ-0004 | 2028-01-10 | 183
G-PRC-PO | MR-ME-022 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-06-30 | ALP-EPC-00000-GE-RPT-0009 | 2028-01-10 | 138
G-PRC-PO | MR-ME-023 | type:SPC@epc IFC | 1 | 1 | 2027-07-23 | ALP-EPC-00000-GE-SPC-0005 | 2027-11-15 | 81
G-PRC-PO | MR-ME-023 | type:MRQ@epc IFC | 1 | 1 | 2027-06-30 | ALP-EPC-00000-GE-MRQ-0005 | 2027-11-15 | 98
G-PRC-PO | MR-ME-023 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-09-15 | ALP-EPC-00000-GE-RPT-0010 | 2027-11-15 | 43
G-PRC-PO | MR-ME-024 | type:SPC@epc IFC | 1 | 1 | 2027-07-21 | ALP-EPC-00UZF-GE-SPC-0001 | 2027-11-15 | 83
G-PRC-PO | MR-ME-024 | type:MRQ@epc IFC | 1 | 1 | 2027-06-28 | ALP-EPC-00UZF-GE-MRQ-0001 | 2027-11-15 | 100
G-PRC-PO | MR-ME-024 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-08-30 | ALP-EPC-00UZF-GE-RPT-0001 | 2027-11-15 | 55
G-PRC-PO | MR-PI-001 | type:SPC@epc IFC | 1 | 1 | 2027-01-04 | ALP-EPC-00000-PI-SPC-0004 | 2027-02-22 | 35
G-PRC-PO | MR-PI-001 | type:MRQ@epc IFC | 1 | 1 | 2026-12-10 | ALP-EPC-00000-PI-MRQ-0001 | 2027-02-22 | 52
G-PRC-PO | MR-PI-001 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-28 | ALP-EPC-00000-GE-RPT-0011 | 2027-02-22 | 17
G-PRC-PO | MR-PI-002 | type:SPC@epc IFC | 1 | 1 | 2027-01-04 | ALP-EPC-00000-PI-SPC-0005 | 2027-02-22 | 35
G-PRC-PO | MR-PI-002 | type:MRQ@epc IFC | 1 | 1 | 2026-12-10 | ALP-EPC-00000-PI-MRQ-0002 | 2027-02-22 | 52
G-PRC-PO | MR-PI-002 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-04 | ALP-EPC-10LBA-GE-RPT-0001 | 2027-02-22 | 12
G-PRC-PO | MR-PI-003 | type:SPC@epc IFC | 1 | 1 | 2027-01-21 | ALP-EPC-00000-PI-SPC-0006 | 2027-06-14 | 102
G-PRC-PO | MR-PI-003 | type:MRQ@epc IFC | 1 | 1 | 2026-12-29 | ALP-EPC-00000-PI-MRQ-0003 | 2027-06-14 | 119
G-PRC-PO | MR-PI-003 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-03-15 | ALP-EPC-00000-GE-RPT-0012 | 2027-06-14 | 65
G-PRC-PO | MR-PI-004 | type:SPC@epc IFC | 1 | 1 | 2027-01-04 | ALP-EPC-00000-PI-SPC-0007 | 2027-02-22 | 35
G-PRC-PO | MR-PI-004 | type:MRQ@epc IFC | 1 | 1 | 2026-11-05 | ALP-EPC-00000-PI-MRQ-0004 | 2027-02-22 | 77
G-PRC-PO | MR-PI-004 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-01-13 | ALP-EPC-00PAB-GE-RPT-0001 | 2027-02-22 | 28
G-PRC-PO | MR-PI-005 | type:SPC@epc IFC | 1 | 1 | 2027-04-26 | ALP-EPC-00000-GE-SPC-0006 | 2027-08-30 | 90
G-PRC-PO | MR-PI-005 | type:MRQ@epc IFC | 1 | 1 | 2027-04-01 | ALP-EPC-00000-GE-MRQ-0006 | 2027-08-30 | 107
G-PRC-PO | MR-PI-005 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-05-27 | ALP-EPC-00000-GE-RPT-0013 | 2027-08-30 | 67
G-PRC-PO | MR-PI-006 | type:SPC@epc IFC | 1 | 1 | 2027-01-04 | ALP-EPC-00000-GE-SPC-0007 | 2027-08-30 | 170
G-PRC-PO | MR-PI-006 | type:MRQ@epc IFC | 1 | 1 | 2026-12-10 | ALP-EPC-00000-GE-MRQ-0007 | 2027-08-30 | 187
G-PRC-PO | MR-PI-006 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-04-05 | ALP-EPC-00000-GE-RPT-0014 | 2027-08-30 | 105
G-PRC-PO | MR-PI-007 | type:SPC@epc IFC | 1 | 1 | 2027-01-04 | ALP-EPC-00000-GE-SPC-0008 | 2027-08-02 | 150
G-PRC-PO | MR-PI-007 | type:MRQ@epc IFC | 1 | 1 | 2026-12-10 | ALP-EPC-00000-GE-MRQ-0008 | 2027-08-02 | 167
G-PRC-PO | MR-PI-007 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-04-01 | ALP-EPC-00000-GE-RPT-0015 | 2027-08-02 | 87
G-PRC-PO | MR-SS-001 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-00000-SS-SPC-0002 | 2027-03-23 | 76
G-PRC-PO | MR-SS-001 | type:MRQ@epc IFC | 1 | 1 | 2026-11-12 | ALP-EPC-00000-SS-MRQ-0001 | 2027-03-23 | 93
G-PRC-PO | MR-SS-001 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-03 | ALP-EPC-00000-GE-RPT-0016 | 2027-03-23 | 34
G-PRC-PO | MR-SS-002 | type:SPC@epc IFC | 1 | 1 | 2026-12-07 | ALP-EPC-10HNE-SS-SPC-0001 | 2027-03-22 | 75
G-PRC-PO | MR-SS-002 | type:MRQ@epc IFC | 1 | 1 | 2026-11-12 | ALP-EPC-10HNE-SS-MRQ-0001 | 2027-03-22 | 92
G-PRC-PO | MR-SS-002 | rule:DL-MR-TBE IFR | 1 | 1 | 2027-02-02 | ALP-EPC-10HNE-GE-RPT-0001 | 2027-03-22 | 34
G-PRC-SHP | MR-EL-001 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-11-30 | ALP-E01-00ACA-ME-TRP-0001 | 2027-12-14 | 10
G-PRC-SHP | MR-EL-001 | rule:DL-V-MDB IFR | 1 | 1 | 2027-11-30 | ALP-E01-00ACA-ME-MDB-0001 | 2027-12-14 | 10
G-PRC-SHP | MR-EL-002 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-11-11 | ALP-E02-10BBT-ME-TRP-0001 | 2027-11-25 | 10
G-PRC-SHP | MR-EL-002 | rule:DL-V-MDB IFR | 1 | 1 | 2027-11-11 | ALP-E02-10BBT-ME-MDB-0001 | 2027-11-25 | 10
G-PRC-SHP | MR-EL-003 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-09 | ALP-E03-00BBA-ME-TRP-0001 | 2027-09-23 | 10
G-PRC-SHP | MR-EL-003 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-09 | ALP-E03-00BBA-ME-MDB-0001 | 2027-09-23 | 10
G-PRC-SHP | MR-EL-004 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-08-17 | ALP-E04-00BFT-ME-TRP-0001 | 2027-08-31 | 10
G-PRC-SHP | MR-EL-004 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-17 | ALP-E04-00BFT-ME-MDB-0001 | 2027-08-31 | 10
G-PRC-SHP | MR-EL-005 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-08-19 | ALP-E05-00BFA-ME-TRP-0001 | 2027-09-02 | 10
G-PRC-SHP | MR-EL-005 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-19 | ALP-E05-00BFA-ME-MDB-0001 | 2027-09-02 | 10
G-PRC-SHP | MR-EL-006 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-09 | ALP-E06-00XJA-ME-TRP-0001 | 2027-09-23 | 10
G-PRC-SHP | MR-EL-006 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-09 | ALP-E06-00XJA-ME-MDB-0001 | 2027-09-23 | 10
G-PRC-SHP | MR-EL-007 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-08-25 | ALP-E07-00BRA-ME-TRP-0001 | 2027-09-08 | 10
G-PRC-SHP | MR-EL-007 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-25 | ALP-E07-00BRA-ME-MDB-0001 | 2027-09-08 | 10
G-PRC-SHP | MR-EL-008 | rule:DL-V-MDB IFR | 1 | 1 | 2027-07-19 | ALP-E08-00000-ME-MDB-0001 | 2027-08-02 | 10
G-PRC-SHP | MR-EL-009 | rule:DL-V-MDB IFR | 1 | 1 | 2027-05-06 | ALP-E09-00BLA-ME-MDB-0001 | 2027-05-20 | 10
G-PRC-SHP | MR-EL-010 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-08-17 | ALP-E10-00BXA-ME-TRP-0001 | 2027-08-31 | 10
G-PRC-SHP | MR-EL-010 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-17 | ALP-E10-00BXA-ME-MDB-0001 | 2027-08-31 | 10
G-PRC-SHP | MR-EL-011 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2026-12-28 | ALP-E11-00000-ME-TRP-0001 | 2027-01-11 | 10
G-PRC-SHP | MR-EL-011 | rule:DL-V-MDB IFR | 1 | 1 | 2026-12-28 | ALP-E11-00000-ME-MDB-0001 | 2027-01-11 | 10
G-PRC-SHP | MR-EL-101 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-27 | ALP-IEC-10MKA-ME-TRP-0001 | 2027-10-11 | 10
G-PRC-SHP | MR-EL-101 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-27 | ALP-IEC-10MKA-ME-MDB-0001 | 2027-10-11 | 10
G-PRC-SHP | MR-EL-102 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-04 | ALP-IEC-10BAT-ME-TRP-0001 | 2027-10-18 | 10
G-PRC-SHP | MR-EL-102 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-04 | ALP-IEC-10BAT-ME-MDB-0001 | 2027-10-18 | 10
G-PRC-SHP | MR-HV-001 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-08-12 | ALP-H01-00SAA-ME-TRP-0001 | 2027-08-26 | 10
G-PRC-SHP | MR-HV-001 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-12 | ALP-H01-00SAA-ME-MDB-0001 | 2027-08-26 | 10
G-PRC-SHP | MR-IC-001 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-14 | ALP-I01-00CJA-ME-TRP-0001 | 2027-10-28 | 10
G-PRC-SHP | MR-IC-001 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-14 | ALP-I01-00CJA-ME-MDB-0001 | 2027-10-28 | 10
G-PRC-SHP | MR-IC-002 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-01 | ALP-I02-00CQA-ME-TRP-0001 | 2027-10-15 | 10
G-PRC-SHP | MR-IC-002 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-01 | ALP-I02-00CQA-ME-MDB-0001 | 2027-10-15 | 10
G-PRC-SHP | MR-IC-003 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-05 | ALP-I03-00QUA-ME-TRP-0001 | 2027-10-19 | 10
G-PRC-SHP | MR-IC-003 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-05 | ALP-I03-00QUA-ME-MDB-0001 | 2027-10-19 | 10
G-PRC-SHP | MR-IC-004 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-08 | ALP-I04-00000-ME-MDB-0001 | 2027-09-22 | 10
G-PRC-SHP | MR-IC-005 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-27 | ALP-I05-00000-ME-MDB-0001 | 2027-10-11 | 10
G-PRC-SHP | MR-IC-006 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-04 | ALP-I06-00SGY-ME-TRP-0001 | 2027-10-18 | 10
G-PRC-SHP | MR-IC-006 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-04 | ALP-I06-00SGY-ME-MDB-0001 | 2027-10-18 | 10
G-PRC-SHP | MR-IC-007 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-27 | ALP-I07-00CYA-ME-TRP-0001 | 2027-10-11 | 10
G-PRC-SHP | MR-IC-007 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-27 | ALP-I07-00CYA-ME-MDB-0001 | 2027-10-11 | 10
G-PRC-SHP | MR-IC-008 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-14 | ALP-I08-00CJG-ME-TRP-0001 | 2027-10-28 | 10
G-PRC-SHP | MR-IC-008 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-14 | ALP-I08-00CJG-ME-MDB-0001 | 2027-10-28 | 10
G-PRC-SHP | MR-IC-009 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2028-02-03 | ALP-I09-00CKA-ME-TRP-0001 | 2028-02-17 | 10
G-PRC-SHP | MR-IC-009 | rule:DL-V-MDB IFR | 1 | 1 | 2028-02-03 | ALP-I09-00CKA-ME-MDB-0001 | 2028-02-17 | 10
G-PRC-SHP | MR-IC-010 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-11 | ALP-I10-00000-ME-MDB-0001 | 2027-08-25 | 10
G-PRC-SHP | MR-IC-101 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-07-26 | ALP-IEC-10MBY-ME-TRP-0001 | 2027-08-09 | 10
G-PRC-SHP | MR-IC-101 | rule:DL-V-MDB IFR | 1 | 1 | 2027-07-26 | ALP-IEC-10MBY-ME-MDB-0001 | 2027-08-09 | 10
G-PRC-SHP | MR-ME-001 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-07 | ALP-M01-10LAC-ME-TRP-0001 | 2027-10-21 | 10
G-PRC-SHP | MR-ME-001 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-07 | ALP-M01-10LAC-ME-MDB-0001 | 2027-10-21 | 10
G-PRC-SHP | MR-ME-002 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-18 | ALP-M02-20LCB-ME-TRP-0001 | 2027-11-01 | 10
G-PRC-SHP | MR-ME-002 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-18 | ALP-M02-20LCB-ME-MDB-0001 | 2027-11-01 | 10
G-PRC-SHP | MR-ME-003 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-11-04 | ALP-M03-00PAC-ME-TRP-0001 | 2027-11-18 | 10
G-PRC-SHP | MR-ME-003 | rule:DL-V-MDB IFR | 1 | 1 | 2027-11-04 | ALP-M03-00PAC-ME-MDB-0001 | 2027-11-18 | 10
G-PRC-SHP | MR-ME-004 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-08 | ALP-M04-00PAA-ME-TRP-0001 | 2027-10-22 | 10
G-PRC-SHP | MR-ME-004 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-08 | ALP-M04-00PAA-ME-MDB-0001 | 2027-10-22 | 10
G-PRC-SHP | MR-ME-005 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-11 | ALP-M05-00PBA-ME-TRP-0001 | 2027-10-25 | 10
G-PRC-SHP | MR-ME-005 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-11 | ALP-M05-00PBA-ME-MDB-0001 | 2027-10-25 | 10
G-PRC-SHP | MR-ME-006 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-29 | ALP-M06-00PAH-ME-TRP-0001 | 2027-10-13 | 10
G-PRC-SHP | MR-ME-006 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-29 | ALP-M06-00PAH-ME-MDB-0001 | 2027-10-13 | 10
G-PRC-SHP | MR-ME-007 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-02 | ALP-M07-00PGA-ME-TRP-0001 | 2027-09-16 | 10
G-PRC-SHP | MR-ME-007 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-02 | ALP-M07-00PGA-ME-MDB-0001 | 2027-09-16 | 10
G-PRC-SHP | MR-ME-008 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-02 | ALP-M08-00QEA-ME-TRP-0001 | 2027-09-16 | 10
G-PRC-SHP | MR-ME-008 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-02 | ALP-M08-00QEA-ME-MDB-0001 | 2027-09-16 | 10
G-PRC-SHP | MR-ME-009 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-07 | ALP-M09-00QHA-ME-TRP-0001 | 2027-10-21 | 10
G-PRC-SHP | MR-ME-009 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-07 | ALP-M09-00QHA-ME-MDB-0001 | 2027-10-21 | 10
G-PRC-SHP | MR-ME-010 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-21 | ALP-M10-00QJA-ME-TRP-0001 | 2027-10-05 | 10
G-PRC-SHP | MR-ME-010 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-21 | ALP-M10-00QJA-ME-MDB-0001 | 2027-10-05 | 10
G-PRC-SHP | MR-ME-011 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-27 | ALP-M11-00QCA-ME-TRP-0001 | 2027-11-10 | 10
G-PRC-SHP | MR-ME-011 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-27 | ALP-M11-00QCA-ME-MDB-0001 | 2027-11-10 | 10
G-PRC-SHP | MR-ME-012 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-11-18 | ALP-M12-00GBA-ME-TRP-0001 | 2027-12-02 | 10
G-PRC-SHP | MR-ME-012 | rule:DL-V-MDB IFR | 1 | 1 | 2027-11-18 | ALP-M12-00GBA-ME-MDB-0001 | 2027-12-02 | 10
G-PRC-SHP | MR-ME-013 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-07-09 | ALP-M13-00GHA-ME-TRP-0001 | 2027-07-23 | 10
G-PRC-SHP | MR-ME-013 | rule:DL-V-MDB IFR | 1 | 1 | 2027-07-09 | ALP-M13-00GHA-ME-MDB-0001 | 2027-07-23 | 10
G-PRC-SHP | MR-ME-014 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-08-12 | ALP-M14-00GNA-ME-TRP-0001 | 2027-08-26 | 10
G-PRC-SHP | MR-ME-014 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-12 | ALP-M14-00GNA-ME-MDB-0001 | 2027-08-26 | 10
G-PRC-SHP | MR-ME-015 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-07 | ALP-M15-00EKA-ME-TRP-0001 | 2027-10-21 | 10
G-PRC-SHP | MR-ME-015 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-07 | ALP-M15-00EKA-ME-MDB-0001 | 2027-10-21 | 10
G-PRC-SHP | MR-ME-016 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-09 | ALP-M16-00EGA-ME-TRP-0001 | 2027-09-23 | 10
G-PRC-SHP | MR-ME-016 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-09 | ALP-M16-00EGA-ME-MDB-0001 | 2027-09-23 | 10
G-PRC-SHP | MR-ME-018 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-06 | ALP-M18-10HSB-ME-TRP-0001 | 2027-09-20 | 10
G-PRC-SHP | MR-ME-018 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-06 | ALP-M18-10HSB-ME-MDB-0001 | 2027-09-20 | 10
G-PRC-SHP | MR-ME-019 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-08-02 | ALP-M19-10HAN-ME-TRP-0001 | 2027-08-16 | 10
G-PRC-SHP | MR-ME-019 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-02 | ALP-M19-10HAN-ME-MDB-0001 | 2027-08-16 | 10
G-PRC-SHP | MR-ME-020 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-08-26 | ALP-M20-00SGA-ME-TRP-0001 | 2027-09-09 | 10
G-PRC-SHP | MR-ME-020 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-26 | ALP-M20-00SGA-ME-MDB-0001 | 2027-09-09 | 10
G-PRC-SHP | MR-ME-021 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-09 | ALP-M21-00SMA-ME-TRP-0001 | 2027-09-23 | 10
G-PRC-SHP | MR-ME-021 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-09 | ALP-M21-00SMA-ME-MDB-0001 | 2027-09-23 | 10
G-PRC-SHP | MR-ME-101 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-10-04 | ALP-IEC-10MBA-ME-TRP-0001 | 2027-10-18 | 10
G-PRC-SHP | MR-ME-101 | rule:DL-V-MDB IFR | 1 | 1 | 2027-10-04 | ALP-IEC-10MBA-ME-MDB-0001 | 2027-10-18 | 10
G-PRC-SHP | MR-ME-102 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-09-20 | ALP-IEC-10HAA-ME-TRP-0001 | 2027-10-04 | 10
G-PRC-SHP | MR-ME-102 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-20 | ALP-IEC-10HAA-ME-MDB-0001 | 2027-10-04 | 10
G-PRC-SHP | MR-ME-103 | rule:DL-V-FTR? ACCEPTED | 1 | 1 | 2027-11-15 | ALP-IEC-20MAA-ME-TRP-0001 | 2027-11-29 | 10
G-PRC-SHP | MR-ME-103 | rule:DL-V-MDB IFR | 1 | 1 | 2027-11-15 | ALP-IEC-20MAA-ME-MDB-0001 | 2027-11-29 | 10
G-PRC-SHP | MR-PI-001 | rule:DL-V-MDB IFR | 1 | 1 | 2027-06-03 | ALP-P01-00000-ME-MDB-0001 | 2027-06-17 | 10
G-PRC-SHP | MR-PI-002 | rule:DL-V-MDB IFR | 1 | 1 | 2027-11-04 | ALP-P02-10LBA-ME-MDB-0001 | 2027-11-18 | 10
G-PRC-SHP | MR-PI-003 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-30 | ALP-P03-00000-ME-MDB-0001 | 2027-09-13 | 10
G-PRC-SHP | MR-PI-004 | rule:DL-V-MDB IFR | 1 | 1 | 2027-07-28 | ALP-P04-00PAB-ME-MDB-0001 | 2027-08-11 | 10
G-PRC-SHP | MR-PI-005 | rule:DL-V-MDB IFR | 1 | 1 | 2027-09-02 | ALP-P05-00000-ME-MDB-0001 | 2027-09-16 | 10
G-PRC-SHP | MR-PI-006 | rule:DL-V-MDB IFR | 1 | 1 | 2027-07-12 | ALP-P06-00000-ME-MDB-0001 | 2027-07-26 | 10
G-PRC-SHP | MR-PI-007 | rule:DL-V-MDB IFR | 1 | 1 | 2027-08-05 | ALP-P07-00000-ME-MDB-0001 | 2027-08-19 | 10

## Release plan
Alpilla 600 MW Combined Cycle Power Plant - Release plan: every document in release order (network waves)
engine release_control v1.2.0 ¦ generated 2026-09-29T02:52:27Z by SETUP ¦ data 6d73bc5813f68e2b ¦ planned dates from the levelled workflow network and the CPM (working days)
Wave | Document | Title | Description | Orig. | Discipline | Type | Review | Status now | Rev | Code | Next action | Next purpose | Next rev | Can issue now | Blocked by (first 6) | Check required (inputs revised) | Start | IFR | IFA | Accepted | IFC | Driver | First gate | Gate need | Gates fed (first 8)
1 | ALP-IEC-00000-GE-LST-0001 | Power Island - Terminal Points and Interface Data |  | IEC | general | LST | review | ACCEPTED | A | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-09-07 | 2026-09-28 |  | 2026-10-12 | 2026-11-02 |  | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
1 | ALP-IEC-00000-GE-RPT-0001 | Power Island and Balance of Plant - Division of Responsibility |  | IEC | general | RPT | review | ACCEPTED | 0 | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-09-07 | 2026-09-28 |  | 2026-10-12 | 2026-11-02
1 | ALP-IEC-00000-GE-SPC-0001 | Power Island Interface Requirements to the EPC |  | IEC | general | SPC | approval | ACCEPTED | 0 | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-08-31 | 2026-09-28 |  | 2026-10-26 | 2026-11-02
1 | ALP-IEC-10MBA-PR-HMB-0001 | Power Island Thermal Performance Data | heat balance | IEC | process | HMB | approval | ACCEPTED | B | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-09-07 | 2026-09-28 |  | 2026-10-26 | 2026-11-02
1 | ALP-IEC-10MBA-PR-HMB-0002 | Power Island Off-Design Heat Balances | case book | IEC | process | HMB | approval | ACCEPTED | A | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-09-07 | 2026-09-28 |  | 2026-10-26 | 2026-11-02
1 | ALP-EPC-00GQA-CM-MDB-0001 | Storm Water Drainage - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-06 | 2026-11-25 |  | 2026-11-25 | 2026-12-02 | capacity commissioning
1 | ALP-EPC-00000-CV-RPT-0003 | Topographic Survey and Site Setting-Out Report |  | EPC | civil | RPT | review | IFR | A |  | await Owner review of IFR |  |  | - |  |  | 2026-11-02 | 2026-11-20 |  | 2026-12-04 | 2026-12-11
1 | ALP-EPC-00000-GE-PRC-0002 | Document Numbering and Document Control Procedure |  | EPC | general | PRC | approval | IFR | A |  | await Owner review of IFR |  |  | - |  |  | 2026-11-02 | 2026-11-13 | 2026-12-11 | 2026-12-11 | 2026-12-18
1 | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report |  | EPC | general | DBR | approval | IFR | A |  | await Owner review of IFR |  |  | - |  |  | 2026-11-02 | 2026-11-16 | 2026-12-21 | 2026-12-21 | 2026-12-28 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
1 | ALP-IEC-10BAT-EL-DSH-0001 | Generator Step-Up Transformers - Supplier Certified Datasheets and Performance Curves | IEC | IEC | electrical | DSH | review | ACCEPTED | 0 | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-09-14 | 2026-09-28 |  | 2026-10-12 | 2026-12-28 |  | G-PRC-FAB MR-EL-102 | 2027-03-22 | G-PRC-FAB MR-EL-102 ACCEPTED
1 | ALP-IEC-10BAT-ME-ITP-0001 | Generator Step-Up Transformers - Supplier Inspection and Test Plan | IEC | IEC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-11-30 |  | 2026-12-21 | 2026-12-28 | PO MR-EL-102 | G-PRC-FAB MR-EL-102 | 2027-03-22 | G-PRC-FAB MR-EL-102 ACCEPTED
1 | ALP-IEC-10HAA-ME-DSH-0001 | HRSG incl. SCR - Supplier Certified Datasheets and Performance Curves | IEC | IEC | mechanical | DSH | review | ACCEPTED | B | 2 | issue IFC | IFC | 0 | yes |  |  | 2026-09-14 | 2026-09-28 |  | 2026-10-12 | 2026-12-28 |  | G-PRC-FAB MR-ME-102 | 2027-03-16 | G-PRC-FAB MR-ME-102 ACCEPTED
1 | ALP-IEC-10HAA-ME-ITP-0001 | HRSG incl. SCR - Supplier Inspection and Test Plan | IEC | IEC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-11-30 |  | 2026-12-21 | 2026-12-28 | PO MR-ME-102 | G-PRC-FAB MR-ME-102 | 2027-03-16 | G-PRC-FAB MR-ME-102 ACCEPTED
1 | ALP-IEC-10MBA-ME-DSH-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Certified Datasheets and Performance Curves | IEC | IEC | mechanical | DSH | review | ACCEPTED | A | 2 | issue IFC | IFC | 0 | yes |  |  | 2026-09-14 | 2026-09-28 |  | 2026-10-12 | 2026-12-28 |  | G-PRC-FAB MR-ME-101 | 2027-03-22 | G-PRC-FAB MR-ME-101 ACCEPTED
1 | ALP-IEC-10MBY-ME-ITP-0001 | Turbine Control System - Supplier Inspection and Test Plan | IEC | IEC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-11-30 |  | 2026-12-21 | 2026-12-28 | PO MR-IC-101 | G-PRC-FAB MR-IC-101 | 2027-02-22 | G-PRC-FAB MR-IC-101 ACCEPTED
1 | ALP-IEC-10MKA-EL-DSH-0001 | Generators, Excitation, GCB and Busducts - Supplier Certified Datasheets and Performance Curves | IEC | IEC | electrical | DSH | review | ACCEPTED | 0 | 2 | issue IFC | IFC | 0 | yes |  |  | 2026-09-14 | 2026-09-28 |  | 2026-10-12 | 2026-12-28 |  | G-PRC-FAB MR-EL-101 | 2027-03-18 | G-PRC-FAB MR-EL-101 ACCEPTED
1 | ALP-IEC-10MKA-ME-ITP-0001 | Generators, Excitation, GCB and Busducts - Supplier Inspection and Test Plan | IEC | IEC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-11-30 |  | 2026-12-21 | 2026-12-28 | PO MR-EL-101 | G-PRC-FAB MR-EL-101 | 2027-03-18 | G-PRC-FAB MR-EL-101 ACCEPTED
1 | ALP-IEC-20MAA-ME-DSH-0001 | Steam Turbine and Condenser - Supplier Certified Datasheets and Performance Curves | IEC | IEC | mechanical | DSH | review | ACCEPTED | 0 | 2 | issue IFC | IFC | 0 | yes |  |  | 2026-09-14 | 2026-09-28 |  | 2026-10-12 | 2026-12-28 |  | G-PRC-FAB MR-ME-103 | 2027-04-07 | G-PRC-FAB MR-ME-103 ACCEPTED
1 | ALP-IEC-20MAA-ME-ITP-0001 | Steam Turbine and Condenser - Supplier Inspection and Test Plan | IEC | IEC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-11-30 |  | 2026-12-21 | 2026-12-28 | PO MR-ME-103 | G-PRC-FAB MR-ME-103 | 2027-04-07 | G-PRC-FAB MR-ME-103 ACCEPTED
1 | ALP-IEC-20MAG-ME-DSH-0001 | Seawater-Cooled Surface Condenser - Datasheet |  | IEC | mechanical | DSH | approval | ACCEPTED | 0 | 2 | issue IFC | IFC | 0 | yes |  |  | 2026-09-14 | 2026-09-28 |  | 2026-10-19 | 2026-12-28
1 | ALP-EPC-00000-GE-PRC-0001 | KKS Identification Manual | project key list and tagging rules | EPC | general | PRC | approval | IFR | A |  | await Owner review of IFR |  |  | - |  |  | 2026-11-02 | 2026-11-20 | 2026-12-25 | 2026-12-25 | 2027-01-01 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
1 | ALP-IEC-10BAT-CV-CAL-0001 | Generator Step-Up Transformers - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IEC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-23 | 2026-12-14 |  | 2026-12-28 | 2027-01-11 | PO MR-EL-102 | G-PRC-FAB MR-EL-102 | 2027-03-22 | G-PRC-FAB MR-EL-102 ACCEPTED
1 | ALP-IEC-10BAT-EL-GAD-0001 | Generator Step-Up Transformers - Supplier GA Drawings | IEC | IEC | electrical | GAD | review | ACCEPTED | 0 | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-08-31 | 2026-09-28 |  | 2026-10-12 | 2027-01-11 |  | G-PRC-FAB MR-EL-102 | 2027-03-22 | G-COM-MC-EL 10BAT IFC G-COM-MC-EL 20BAT IFC G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC G-PRC-FAB MR-EL-102 ACCEPTED
1 | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IEC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-23 | 2026-12-14 |  | 2026-12-28 | 2027-01-11 |  | G-PRC-FAB MR-ME-102 | 2027-03-16 | G-PRC-FAB MR-ME-102 ACCEPTED
1 | ALP-IEC-10HAA-ME-GAD-0001 | HRSG incl. SCR - Supplier GA Drawings | IEC | IEC | mechanical | GAD | review | ACCEPTED | 0 | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-08-31 | 2026-09-28 |  | 2026-10-12 | 2027-01-11 |  | G-PRC-FAB MR-ME-102 | 2027-03-16 | G-COM-MC-FF 10HAA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC G-PRC-FAB MR-ME-102 ACCEPTED
1 | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IEC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-23 | 2026-12-14 |  | 2026-12-28 | 2027-01-11 |  | G-PRC-FAB MR-ME-101 | 2027-03-22 | G-PRC-FAB MR-ME-101 ACCEPTED
1 | ALP-IEC-10MBA-ME-GAD-0001 | Gas Turbine Package incl. Auxiliaries - Supplier GA Drawings | IEC | IEC | mechanical | GAD | review | ACCEPTED | 0 | 2 | issue IFC | IFC | 0 | yes |  |  | 2026-08-31 | 2026-09-28 |  | 2026-10-12 | 2027-01-11 |  | G-PRC-FAB MR-ME-101 | 2027-03-22 | G-COM-MC-FF 10MBA IFC G-COM-MC-FF 10MKA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC G-PRC-FAB MR-ME-101 ACCEPTED
1 | ALP-IEC-10MBA-ME-LAY-0001 | Power Island Arrangement - Installation and Maintenance Spaces |  | IEC | mechanical | LAY | approval | ACCEPTED | 0 | 1 | issue IFC | IFC | 0 | yes |  |  | 2026-08-31 | 2026-09-28 |  | 2026-10-26 | 2027-01-11 |  | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-COM-MC-FF 10MBA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC
1 | ALP-IEC-10MBY-ME-DSH-0001 | Turbine Control System - Supplier Certified Datasheets and Performance Curves | IEC | IEC | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-11-30 |  | 2026-12-14 | 2027-01-11 | PO MR-IC-101 | G-PRC-FAB MR-IC-101 | 2027-02-22 | G-PRC-FAB MR-IC-101 ACCEPTED
1 | ALP-IEC-10MKA-CV-CAL-0001 | Generators, Excitation, GCB and Busducts - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IEC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-23 | 2026-12-14 |  | 2026-12-28 | 2027-01-11 | PO MR-EL-101 | G-PRC-FAB MR-EL-101 | 2027-03-18 | G-PRC-FAB MR-EL-101 ACCEPTED
1 | ALP-IEC-20MAA-ME-GAD-0001 | Steam Turbine and Condenser - Supplier GA Drawings | IEC | IEC | mechanical | GAD | review | ACCEPTED | 0 | 2 | issue IFC | IFC | 0 | yes |  |  | 2026-08-31 | 2026-09-28 |  | 2026-10-12 | 2027-01-11 |  | G-PRC-FAB MR-ME-103 | 2027-04-07 | G-COM-MC-FF 20MKA IFC G-COM-MC-WS 20MAA IFC G-COM-MC-WS 20MAG IFC G-CON-CWP CWP-02-ME-01 IFC G-CON-IWP CWP-02-ME-01 IFC G-PRC-FAB MR-ME-103 ACCEPTED
1 | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IF-001 attachment A | IEC | piping | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-01-25 |  | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
1 | ALP-IEC-10MBY-ME-GAD-0001 | Turbine Control System - Supplier GA Drawings | IEC | IEC | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-12-14 |  | 2026-12-28 | 2027-01-25 | PO MR-IC-101 | G-PRC-FAB MR-IC-101 | 2027-02-22 | G-COM-MC-FF 10MBY IFC G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC G-PRC-FAB MR-IC-101 ACCEPTED
1 | ALP-IEC-10MKA-ME-GAD-0001 | Generators, Excitation, GCB and Busducts - Supplier GA Drawings | IEC | IEC | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-12-14 |  | 2026-12-28 | 2027-01-25 | PO MR-EL-101 | G-PRC-FAB MR-EL-101 | 2027-03-18 | G-COM-MC-FF 10MKA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC G-PRC-FAB MR-EL-101 ACCEPTED
1 | ALP-IEC-20MAA-CV-CAL-0001 | Steam Turbine and Condenser - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IEC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-01-25 |  | G-PRC-FAB MR-ME-103 | 2027-04-07 | G-PRC-FAB MR-ME-103 ACCEPTED
1 | ALP-IEC-10BAA-EL-SLD-0001 | Power Island Single Line Diagram | generators, GCB, GSU, UAT tap-offs, SFC | IEC | electrical | SLD | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-25 | 2027-02-08 |  | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
1 | ALP-IEC-10BAT-IC-IOL-0001 | Generator Step-Up Transformers - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IEC | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-EL-102
1 | ALP-IEC-10BAT-ME-CAL-0001 | Generator Step-Up Transformers - Supplier Design Calculations | IEC | IEC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-EL-102 | G-PRC-FAB MR-EL-102 | 2027-03-22 | G-PRC-FAB MR-EL-102 ACCEPTED
1 | ALP-IEC-10HAA-IC-IOL-0001 | HRSG incl. SCR - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IEC | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-ME-102
1 | ALP-IEC-10HAA-ME-CAL-0001 | HRSG incl. SCR - Supplier Design Calculations | IEC | IEC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-ME-102 | G-PRC-FAB MR-ME-102 | 2027-03-16 | G-PRC-FAB MR-ME-102 ACCEPTED
1 | ALP-IEC-10MBA-EL-LST-0001 | Power Island Electrical Load List |  | IEC | electrical | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08
1 | ALP-IEC-10MBA-IC-IOL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IEC | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-ME-101
1 | ALP-IEC-10MBA-ME-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Design Calculations | IEC | IEC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-ME-101 | G-PRC-FAB MR-ME-101 | 2027-03-22 | G-PRC-FAB MR-ME-101 ACCEPTED
1 | ALP-IEC-10MBY-ME-CAL-0001 | Turbine Control System - Supplier Design Calculations | IEC | IEC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-IC-101 | G-PRC-FAB MR-IC-101 | 2027-02-22 | G-PRC-FAB MR-IC-101 ACCEPTED
1 | ALP-IEC-10MKA-IC-IOL-0001 | Generators, Excitation, GCB and Busducts - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IEC | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-EL-101
1 | ALP-IEC-10MKA-ME-CAL-0001 | Generators, Excitation, GCB and Busducts - Supplier Design Calculations | IEC | IEC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-EL-101 | G-PRC-FAB MR-EL-101 | 2027-03-18 | G-PRC-FAB MR-EL-101 ACCEPTED
1 | ALP-IEC-20MAA-IC-IOL-0001 | Steam Turbine and Condenser - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IEC | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-ME-103
1 | ALP-IEC-20MAA-ME-CAL-0001 | Steam Turbine and Condenser - Supplier Design Calculations | IEC | IEC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-02-08 | PO MR-ME-103 | G-PRC-FAB MR-ME-103 | 2027-04-07 | G-PRC-FAB MR-ME-103 ACCEPTED
1 | ALP-IEC-10MBA-HS-RPT-0001 | Power Island Noise Data | ISO 10494 | IEC | hse | RPT | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-01-25 | 2027-02-22
1 | ALP-IEC-10MBA-ME-ITP-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Inspection and Test Plan | IEC | IEC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-11 | 2027-01-25 |  | 2027-02-15 | 2027-02-22 |  | G-PRC-FAB MR-ME-101 | 2027-03-22 | G-PRC-FAB MR-ME-101 ACCEPTED
1 | ALP-IEC-10MBY-IC-BLK-0001 | TCS Architecture and DCS Integration | OPC UA, IEC 62443 zone | IEC | i_and_c | BLK | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-02-08 | 2027-02-22
1 | ALP-IEC-10BAT-EL-WIR-0001 | Generator Step-Up Transformers - Supplier Electrical Schematics and Wiring Diagrams | IEC | IEC | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-EL-102 | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-COM-MC-EL 10BAT IFC G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
1 | ALP-IEC-10BAT-IC-DSH-0001 | Generator Step-Up Transformers - Supplier Instrument List and Datasheets | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-EL-102
1 | ALP-IEC-10HAA-EL-WIR-0001 | HRSG incl. SCR - Supplier Electrical Schematics and Wiring Diagrams | IEC | IEC | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-102 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-COM-MC-FF 10HAA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC
1 | ALP-IEC-10HAA-IC-DSH-0001 | HRSG incl. SCR - Supplier Instrument List and Datasheets, Part 1 of 2 | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-102
1 | ALP-IEC-10HAA-IC-DSH-0002 | HRSG incl. SCR - Supplier Instrument List and Datasheets, Part 2 of 2 | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-102
1 | ALP-IEC-10HAA-PR-PID-0001 | HRSG incl. SCR - Supplier P&IDs | IEC | IEC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2027-01-11 |  | 2027-02-15 | 2027-03-08 |  | G-PRC-FAB MR-ME-102 | 2027-03-16 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-102 ACCEPTED
1 | ALP-IEC-10MBA-EL-WIR-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Electrical Schematics and Wiring Diagrams, Part 1 of 2 | IEC | IEC | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-101 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-COM-MC-FF 10MBA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC
1 | ALP-IEC-10MBA-EL-WIR-0002 | Gas Turbine Package incl. Auxiliaries - Supplier Electrical Schematics and Wiring Diagrams, Part 2 of 2 | IEC | IEC | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-101 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-COM-MC-FF 10MBA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC
1 | ALP-IEC-10MBA-IC-DSH-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Instrument List and Datasheets, Part 1 of 3 | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-101
1 | ALP-IEC-10MBA-IC-DSH-0002 | Gas Turbine Package incl. Auxiliaries - Supplier Instrument List and Datasheets, Part 2 of 3 | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-101
1 | ALP-IEC-10MBA-IC-DSH-0003 | Gas Turbine Package incl. Auxiliaries - Supplier Instrument List and Datasheets, Part 3 of 3 | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-101
1 | ALP-IEC-10MBA-PR-PID-0001 | Gas Turbine Package incl. Auxiliaries - Supplier P&IDs | IEC | IEC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-07 | 2027-01-11 |  | 2027-02-15 | 2027-03-08 |  | G-PRC-FAB MR-ME-101 | 2027-03-22 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-101 ACCEPTED
1 | ALP-IEC-10MBY-EL-WIR-0001 | Turbine Control System - Supplier Electrical Schematics and Wiring Diagrams | IEC | IEC | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-IC-101 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-COM-MC-FF 10MBY IFC G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
1 | ALP-IEC-10MKA-EL-WIR-0001 | Generators, Excitation, GCB and Busducts - Supplier Electrical Schematics and Wiring Diagrams | IEC | IEC | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-EL-101 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-COM-MC-FF 10MKA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC
1 | ALP-IEC-10MKA-IC-DSH-0001 | Generators, Excitation, GCB and Busducts - Supplier Instrument List and Datasheets | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-EL-101
1 | ALP-IEC-20MAA-EL-WIR-0001 | Steam Turbine and Condenser - Supplier Electrical Schematics and Wiring Diagrams | IEC | IEC | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-103 | G-CON-CWP CWP-02-ME-01 | 2027-12-20 | G-COM-MC-WS 20MAA IFC G-CON-CWP CWP-02-ME-01 IFC G-CON-IWP CWP-02-ME-01 IFC
1 | ALP-IEC-20MAA-IC-DSH-0001 | Steam Turbine and Condenser - Supplier Instrument List and Datasheets, Part 1 of 2 | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-103
1 | ALP-IEC-20MAA-IC-DSH-0002 | Steam Turbine and Condenser - Supplier Instrument List and Datasheets, Part 2 of 2 | IEC | IEC | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-28 | 2027-01-11 |  | 2027-01-25 | 2027-03-08 | PO MR-ME-103
1 | ALP-IEC-10BAT-ME-LST-0001 | Generator Step-Up Transformers - Spare Parts and Special Tools Lists | IEC | IEC | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-04 | 2027-01-25 |  | 2027-02-08 | 2027-03-22 | PO MR-EL-102
1 | ALP-IEC-10HAA-ME-LST-0001 | HRSG incl. SCR - Spare Parts and Special Tools Lists | IEC | IEC | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-04 | 2027-01-25 |  | 2027-02-08 | 2027-03-22 | PO MR-ME-102
1 | ALP-IEC-10MBA-ME-LST-0001 | Gas Turbine Package incl. Auxiliaries - Spare Parts and Special Tools Lists | IEC | IEC | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-04 | 2027-01-25 |  | 2027-02-08 | 2027-03-22 | PO MR-ME-101
1 | ALP-IEC-10MBY-ME-LST-0001 | Turbine Control System - Spare Parts and Special Tools Lists | IEC | IEC | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-04 | 2027-01-25 |  | 2027-02-08 | 2027-03-22 | PO MR-IC-101
1 | ALP-IEC-10MKA-EL-RPT-0001 | Generator Capability Curves and Dynamic Models | Grid Code | IEC | electrical | RPT | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-04 | 2027-01-25 |  | 2027-02-08 | 2027-03-22
1 | ALP-IEC-10MKA-ME-LST-0001 | Generators, Excitation, GCB and Busducts - Spare Parts and Special Tools Lists | IEC | IEC | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-04 | 2027-01-25 |  | 2027-02-08 | 2027-03-22 | PO MR-EL-101
1 | ALP-IEC-10MKA-PR-PID-0001 | Generators, Excitation, GCB and Busducts - Supplier P&IDs | IEC | IEC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-25 |  | 2027-03-01 | 2027-03-22 |  | G-PRC-FAB MR-EL-101 | 2027-03-18 | G-OPS-AB 00000 AB G-PRC-FAB MR-EL-101 ACCEPTED
1 | ALP-IEC-20MAA-ME-LST-0001 | Steam Turbine and Condenser - Spare Parts and Special Tools Lists | IEC | IEC | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-04 | 2027-01-25 |  | 2027-02-08 | 2027-03-22 | PO MR-ME-103
1 | ALP-IEC-20MAA-PR-PID-0001 | Steam Turbine and Condenser - Supplier P&IDs | IEC | IEC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-21 | 2027-01-25 |  | 2027-03-01 | 2027-03-22 |  | G-PRC-FAB MR-ME-103 | 2027-04-07 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-103 ACCEPTED
1 | ALP-IEC-10MBY-IC-CNR-0001 | Power Island Operating and Control Description | start-up, load, trips | IEC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-01-18 | 2027-02-08 |  | 2027-02-22 | 2027-04-05
1 | ALP-IEC-10MBA-PI-M3D-0001 | Power Island 3D Model Export | for the plant model | IEC | piping | M3D | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-01 | 2027-02-22 |  | 2027-03-08 | 2027-04-19
1 | ALP-IEC-10MBY-IC-IOL-0001 | Turbine Control System - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IEC | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-01 | 2027-02-22 |  | 2027-03-08 | 2027-04-19
1 | ALP-IEC-10MBY-ME-TST-0001 | Turbine Control System - Factory Acceptance Test Procedure | IEC | IEC | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-03-29 | 2027-04-19 |  | 2027-05-17 | 2027-05-31 | PO MR-IC-101 | G-PRC-FAT MR-IC-101 | 2027-07-12 | G-PRC-FAT MR-IC-101 ACCEPTED
1 | ALP-IEC-10MBY-CM-CMP-0001 | Turbine Control System - Supplier Commissioning Procedures | IEC | IEC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-22 | 2027-03-22 |  | 2027-04-19 | 2027-06-14 | PO MR-IC-101 | G-COM-SC-FF 10MBY | 2028-07-24 | G-COM-SC-FF 10MBY ACCEPTED G-COM-SC-FF 20MAY ACCEPTED
1 | ALP-IEC-10MBY-IC-LOG-0001 | Turbine Control System - Supplier Logic Diagrams, Part 1 of 6 | IEC | IEC | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-22 | 2027-03-22 |  | 2027-04-05 | 2027-06-14 | PO MR-IC-101
1 | ALP-IEC-10MBY-IC-LOG-0002 | Turbine Control System - Supplier Logic Diagrams, Part 2 of 6 | IEC | IEC | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-22 | 2027-03-22 |  | 2027-04-05 | 2027-06-14 | PO MR-IC-101
1 | ALP-IEC-10MBY-IC-LOG-0003 | Turbine Control System - Supplier Logic Diagrams, Part 3 of 6 | IEC | IEC | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-22 | 2027-03-22 |  | 2027-04-05 | 2027-06-14 | PO MR-IC-101
1 | ALP-IEC-10MBY-IC-LOG-0004 | Turbine Control System - Supplier Logic Diagrams, Part 4 of 6 | IEC | IEC | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-22 | 2027-03-22 |  | 2027-04-05 | 2027-06-14 | PO MR-IC-101
1 | ALP-IEC-10MBY-IC-LOG-0005 | Turbine Control System - Supplier Logic Diagrams, Part 5 of 6 | IEC | IEC | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-22 | 2027-03-22 |  | 2027-04-05 | 2027-06-14 | PO MR-IC-101
1 | ALP-IEC-10MBY-IC-LOG-0006 | Turbine Control System - Supplier Logic Diagrams, Part 6 of 6 | IEC | IEC | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-02-22 | 2027-03-22 |  | 2027-04-05 | 2027-06-14 | PO MR-IC-101
1 | ALP-IEC-10MBY-ME-PRC-0001 | Turbine Control System - Supplier Installation and Erection Manual | IEC | IEC | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-04-26 | 2027-05-17 |  | 2027-05-31 | 2027-06-28 | PO MR-IC-101 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFR G-CON-CWP CWP-02-IC-01 IFR
1 | ALP-IEC-10HAA-ME-TST-0001 | HRSG incl. SCR - Factory Acceptance Test Procedure | IEC | IEC | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-05-24 | 2027-06-14 |  | 2027-07-12 | 2027-07-26 | PO MR-ME-102 | G-PRC-FAT MR-ME-102 | 2027-09-06 | G-PRC-FAT MR-ME-102 ACCEPTED
1 | ALP-IEC-10MBY-IC-CBL-0001 | Power Island Cable List | IEC scope and interfaces | IEC | i_and_c | CBL | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-05-10 | 2027-05-31 |  | 2027-05-31 | 2027-07-26 |  | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-COM-MC-FF 10MBY IFC G-COM-MC-FF 20MAY IFC G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
1 | ALP-IEC-10MBY-ME-TRP-0001 | Turbine Control System - Factory Acceptance Test Report | IEC | IEC | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-07-05 | 2027-07-12 |  | 2027-07-26 | 2027-07-26 | PO MR-IC-101 | G-PRC-SHP MR-IC-101 | 2027-08-09 | G-PRC-SHP MR-IC-101 ACCEPTED
1 | ALP-IEC-10MKA-ME-TST-0001 | Generators, Excitation, GCB and Busducts - Factory Acceptance Test Procedure | IEC | IEC | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-05-31 | 2027-06-21 |  | 2027-07-19 | 2027-08-02 | PO MR-EL-101 | G-PRC-FAT MR-EL-101 | 2027-09-13 | G-PRC-FAT MR-EL-101 ACCEPTED
1 | ALP-IEC-10BAT-ME-TST-0001 | Generator Step-Up Transformers - Factory Acceptance Test Procedure | IEC | IEC | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-06-07 | 2027-06-28 |  | 2027-07-26 | 2027-08-09 | PO MR-EL-102 | G-PRC-FAT MR-EL-102 | 2027-09-20 | G-PRC-FAT MR-EL-102 ACCEPTED
1 | ALP-IEC-10HAA-CM-CMP-0001 | HRSG incl. SCR - Supplier Commissioning Procedures | IEC | IEC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-04-19 | 2027-05-17 |  | 2027-06-14 | 2027-08-09 | PO MR-ME-102 | G-COM-SC-FF 10HAA | 2028-07-24 | G-COM-SC-FF 10HAA ACCEPTED G-COM-SC-FF 10HNA ACCEPTED G-COM-SC-FF 10HSA ACCEPTED
1 | ALP-IEC-10MBA-ME-TST-0001 | Gas Turbine Package incl. Auxiliaries - Factory Acceptance Test Procedure | IEC | IEC | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-06-07 | 2027-06-28 |  | 2027-07-26 | 2027-08-09 | PO MR-ME-101 | G-PRC-FAT MR-ME-101 | 2027-09-20 | G-PRC-FAT MR-ME-101 ACCEPTED
1 | ALP-IEC-10MKA-CM-CMP-0001 | Generators, Excitation, GCB and Busducts - Supplier Commissioning Procedures | IEC | IEC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-04-26 | 2027-05-24 |  | 2027-06-21 | 2027-08-16 | PO MR-EL-101 | G-COM-SC-EL 10BAA | 2028-05-09 | G-COM-SC-EL 10BAA ACCEPTED G-COM-SC-EL 10BAC ACCEPTED G-COM-SC-EL 20BAA ACCEPTED G-COM-SC-EL 20BAC ACCEPTED G-COM-SC-FF 10MKA ACCEPTED G-COM-SC-FF 10MKC ACCEPTED G-COM-SC-FF 10MKG ACCEPTED G-COM-SC-FF 20MKA ACCEPTED
1 | ALP-IEC-10BAT-CM-CMP-0001 | Generator Step-Up Transformers - Supplier Commissioning Procedures | IEC | IEC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-05-03 | 2027-05-31 |  | 2027-06-28 | 2027-08-23 | PO MR-EL-102 | G-COM-SC-EL 10BAT | 2028-05-09 | G-COM-SC-EL 10BAT ACCEPTED G-COM-SC-EL 20BAT ACCEPTED
1 | ALP-IEC-10HAA-ME-PRC-0001 | HRSG incl. SCR - Supplier Installation and Erection Manual | IEC | IEC | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-06-21 | 2027-07-12 |  | 2027-07-26 | 2027-08-23 | PO MR-ME-102 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-CON-CWP CWP-01-ME-01 IFR
1 | ALP-IEC-10MBA-CM-CMP-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Commissioning Procedures | IEC | IEC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-05-03 | 2027-05-31 |  | 2027-06-28 | 2027-08-23 | PO MR-ME-101 | G-COM-SC-FF 10MBA | 2028-07-24 | G-COM-SC-FF 10MBA ACCEPTED G-COM-SC-FF 10MBL ACCEPTED G-COM-SC-FF 10MBN ACCEPTED G-COM-SC-FF 10MBP ACCEPTED G-COM-SC-FF 10MBU ACCEPTED G-COM-SC-FF 10MBV ACCEPTED
1 | ALP-IEC-10MKA-ME-PRC-0001 | Generators, Excitation, GCB and Busducts - Supplier Installation and Erection Manual | IEC | IEC | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-06-28 | 2027-07-19 |  | 2027-08-02 | 2027-08-30 | PO MR-EL-101 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-CON-CWP CWP-01-ME-01 IFR G-CON-CWP CWP-02-ME-01 IFR
1 | ALP-IEC-10BAT-ME-PRC-0001 | Generator Step-Up Transformers - Supplier Installation and Erection Manual | IEC | IEC | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-07-05 | 2027-07-26 |  | 2027-08-09 | 2027-09-06 | PO MR-EL-102 | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFR G-CON-CWP CWP-02-EL-01 IFR
1 | ALP-IEC-10MBA-ME-PRC-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Installation and Erection Manual | IEC | IEC | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-06-21 | 2027-07-12 |  | 2027-07-26 | 2027-09-06 |  | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-CON-CWP CWP-01-ME-01 IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-CWP CWP-01-ME-01 IFR G-CON-IWP CWP-01-ME-01 IFC
1 | ALP-IEC-10HAA-ME-TRP-0001 | HRSG incl. SCR - Factory Acceptance Test Report | IEC | IEC | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-08-30 | 2027-09-06 |  | 2027-09-20 | 2027-09-20 | PO MR-ME-102 | G-PRC-SHP MR-ME-102 | 2027-10-04 | G-PRC-SHP MR-ME-102 ACCEPTED
1 | ALP-IEC-10MBY-ME-MDB-0001 | Turbine Control System - Manufacturing Record Book and Conformity Certificates | IEC | IEC | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-07-12 | 2027-07-26 |  | 2027-07-26 | 2027-09-20 | PO MR-IC-101 | G-PRC-SHP MR-IC-101 | 2027-08-09 | G-PRC-SHP MR-IC-101 IFR
1 | ALP-IEC-20MAA-ME-TST-0001 | Steam Turbine and Condenser - Factory Acceptance Test Procedure | IEC | IEC | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-07-19 | 2027-08-09 |  | 2027-09-06 | 2027-09-20 | PO MR-ME-103 | G-PRC-FAT MR-ME-103 | 2027-11-01 | G-PRC-FAT MR-ME-103 ACCEPTED
1 | ALP-IEC-10MKA-ME-TRP-0001 | Generators, Excitation, GCB and Busducts - Factory Acceptance Test Report | IEC | IEC | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-09-06 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-EL-101 | G-PRC-SHP MR-EL-101 | 2027-10-11 | G-PRC-SHP MR-EL-101 ACCEPTED
1 | ALP-IEC-10BAT-ME-TRP-0001 | Generator Step-Up Transformers - Factory Acceptance Test Report | IEC | IEC | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-09-13 | 2027-09-20 |  | 2027-10-04 | 2027-10-04 | PO MR-EL-102 | G-PRC-SHP MR-EL-102 | 2027-10-18 | G-PRC-SHP MR-EL-102 ACCEPTED
1 | ALP-IEC-10MBA-ME-RPT-0001 | Maintenance Concept and Long-Term Service Offer |  | IEC | mechanical | RPT | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-07-19 | 2027-08-09 |  | 2027-08-23 | 2027-10-04
1 | ALP-IEC-10MBA-ME-TRP-0001 | Gas Turbine Package incl. Auxiliaries - Factory Acceptance Test Report | IEC | IEC | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-09-13 | 2027-09-20 |  | 2027-10-04 | 2027-10-04 | PO MR-ME-101 | G-PRC-SHP MR-ME-101 | 2027-10-18 | G-PRC-SHP MR-ME-101 ACCEPTED
1 | ALP-IEC-20MAA-CM-CMP-0001 | Steam Turbine and Condenser - Supplier Commissioning Procedures | IEC | IEC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-06-14 | 2027-07-12 |  | 2027-08-09 | 2027-10-04 | PO MR-ME-103 | G-COM-SC-WS 20MAA | 2028-09-25 | G-COM-SC-WS 20MAA ACCEPTED G-COM-SC-WS 20MAB ACCEPTED G-COM-SC-WS 20MAG ACCEPTED G-COM-SC-WS 20MAJ ACCEPTED G-COM-SC-WS 20MAV ACCEPTED G-COM-SC-WS 20MAW ACCEPTED G-COM-SC-WS 20MAX ACCEPTED
1 | ALP-IEC-20MAA-ME-PRC-0001 | Steam Turbine and Condenser - Supplier Installation and Erection Manual | IEC | IEC | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-08-16 | 2027-09-06 |  | 2027-09-20 | 2027-10-18 | PO MR-ME-103 | G-CON-CWP CWP-02-ME-01 | 2027-12-20 | G-CON-CWP CWP-02-ME-01 IFR
1 | ALP-IEC-10MBY-ME-OMM-0001 | Turbine Control System - Supplier Operation and Maintenance Manual | IEC | IEC | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-05-03 | 2027-06-14 |  | 2027-06-28 | 2027-11-01 | PO MR-IC-101 | G-COM-SC-FF 10MBY | 2028-07-24 | G-COM-SC-FF 10MBY IFR G-COM-SC-FF 20MAY IFR G-OPS-HO-FF 10MBY IFC G-OPS-HO-FF 20MAY IFC
1 | ALP-IEC-10HAA-ME-MDB-0001 | HRSG incl. SCR - Manufacturing Record Book and Conformity Certificates | IEC | IEC | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-09-06 | 2027-09-20 |  | 2027-09-20 | 2027-11-15 | PO MR-ME-102 | G-PRC-SHP MR-ME-102 | 2027-10-04 | G-PRC-SHP MR-ME-102 IFR
1 | ALP-IEC-20MAA-ME-TRP-0001 | Steam Turbine and Condenser - Factory Acceptance Test Report | IEC | IEC | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-10-25 | 2027-11-01 |  | 2027-11-15 | 2027-11-15 | PO MR-ME-103 | G-PRC-SHP MR-ME-103 | 2027-11-29 | G-PRC-SHP MR-ME-103 ACCEPTED
1 | ALP-IEC-10MKA-ME-MDB-0001 | Generators, Excitation, GCB and Busducts - Manufacturing Record Book and Conformity Certificates | IEC | IEC | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-09-13 | 2027-09-27 |  | 2027-09-27 | 2027-11-22 | PO MR-EL-101 | G-PRC-SHP MR-EL-101 | 2027-10-11 | G-PRC-SHP MR-EL-101 IFR
1 | ALP-IEC-10BAT-ME-MDB-0001 | Generator Step-Up Transformers - Manufacturing Record Book and Conformity Certificates | IEC | IEC | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-09-20 | 2027-10-04 |  | 2027-10-04 | 2027-11-29 | PO MR-EL-102 | G-PRC-SHP MR-EL-102 | 2027-10-18 | G-PRC-SHP MR-EL-102 IFR
1 | ALP-IEC-10MBA-ME-MDB-0001 | Gas Turbine Package incl. Auxiliaries - Manufacturing Record Book and Conformity Certificates | IEC | IEC | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-09-20 | 2027-10-04 |  | 2027-10-04 | 2027-11-29 | PO MR-ME-101 | G-PRC-SHP MR-ME-101 | 2027-10-18 | G-PRC-SHP MR-ME-101 IFR
1 | ALP-IEC-10HAA-ME-OMM-0001 | HRSG incl. SCR - Supplier Operation and Maintenance Manual | IEC | IEC | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-06-28 | 2027-08-09 |  | 2027-08-23 | 2027-12-27 | PO MR-ME-102 | G-COM-SC-FF 10HAA | 2028-07-24 | G-COM-SC-FF 10HAA IFR G-COM-SC-FF 10HNA IFR G-COM-SC-FF 10HSA IFR G-OPS-HO-FF 10HAA IFC G-OPS-HO-FF 10HNA IFC G-OPS-HO-FF 10HSA IFC
1 | ALP-IEC-10MKA-ME-OMM-0001 | Generators, Excitation, GCB and Busducts - Supplier Operation and Maintenance Manual | IEC | IEC | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-07-05 | 2027-08-16 |  | 2027-08-30 | 2028-01-03 | PO MR-EL-101 | G-COM-SC-EL 10BAA | 2028-05-09 | G-COM-SC-EL 10BAA IFR G-COM-SC-EL 10BAC IFR G-COM-SC-EL 20BAA IFR G-COM-SC-EL 20BAC IFR G-COM-SC-FF 10MKA IFR G-COM-SC-FF 10MKC IFR G-COM-SC-FF 10MKG IFR G-COM-SC-FF 20MKA IFR
1 | ALP-IEC-10BAT-ME-OMM-0001 | Generator Step-Up Transformers - Supplier Operation and Maintenance Manual | IEC | IEC | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-07-12 | 2027-08-23 |  | 2027-09-06 | 2028-01-10 | PO MR-EL-102 | G-COM-SC-EL 10BAT | 2028-05-09 | G-COM-SC-EL 10BAT IFR G-COM-SC-EL 20BAT IFR G-OPS-HO-EL 10BAT IFC G-OPS-HO-EL 20BAT IFC
1 | ALP-IEC-20MAA-ME-MDB-0001 | Steam Turbine and Condenser - Manufacturing Record Book and Conformity Certificates | IEC | IEC | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-11-01 | 2027-11-15 |  | 2027-11-15 | 2028-01-10 | PO MR-ME-103 | G-PRC-SHP MR-ME-103 | 2027-11-29 | G-PRC-SHP MR-ME-103 IFR
1 | ALP-EPC-10BAA-CM-MDB-0001 | GT Generator Busduct - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 10BAA | 2028-04-11 | G-COM-MC-EL 10BAA IFR G-COM-SC-EL 10BAA IFR G-OPS-HO-EL 10BAA IFC
1 | ALP-EPC-10BAC-CM-MDB-0001 | GT Generator Circuit Breaker - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 10BAC | 2028-04-11 | G-COM-MC-EL 10BAC IFR G-COM-SC-EL 10BAC IFR G-OPS-HO-EL 10BAC IFC
1 | ALP-EPC-10BAT-CM-MDB-0001 | GT Generator Step-Up Transformer - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 10BAT | 2028-04-11 | G-COM-MC-EL 10BAT IFR G-COM-SC-EL 10BAT IFR G-OPS-HO-EL 10BAT IFC
1 | ALP-EPC-20BAA-CM-MDB-0001 | ST Generator Busduct - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-01-18 | 2028-02-01 |  | 2028-02-01 | 2028-02-08 | capacity commissioning | G-COM-MC-EL 20BAA | 2028-04-11 | G-COM-MC-EL 20BAA IFR G-COM-SC-EL 20BAA IFR G-OPS-HO-EL 20BAA IFC
1 | ALP-EPC-20BAC-CM-MDB-0001 | ST Generator Circuit Breaker - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-01-18 | 2028-02-01 |  | 2028-02-01 | 2028-02-08 | capacity commissioning | G-COM-MC-EL 20BAC | 2028-04-11 | G-COM-MC-EL 20BAC IFR G-COM-SC-EL 20BAC IFR G-OPS-HO-EL 20BAC IFC
1 | ALP-EPC-20BAT-CM-MDB-0001 | ST Generator Step-Up Transformer - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-01-18 | 2028-02-01 |  | 2028-02-01 | 2028-02-08 | capacity commissioning | G-COM-MC-EL 20BAT | 2028-04-11 | G-COM-MC-EL 20BAT IFR G-COM-SC-EL 20BAT IFR G-OPS-HO-EL 20BAT IFC
1 | ALP-IEC-20MAA-ME-OMM-0001 | Steam Turbine and Condenser - Supplier Operation and Maintenance Manual | IEC | IEC | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-08-23 | 2027-10-04 |  | 2027-10-18 | 2028-02-21 | PO MR-ME-103 | G-COM-SC-WS 20MAA | 2028-09-25 | G-COM-SC-WS 20MAA IFR G-COM-SC-WS 20MAB IFR G-COM-SC-WS 20MAG IFR G-COM-SC-WS 20MAJ IFR G-COM-SC-WS 20MAV IFR G-COM-SC-WS 20MAW IFR G-COM-SC-WS 20MAX IFR G-OPS-HO-WS 20MAA IFC
1 | ALP-EPC-10HAA-CM-MDB-0001 | HRSG Pressure System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 10HAA | 2028-06-26 | G-COM-MC-FF 10HAA IFR G-COM-SC-FF 10HAA IFR G-OPS-HO-FF 10HAA IFC
1 | ALP-EPC-10HNA-CM-MDB-0001 | HRSG Flue Gas Ducting - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 10HNA | 2028-06-26 | G-COM-MC-FF 10HNA IFR G-COM-SC-FF 10HNA IFR G-OPS-HO-FF 10HNA IFC
1 | ALP-EPC-10HSA-CM-MDB-0001 | SCR Catalyst and Ammonia Injection - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 10HSA | 2028-06-26 | G-COM-MC-FF 10HSA IFR G-COM-SC-FF 10HSA IFR G-OPS-HO-FF 10HSA IFC
1 | ALP-EPC-10MBA-CM-MDB-0001 | Gas Turbine - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 10MBA | 2028-06-26 | G-COM-MC-FF 10MBA IFR G-COM-SC-FF 10MBA IFR G-OPS-HO-FF 10MBA IFC
1 | ALP-EPC-10MBL-CM-MDB-0001 | GT Inlet Air System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 10MBL | 2028-06-26 | G-COM-MC-FF 10MBL IFR G-COM-SC-FF 10MBL IFR G-OPS-HO-FF 10MBL IFC
1 | ALP-EPC-10MBN-CM-MDB-0001 | GT Liquid Fuel and Water Injection - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 10MBN | 2028-06-26 | G-COM-MC-FF 10MBN IFR G-COM-SC-FF 10MBN IFR G-OPS-HO-FF 10MBN IFC
1 | ALP-EPC-10MBP-CM-MDB-0001 | GT Fuel Gas System incl. Performance Heater - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 10MBP | 2028-06-26 | G-COM-MC-FF 10MBP IFR G-COM-SC-FF 10MBP IFR G-OPS-HO-FF 10MBP IFC
1 | ALP-EPC-10MBU-CM-MDB-0001 | GT Compressor Washing - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 10MBU | 2028-06-26 | G-COM-MC-FF 10MBU IFR G-COM-SC-FF 10MBU IFR G-OPS-HO-FF 10MBU IFC
1 | ALP-EPC-10MBV-CM-MDB-0001 | GT Lube Oil System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 10MBV | 2028-06-26 | G-COM-MC-FF 10MBV IFR G-COM-SC-FF 10MBV IFR G-OPS-HO-FF 10MBV IFC
1 | ALP-EPC-10MBY-CM-MDB-0001 | GT Control and Protection - System Turnover Dossier | TCS | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 10MBY | 2028-06-26 | G-COM-MC-FF 10MBY IFR G-COM-SC-FF 10MBY IFR G-OPS-HO-FF 10MBY IFC
1 | ALP-EPC-10MKA-CM-MDB-0001 | GT Generator - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 10MKA | 2028-06-26 | G-COM-MC-FF 10MKA IFR G-COM-SC-FF 10MKA IFR G-OPS-HO-FF 10MKA IFC
1 | ALP-EPC-10MKC-CM-MDB-0001 | GT Excitation and Static Frequency Converter - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 10MKC | 2028-06-26 | G-COM-MC-FF 10MKC IFR G-COM-SC-FF 10MKC IFR G-OPS-HO-FF 10MKC IFC
1 | ALP-EPC-10MKG-CM-MDB-0001 | GT Generator Gas System - System Turnover Dossier | H2/CO2 | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 10MKG | 2028-06-26 | G-COM-MC-FF 10MKG IFR G-COM-SC-FF 10MKG IFR G-OPS-HO-FF 10MKG IFC
1 | ALP-EPC-20MAY-CM-MDB-0001 | ST Control and Protection - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 20MAY | 2028-06-26 | G-COM-MC-FF 20MAY IFR G-COM-SC-FF 20MAY IFR G-OPS-HO-FF 20MAY IFC
1 | ALP-EPC-20MKA-CM-MDB-0001 | ST Generator - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 20MKA | 2028-06-26 | G-COM-MC-FF 20MKA IFR G-COM-SC-FF 20MKA IFR G-OPS-HO-FF 20MKA IFC
1 | ALP-EPC-20MKC-CM-MDB-0001 | ST Excitation - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-01 | 2028-05-15 |  | 2028-05-15 | 2028-05-22 | capacity commissioning | G-COM-MC-FF 20MKC | 2028-06-26 | G-COM-MC-FF 20MKC IFR G-COM-SC-FF 20MKC IFR G-OPS-HO-FF 20MKC IFC
1 | ALP-EPC-20MAA-CM-MDB-0001 | HP Turbine - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 20MAA | 2028-08-28 | G-COM-MC-WS 20MAA IFR G-COM-SC-WS 20MAA IFR G-OPS-HO-WS 20MAA IFC
1 | ALP-EPC-20MAB-CM-MDB-0001 | IP/LP Turbine - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 20MAB | 2028-08-28 | G-COM-MC-WS 20MAB IFR G-COM-SC-WS 20MAB IFR G-OPS-HO-WS 20MAB IFC
1 | ALP-EPC-20MAG-CM-MDB-0001 | Condensing System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-06-05 | 2028-06-19 |  | 2028-06-19 | 2028-06-26 | capacity commissioning | G-COM-MC-WS 20MAG | 2028-08-28 | G-COM-MC-WS 20MAG IFR G-COM-SC-WS 20MAG IFR G-OPS-HO-WS 20MAG IFC
1 | ALP-EPC-20MAJ-CM-MDB-0001 | Condenser Vacuum System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-06-05 | 2028-06-19 |  | 2028-06-19 | 2028-06-26 | capacity commissioning | G-COM-MC-WS 20MAJ | 2028-08-28 | G-COM-MC-WS 20MAJ IFR G-COM-SC-WS 20MAJ IFR G-OPS-HO-WS 20MAJ IFC
1 | ALP-EPC-20MAV-CM-MDB-0001 | ST Lube Oil System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-06-05 | 2028-06-19 |  | 2028-06-19 | 2028-06-26 | capacity commissioning | G-COM-MC-WS 20MAV | 2028-08-28 | G-COM-MC-WS 20MAV IFR G-COM-SC-WS 20MAV IFR G-OPS-HO-WS 20MAV IFC
1 | ALP-EPC-20MAW-CM-MDB-0001 | Gland Steam System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-06-05 | 2028-06-19 |  | 2028-06-19 | 2028-06-26 | capacity commissioning | G-COM-MC-WS 20MAW | 2028-08-28 | G-COM-MC-WS 20MAW IFR G-COM-SC-WS 20MAW IFR G-OPS-HO-WS 20MAW IFC
1 | ALP-EPC-20MAX-CM-MDB-0001 | ST Control Fluid System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-06-05 | 2028-06-19 |  | 2028-06-19 | 2028-06-26 | capacity commissioning | G-COM-MC-WS 20MAX | 2028-08-28 | G-COM-MC-WS 20MAX IFR G-COM-SC-WS 20MAX IFR G-OPS-HO-WS 20MAX IFC
1 | ALP-IEC-10MBA-ME-OMM-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Operation and Maintenance Manual | IEC | IEC | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2028-01-24 | 2028-03-06 |  | 2028-03-20 | 2028-07-24 |  | G-COM-SC-FF 10MBA | 2028-07-24 | G-COM-SC-FF 10MBA IFR G-COM-SC-FF 10MBL IFR G-COM-SC-FF 10MBN IFR G-COM-SC-FF 10MBP IFR G-COM-SC-FF 10MBU IFR G-COM-SC-FF 10MBV IFR G-OPS-HO-FF 10MBA IFC G-OPS-HO-FF 10MBL IFC
2 | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria |  | EPC | hvac | DBR | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07
2 | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | rotating and static equipment | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07
2 | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | TBDY 2018, Eurocodes | EPC | civil | DBR | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-02 | 2026-11-02 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
2 | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria |  | EPC | electrical | DBR | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-02 | 2026-11-02 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
2 | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy |  | EPC | i_and_c | DBR | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-02 | 2026-11-02 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
2 | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | 9 cases | EPC | process | HMB | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-02 | 2026-11-02 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
2 | ALP-EPC-00000-ME-RPT-0002 | Materials Selection and Corrosion Control Report | marine atmosphere, seawater | EPC | mechanical | RPT | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-12-07 |  | 2026-12-21 | 2026-12-28 | ALP-EPC-00000-GE-DBR-0001
2 | ALP-EPC-00000-ME-SPC-0002 | Painting and Coating Specification | ISO 12944, C5 | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-16 | 2026-12-14 | 2027-01-11 | 2027-01-11 | 2027-01-18 | ALP-EPC-00000-GE-DBR-0001
2 | ALP-EPC-00000-HS-RPT-0001 | EIA Conditions Compliance Matrix |  | EPC | hse | RPT | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-09 | 2026-12-31 |  | 2027-01-14 | 2027-01-21 | capacity hse
2 | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria |  | EPC | piping | SPC | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-20 | 2026-12-18 | 2027-01-15 | 2027-01-15 | 2027-01-22 | capacity piping
2 | ALP-EPC-00000-PC-PRC-0001 | Progress Measurement and Reporting Procedure |  | EPC | project_control | PRC | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-26 | 2026-12-22 | 2027-01-19 | 2027-01-19 | 2027-01-26 | capacity project_control
2 | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | noise, safety distances, escape and access, ergonomics, hazardous substances | EPC | hse | DBR | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-19 | 2026-12-25 | 2027-01-29 | 2027-01-29 | 2027-02-05 | capacity hse | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
2 | ALP-EPC-00000-ME-SPC-0003 | Insulation Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-17 | 2027-02-11 | 2027-03-11 | 2027-03-11 | 2027-03-18 | capacity mechanical
2 | ALP-EPC-00000-HS-PLN-0001 | HSE in Design Plan and Safety-in-Design Register |  | EPC | hse | PLN | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-12-24 | 2027-03-09 | 2027-04-06 | 2027-04-06 | 2027-04-13 | capacity hse
2 | ALP-EPC-00000-GE-LST-0004 | Variation and Change Register | technical proposals | EPC | general | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-20 | 2027-04-07 |  | 2027-04-21 | 2027-05-05 | capacity general | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
2 | ALP-EPC-00000-GE-PRC-0003 | As-Built Documentation and Engineering Database Handover Procedure |  | EPC | general | PRC | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2026-11-25 | 2027-04-05 | 2027-05-03 | 2027-05-03 | 2027-05-10 | capacity general
2 | ALP-EPC-00000-GE-LST-0001 | Codes, Standards and Regulations Register | Appendix A.19 | EPC | general | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-03-23 | 2027-04-14 |  | 2027-04-28 | 2027-05-12 | capacity general | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
2 | ALP-EPC-00000-GE-LST-0002 | Permits and Authorities Register |  | EPC | general | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-03-24 | 2027-04-14 |  | 2027-04-28 | 2027-05-12 | capacity general | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
2 | ALP-EPC-00000-GE-LST-0003 | Tie-in and Terminal Point Register |  | EPC | general | LST | review | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-03-29 | 2027-04-19 |  | 2027-05-03 | 2027-05-17 | capacity general | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
2 | ALP-EPC-00000-GE-PLN-0001 | Engineering Execution Plan | workflow, interfaces, timeline | EPC | general | PLN | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-04-05 | 2027-05-03 | 2027-05-31 | 2027-05-31 | 2027-06-07 | capacity general
2 | ALP-EPC-00000-GE-PLN-0003 | Project Quality Plan | engineering, procurement, construction | EPC | general | PLN | approval | NONE |  |  | issue IFR | IFR | A | yes |  |  | 2027-04-07 | 2027-05-07 | 2027-06-04 | 2027-06-04 | 2027-06-11 | capacity general
3 | ALP-EPC-00000-CV-SPC-0001 | Concrete and Civil Works Specification |  | EPC | civil | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07
3 | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes |  | EPC | piping | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07
3 | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification |  | EPC | structural | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07
3 | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis |  | EPC | civil | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-23 |  | 2026-12-07 | 2026-12-14
3 | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EEMUA 191 / IEC 62682 | EPC | i_and_c | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-23 |  | 2026-12-07 | 2026-12-14
3 | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | IEC 62443, SL2 | EPC | i_and_c | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-23 |  | 2026-12-07 | 2026-12-14
3 | ALP-EPC-00000-PR-CAL-0001 | Performance Guarantee Calculation and Correction Curves |  | EPC | process | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-23 |  | 2026-12-07 | 2026-12-14
3 | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams |  | EPC | process | PFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
3 | ALP-EPC-00000-EL-SPC-0005 | Cable Trays, Earthing and Lighting Materials - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04 |  | G-PRC-ENQ MR-EL-009 | 2026-12-21 | G-PRC-ENQ MR-EL-009 IFR G-PRC-PO MR-EL-009 IFC
3 | ALP-EPC-00000-HS-STU-0002 | Stack Dispersion Confirmation | stack height 65 m | EPC | hse | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-07 |  | 2026-12-21 | 2027-01-04
3 | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification |  | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04
3 | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification |  | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04
3 | ALP-EPC-00000-IC-SPC-0003 | Field Instruments - Technical Specification |  | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04 |  | G-PRC-ENQ MR-IC-004 | 2027-05-24 | G-PRC-ENQ MR-IC-004 IFR G-PRC-PO MR-IC-004 IFC
3 | ALP-EPC-00000-IC-SPC-0004 | Control Valves - Technical Specification |  | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04 |  | G-PRC-ENQ MR-IC-005 | 2027-03-15 | G-PRC-ENQ MR-IC-005 IFR G-PRC-PO MR-IC-005 IFC
3 | ALP-EPC-00000-PR-PFD-0002 | Utility Flow Diagrams | water, air, nitrogen, steam, chemicals | EPC | process | PFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04
3 | ALP-EPC-00000-PR-STU-0001 | Plant Water Balance |  | EPC | process | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-07 |  | 2026-12-21 | 2027-01-04
3 | ALP-EPC-00000-PR-STU-0003 | CW Thermal Plume and Outfall Dispersion Study |  | EPC | process | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-07 |  | 2026-12-21 | 2027-01-04
3 | ALP-EPC-00000-IC-SPC-0005 | DCS Functional Design Specification |  | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-03 | 2026-12-03 | 2026-12-31 | 2026-12-31 | 2027-01-07 | capacity i_and_c
3 | ALP-EPC-00000-EL-SPC-0001 | Power and Control Cable Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-06 | 2026-12-04 | 2027-01-01 | 2027-01-01 | 2027-01-08 | capacity electrical
3 | ALP-EPC-00000-IC-TST-0001 | DCS Site Acceptance Test Procedure |  | EPC | i_and_c | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-16 | 2026-12-11 | 2027-01-08 | 2027-01-08 | 2027-01-15 | capacity i_and_c
3 | ALP-EPC-00000-EL-CAL-0005 | Cathodic Protection Design | marine structures, buried piping and tanks | EPC | electrical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-RPT-0002 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-01-18 | ALP-EPC-00000-ME-RPT-0002
3 | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | design margins, design pressure / temperature, line sizing, overpressure protection API 520/521, utility and site conditions | EPC | process | DBR | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-16 | 2026-12-14 | 2027-01-18 | 2027-01-18 | 2027-01-25 | ALP-EPC-00000-GE-DBR-0001 | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
3 | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List |  | EPC | piping | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-12-18 | 2027-01-08 |  | 2027-01-22 | 2027-01-29 | ALP-EPC-00000-PI-SPC-0002
3 | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-DBR-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-20MAA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-01-18 |  | 2027-02-01 | 2027-02-08 | ALP-IEC-20MAA-CV-CAL-0001
3 | ALP-EPC-00CJA-IC-BLK-0001 | Plant DCS - System Architecture |  | EPC | i_and_c | BLK | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBY-IC-BLK-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-02-01 | 2027-03-08 | 2027-03-08 | 2027-03-15 | ALP-IEC-10MBY-IC-BLK-0001 | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
3 | ALP-EPC-00000-IC-CNR-0001 | Unit Coordination, Load Control, Export Limiter and Fuel Transfer |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBY-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-01 |  | 2027-03-15 | 2027-03-29 | ALP-IEC-10MBY-IC-CNR-0001
3 | ALP-EPC-00000-HS-PLN-0003 | Construction Environmental and Social Management Plan | CESMP | EPC | hse | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-23 | 2027-04-20 | 2027-04-20 | 2027-04-27 | capacity hse
3 | ALP-EPC-00000-HS-PLN-0004 | Waste Management Plan | construction and operation | EPC | hse | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-02 | 2027-04-30 | 2027-04-30 | 2027-05-07 | capacity hse
3 | ALP-EPC-00000-HS-PLN-0002 | Construction HSE Plan and Site Safety Plan | ISO 45001 | EPC | hse | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-09 | 2027-04-06 | 2027-05-04 | 2027-05-04 | 2027-05-11 | ALP-EPC-00000-HS-PLN-0001
3 | ALP-EPC-00000-GE-LST-0005 | As-Built Documentation Index |  | EPC | general | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-PRC-0003 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-04-26 |  | 2027-05-10 | 2027-05-24 | ALP-EPC-00000-GE-PRC-0003 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
3 | ALP-EPC-00000-GE-MDL-0001 | Master Document List | MDL | EPC | general | MDL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-17 |  | 2027-05-17 | 2027-05-24 | ALP-EPC-00000-GE-PLN-0001
3 | ALP-EPC-00000-GE-PLN-0004 | Interface Management Plan | Owner, IEC, TSO, gas network operator | EPC | general | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-LST-0003 is NONE, IFR needs it at IFR |  | 2027-04-19 | 2027-05-17 | 2027-06-14 | 2027-06-14 | 2027-06-21 | ALP-EPC-00000-GE-LST-0003
3 | ALP-EPC-00000-GE-PLN-0002 | Advanced Work Packaging Execution Plan | CWA, CWP, EWP, PWP, IWP | EPC | general | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-31 | 2027-06-28 | 2027-06-28 | 2027-07-05 | ALP-EPC-00000-GE-PLN-0001
3 | ALP-EPC-00000-GE-PLN-0005 | Project Execution Plan |  | EPC | general | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-PLN-0003 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-11 | 2027-07-09 | 2027-07-09 | 2027-07-16 | capacity general
3 | ALP-EPC-00000-EL-CAL-0004 | Lighting Calculation | indoor, outdoor, emergency | EPC | electrical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-10-20 |  | 2027-11-03 | 2027-11-10 | capacity electrical
3 | ALP-EPC-00000-EL-RPT-0001 | Electrical Control and Interlock Philosophy |  | EPC | electrical | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-10-20 |  | 2027-11-03 | 2027-11-10 | capacity electrical
3 | ALP-EPC-00000-EL-SPC-0002 | LV and MV Motor Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-10-27 | 2027-11-24 | 2027-11-24 | 2027-12-01 | capacity electrical
4 | ALP-EPC-00000-PR-LST-0001 | Equipment List |  | EPC | process | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-PFD-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30 |  | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
4 | ALP-EPC-00EGA-PR-SDS-0001 | LDO Unloading - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00EGB-PR-SDS-0001 | LDO Storage - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00EGC-PR-SDS-0001 | LDO Forwarding and Treatment - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00EKA-PR-SDS-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00EKC-PR-SDS-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00GBA-PR-SDS-0001 | Seawater Reverse Osmosis - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00GCA-PR-SDS-0001 | Demineralisation - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00GHA-PR-SDS-0001 | Demineralised Water Storage and Distribution - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00GNA-PR-SDS-0001 | Waste Water Treatment - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00GUA-PR-SDS-0001 | Sanitary Waste Water Treatment - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00LBG-PR-SDS-0001 | Auxiliary Steam - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00LDA-PR-SDS-0001 | Condensate Polishing - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00PAB-PR-SDS-0001 | CW Piping - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00PAC-PR-SDS-0001 | CW Pumps - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00PAH-PR-SDS-0001 | Condenser Tube Cleaning - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00PBA-PR-SDS-0001 | Electro-Chlorination - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00PGA-PR-SDS-0001 | Closed Cooling Water - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00QCA-PR-SDS-0001 | Chemical Dosing - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00QEA-PR-SDS-0001 | Compressed Air - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00QHA-PR-SDS-0001 | Auxiliary Boiler - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00QJA-PR-SDS-0001 | Nitrogen Supply - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00QJB-PR-SDS-0001 | Hydrogen and CO2 Supply - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00QUA-PR-SDS-0001 | Sampling and SWAS - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00SAA-HV-SDS-0001 | HVAC - System Design Description |  | EPC | hvac | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00SGC-PR-SDS-0001 | Deluge, Spray and Foam Systems - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10HAN-PR-SDS-0001 | HRSG Blowdown and Drains - System Design Description | EPC tanks and headers | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10HSB-PR-SDS-0001 | Ammonia Storage and Supply - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10LAB-PR-SDS-0001 | Feedwater Piping - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10LAC-PR-SDS-0001 | Boiler Feed Pumps - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10LAE-PR-SDS-0001 | HP Attemperation Spray Water - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10LAF-PR-SDS-0001 | Reheat Attemperation Spray Water - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10LBA-PR-SDS-0001 | Main Steam Piping - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10LBB-PR-SDS-0001 | Hot Reheat Piping - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10LBC-PR-SDS-0001 | Cold Reheat Piping - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-10LBD-PR-SDS-0001 | LP Steam Piping - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-20LCA-PR-SDS-0001 | Main Condensate Piping - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-20LCB-PR-SDS-0001 | Condensate Extraction Pumps - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-20MAN-PR-SDS-0001 | Turbine Bypass Stations and Piping - System Design Description |  | EPC | process | SDS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30
4 | ALP-EPC-00000-CV-SPC-0004 | Civil and Building Works - Technical Specification |  | EPC | civil | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-CV-002 | 2026-11-23 | G-PRC-ENQ MR-CV-002 IFR G-PRC-PO MR-CV-002 IFC
4 | ALP-EPC-00000-CV-SPC-0005 | Marine Works - Technical Specification |  | EPC | civil | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-CV-003 | 2027-03-05 | G-PRC-ENQ MR-CV-003 IFR G-PRC-PO MR-CV-003 IFC
4 | ALP-EPC-00000-SS-SPC-0002 | Structural Steel Supply and Fabrication - Technical Specification |  | EPC | structural | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-SS-001 | 2027-01-19 | G-PRC-ENQ MR-SS-001 IFR G-PRC-PO MR-SS-001 IFC
4 | ALP-EPC-10HNE-SS-SPC-0001 | Stack 65 m with Silencer - Technical Specification |  | EPC | structural | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-STU-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-SS-002 | 2027-01-11 | G-PRC-ENQ MR-SS-002 IFR G-PRC-PO MR-SS-002 IFC
4 | ALP-EPC-00000-EL-MRQ-0002 | Cable Trays, Earthing and Lighting Materials - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SPC-0005 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-07 |  | 2026-12-07 | 2026-12-10 | ALP-EPC-00000-EL-SPC-0005 | G-PRC-ENQ MR-EL-009 | 2026-12-21 | G-PRC-ENQ MR-EL-009 IFR G-PRC-PO MR-EL-009 IFC
4 | ALP-EPC-00000-IC-MRQ-0001 | Field Instruments - Material Requisition |  | EPC | i_and_c | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0003 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-07 |  | 2026-12-07 | 2026-12-10 | ALP-EPC-00000-IC-SPC-0003 | G-PRC-ENQ MR-IC-004 | 2027-05-24 | G-PRC-ENQ MR-IC-004 IFR G-PRC-PO MR-IC-004 IFC
4 | ALP-EPC-00000-IC-MRQ-0002 | Control Valves - Material Requisition |  | EPC | i_and_c | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0004 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-07 |  | 2026-12-07 | 2026-12-10 | ALP-EPC-00000-IC-SPC-0004 | G-PRC-ENQ MR-IC-005 | 2027-03-15 | G-PRC-ENQ MR-IC-005 IFR G-PRC-PO MR-IC-005 IFC
4 | ALP-EPC-00000-PI-PLT-0001 | Plot Plan |  | EPC | piping | PLT | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
4 | ALP-EPC-00000-PR-RPT-0001 | Cycle Chemistry Concept | AVT(O), sampling, dosing | EPC | process | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-23 |  | 2026-12-07 | 2026-12-14
4 | ALP-EPC-00000-PR-RPT-0002 | Operating Philosophy | start-up, load, shutdown, fuel changeover | EPC | process | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-23 |  | 2026-12-07 | 2026-12-14
4 | ALP-EPC-00000-PR-RPT-0003 | Isolation, Drainage and Venting Philosophy |  | EPC | process | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-05 | 2026-11-30 |  | 2026-12-14 | 2026-12-21 | capacity process
4 | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan |  | EPC | commissioning | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04
4 | ALP-EPC-00000-GE-SPC-0007 | Piping Specialty Items - Technical Specification | strainers, steam traps, expansion joints, sight glasses | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04 |  | G-PRC-ENQ MR-PI-006 | 2027-07-12 | G-PRC-ENQ MR-PI-006 IFR G-PRC-PO MR-PI-006 IFC
4 | ALP-EPC-00000-GE-SPC-0008 | Safety and Relief Valves - Technical Specification |  | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04 |  | G-PRC-ENQ MR-PI-007 | 2027-06-14 | G-PRC-ENQ MR-PI-007 IFR G-PRC-PO MR-PI-007 IFC
4 | ALP-EPC-00000-PI-SPC-0004 | Piping Bulk Materials - Technical Specification | carbon steel, stainless | EPC | piping | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04 |  | G-PRC-ENQ MR-PI-001 | 2027-01-04 | G-PRC-ENQ MR-PI-001 IFR G-PRC-PO MR-PI-001 IFC
4 | ALP-EPC-00000-PR-CAL-0002 | Degradation Curves | recoverable and non-recoverable, output and heat rate | EPC | process | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-CAL-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 |  | 2026-12-28 | 2027-01-04 | ALP-EPC-00000-PR-CAL-0001
4 | ALP-EPC-00000-IC-LST-0002 | Alarm List |  | EPC | i_and_c | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 |  | 2026-12-28 | 2027-01-11 | ALP-EPC-00000-IC-RPT-0001 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
4 | ALP-EPC-00000-IC-TST-0002 | OT Cybersecurity Acceptance Test Procedure | IEC 62443 | EPC | i_and_c | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0002 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 | 2027-01-11 | 2027-01-11 | 2027-01-18 | ALP-EPC-00000-IC-RPT-0002
4 | ALP-EPC-00CJG-IC-BLK-0001 | Safety Instrumented Systems - System Architecture | BOP | EPC | i_and_c | BLK | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0002 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 | 2027-01-11 | 2027-01-11 | 2027-01-18 | ALP-EPC-00000-IC-RPT-0002
4 | ALP-EPC-00CKA-IC-BLK-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Architecture |  | EPC | i_and_c | BLK | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0002 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 | 2027-01-11 | 2027-01-11 | 2027-01-18 | ALP-EPC-00000-IC-RPT-0002
4 | ALP-EPC-00CQA-IC-BLK-0001 | Continuous Emission Monitoring - System Architecture |  | EPC | i_and_c | BLK | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0002 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 | 2027-01-11 | 2027-01-11 | 2027-01-18 | ALP-EPC-00000-IC-RPT-0002
4 | ALP-EPC-00CYA-IC-BLK-0001 | Telecom, CCTV, Access Control, Security - System Architecture |  | EPC | i_and_c | BLK | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0002 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 | 2027-01-11 | 2027-01-11 | 2027-01-18 | ALP-EPC-00000-IC-RPT-0002
4 | ALP-EPC-00SGY-IC-BLK-0001 | Fire Detection and Alarm - System Architecture |  | EPC | i_and_c | BLK | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0002 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 | 2027-01-11 | 2027-01-11 | 2027-01-18 | ALP-EPC-00000-IC-RPT-0002
4 | ALP-EPC-00000-PI-SPC-0006 | Valves - Technical Specification | manual and check | EPC | piping | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-19 | 2026-12-17 | 2027-01-14 | 2027-01-14 | 2027-01-21 | capacity piping | G-PRC-ENQ MR-PI-003 | 2027-04-12 | G-PRC-ENQ MR-PI-003 IFR G-PRC-PO MR-PI-003 IFC
4 | ALP-EPC-00000-CV-SPC-0002 | Piling Specification |  | EPC | civil | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-21 | 2027-01-18 | 2027-01-18 | 2027-01-25 | ALP-EPC-00000-CV-RPT-0001
4 | ALP-EPC-00ACA-IC-DSH-0001 | 380 kV GIS Switchyard - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-28 | 2027-01-18 | 2027-01-18 | 2027-01-25 | ALP-EPC-00000-IC-SPC-0001
4 | ALP-EPC-10BBT-IC-DSH-0001 | GT Unit Auxiliary Transformer - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-12-01 | 2026-12-30 | 2027-01-20 | 2027-01-20 | 2027-01-27 | capacity i_and_c
4 | ALP-EPC-00000-EL-SPC-0004 | Power and Control Cables - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-04 | 2027-01-01 | 2027-01-29 | 2027-01-29 | 2027-02-05 | ALP-EPC-00000-EL-SPC-0001 | G-PRC-ENQ MR-EL-008 | 2027-05-03 | G-PRC-ENQ MR-EL-008 IFR G-PRC-PO MR-EL-008 IFC
4 | ALP-EPC-00CKA-IC-LOG-0001 | Historian, Performance Monitoring and Operator Training Simulator - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-11-24 | 2027-01-04 | 2027-02-01 | 2027-02-01 | 2027-02-08 | capacity i_and_c
4 | ALP-EPC-00CQA-IC-DSH-0002 | Continuous Emission Monitoring - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-11 | 2027-02-01 | 2027-02-01 | 2027-02-08 | capacity i_and_c
4 | ALP-EPC-00XJA-IC-DSH-0001 | Emergency Diesel Generator - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-11 | 2027-02-01 | 2027-02-01 | 2027-02-08 | capacity i_and_c
4 | ALP-EPC-20BBT-IC-DSH-0001 | ST Unit Auxiliary Transformer - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-13 | 2027-02-03 | 2027-02-03 | 2027-02-10 | capacity i_and_c
4 | ALP-EPC-10HNE-IC-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-12-21 | 2027-01-19 | 2027-02-09 | 2027-02-09 | 2027-02-16 | capacity i_and_c
4 | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | rotating and static equipment codes, margins, NPSH, vibration, noise, materials and corrosion allowance | EPC | mechanical | DBR | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-11 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-PR-DBR-0001 | G-OWN-BDP 00000 | 2027-04-02 | G-OWN-BDP 00000 ACCEPTED
4 | ALP-EPC-00ACA-IC-LOG-0001 | 380 kV GIS Switchyard - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2027-01-21 | 2027-02-18 | 2027-02-18 | 2027-02-25 | capacity i_and_c
4 | ALP-EPC-00CYA-IC-LOG-0001 | Telecom, CCTV, Access Control, Security - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-21 | 2027-02-18 | 2027-02-18 | 2027-02-25 | capacity i_and_c
4 | ALP-EPC-00BMA-IC-LOG-0001 | Emergency LV Switchgear - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-01-22 | 2027-02-19 | 2027-02-19 | 2027-02-26 | capacity i_and_c
4 | ALP-EPC-00BTA-IC-LOG-0001 | Batteries and DC 220 V - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-08 | 2027-01-25 | 2027-02-22 | 2027-02-22 | 2027-03-01 | capacity i_and_c
4 | ALP-EPC-00UAC-CV-CAL-0001 | GIS Building - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-08 |  | 2027-02-22 | 2027-03-01 | ALP-EPC-00000-CV-CAL-0001
4 | ALP-EPC-00SMA-IC-LOG-0001 | Cranes and Hoists - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-26 | 2027-02-23 | 2027-02-23 | 2027-03-02 | capacity i_and_c
4 | ALP-EPC-00UPC-CV-CAL-0001 | CW Pump House - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-09 |  | 2027-02-23 | 2027-03-02 | ALP-EPC-00000-CV-CAL-0001
4 | ALP-EPC-00UZD-CV-CAL-0001 | Pipe Racks and Pipe Sleepers - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-10 |  | 2027-02-24 | 2027-03-03 | ALP-EPC-00000-CV-CAL-0001
4 | ALP-EPC-00XJA-IC-LOG-0001 | Emergency Diesel Generator - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-16 | 2027-01-27 | 2027-02-24 | 2027-02-24 | 2027-03-03 | capacity i_and_c
4 | ALP-EPC-00BLA-IC-LOG-0001 | Lighting and Small Power - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-02 | 2027-01-28 | 2027-02-25 | 2027-02-25 | 2027-03-04 | capacity i_and_c
4 | ALP-EPC-00CQA-IC-LOG-0001 | Continuous Emission Monitoring - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-28 | 2027-02-25 | 2027-02-25 | 2027-03-04 | capacity i_and_c
4 | ALP-EPC-10BBT-IC-LOG-0001 | GT Unit Auxiliary Transformer - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-22 | 2027-01-29 | 2027-02-26 | 2027-02-26 | 2027-03-05 | capacity i_and_c
4 | ALP-EPC-00BRA-IC-LOG-0001 | UPS - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-02-01 | 2027-03-01 | 2027-03-01 | 2027-03-08 | capacity i_and_c
4 | ALP-EPC-00CJA-IC-LOG-0001 | Plant DCS - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-10 | 2027-02-04 | 2027-03-04 | 2027-03-04 | 2027-03-11 | capacity i_and_c
4 | ALP-EPC-00UEG-CV-CAL-0001 | LDO Tank Farm Structures - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-02-25 |  | 2027-03-11 | 2027-03-18 | capacity civil
4 | ALP-EPC-00UBA-CV-CAL-0001 | Electrical Building - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-02 |  | 2027-03-16 | 2027-03-23 | capacity civil
4 | ALP-EPC-00UGA-CV-CAL-0001 | Water Treatment Building and Basins - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-03 |  | 2027-03-17 | 2027-03-24 | capacity civil
4 | ALP-EPC-20BBT-IC-LOG-0001 | ST Unit Auxiliary Transformer - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-29 | 2027-02-23 | 2027-03-23 | 2027-03-23 | 2027-03-30 | capacity i_and_c
4 | ALP-EPC-00BXA-GE-SPC-0001 | Cathodic Protection - Technical Specification | marine structures, buried piping and tanks | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0005 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-25 | 2027-03-25 | 2027-03-25 | 2027-04-01 | capacity general | G-PRC-ENQ MR-EL-010 | 2027-04-26 | G-PRC-ENQ MR-EL-010 IFR G-PRC-PO MR-EL-010 IFC
4 | ALP-EPC-00UQA-CV-CAL-0001 | Utility Building - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-03-29 |  | 2027-04-12 | 2027-04-19 | capacity civil
4 | ALP-EPC-00UCA-CV-CAL-0001 | Control Building - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-03-31 |  | 2027-04-14 | 2027-04-21 | capacity civil
4 | ALP-EPC-00USA-CV-CAL-0001 | Workshop and Warehouse - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-03-31 |  | 2027-04-14 | 2027-04-21 | capacity civil
4 | ALP-EPC-00UYA-CV-CAL-0001 | Administration Building - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-12 | 2027-04-02 |  | 2027-04-16 | 2027-04-23 | capacity civil
4 | ALP-EPC-00000-GE-SPC-0006 | Pipe Supports, Spring Hangers and Snubbers - Technical Specification |  | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-22 | 2027-04-19 | 2027-04-19 | 2027-04-26 | capacity general | G-PRC-ENQ MR-PI-005 | 2027-07-12 | G-PRC-ENQ MR-PI-005 IFR G-PRC-PO MR-PI-005 IFC
4 | ALP-EPC-10UMA-CV-CAL-0001 | Gas Turbine Hall - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-05 |  | 2027-04-19 | 2027-04-26 | capacity civil
4 | ALP-EPC-20UMB-CV-CAL-0001 | Steam Turbine Hall - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-IEC-20MAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-12 | 2027-04-05 |  | 2027-04-19 | 2027-04-26 | capacity civil
4 | ALP-EPC-00000-HS-RPT-0003 | Soil and Groundwater Baseline Survey Report |  | EPC | hse | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-23 | 2027-04-13 |  | 2027-04-27 | 2027-05-04 | capacity hse
4 | ALP-EPC-00000-GE-SPC-0003 | Instrument Installation Materials - Technical Specification | tubing, fittings, junction boxes, supports | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2027-04-02 | 2027-04-30 | 2027-04-30 | 2027-05-07 | capacity general | G-PRC-ENQ MR-IC-010 | 2027-10-25 | G-PRC-ENQ MR-IC-010 IFR G-PRC-PO MR-IC-010 IFC
4 | ALP-EPC-00UEK-CV-CAL-0001 | Gas Station Structures - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-04-06 | 2027-04-27 |  | 2027-05-11 | 2027-05-18 | capacity civil
4 | ALP-EPC-00UBF-CV-CAL-0001 | Transformer Bays - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-03 |  | 2027-05-17 | 2027-05-24 | capacity civil
4 | ALP-EPC-00000-CV-RPT-0002 | Dewatering Design and Discharge Plan |  | EPC | civil | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2027-05-06 |  | 2027-05-20 | 2027-05-27 | capacity civil
4 | ALP-EPC-00UPA-CV-RPT-0001 | Marine Route Survey for Intake and Outfall Pipelines | bathymetry, geophysics | EPC | civil | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2027-05-11 |  | 2027-05-25 | 2027-06-01 | capacity civil
4 | ALP-EPC-00UZF-CV-CAL-0001 | Temporary Barge Landing - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-04-29 | 2027-05-21 |  | 2027-06-04 | 2027-06-11 | capacity civil
4 | ALP-EPC-00UPA-CV-CAL-0001 | CW Intake and Outfall Marine Structures - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-05-27 |  | 2027-06-10 | 2027-06-17 | capacity civil
4 | ALP-EPC-00000-CV-STU-0001 | Site-Specific Seismic Hazard Study | DD-2 / DD-3 | EPC | civil | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2027-05-21 |  | 2027-06-04 | 2027-06-18 | capacity civil
4 | ALP-EPC-00000-PR-STU-0002 | Reliability, Availability and Maintainability Study |  | EPC | process | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-10 | 2027-05-24 |  | 2027-06-07 | 2027-06-21 | capacity process
4 | ALP-EPC-00UZB-CV-CAL-0001 | Fencing and Gates - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-07 | 2027-06-01 |  | 2027-06-15 | 2027-06-22 | capacity civil
4 | ALP-EPC-00000-PR-LST-0003 | Chemical Consumption, Effluent and Emission Inventory |  | EPC | process | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-STU-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-05-27 |  | 2027-06-10 | 2027-06-24 | capacity process | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
4 | ALP-EPC-00UZA-CV-CAL-0001 | Roads and Paving - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-05 | 2027-06-03 |  | 2027-06-17 | 2027-06-24 | capacity civil
4 | ALP-EPC-00000-PI-SPC-0003 | Welding, Heat Treatment and NDE Specification |  | EPC | piping | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-12-01 | 2027-05-21 | 2027-06-18 | 2027-06-18 | 2027-06-25 | capacity piping
4 | ALP-EPC-00000-PR-STU-0004 | Carbon Capture Readiness Study |  | EPC | process | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2027-06-01 |  | 2027-06-15 | 2027-06-29 | capacity process
4 | ALP-EPC-00UZC-CV-CAL-0001 | Site Drainage and Culverts - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-11 | 2027-06-09 |  | 2027-06-23 | 2027-06-30 | capacity civil
4 | ALP-EPC-00UZE-CV-CAL-0001 | Cable Trenches and Duct Banks - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-12 | 2027-06-09 |  | 2027-06-23 | 2027-06-30 | capacity civil
4 | ALP-EPC-10UHN-CV-CAL-0001 | Stack Foundation - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-19 | 2027-06-09 |  | 2027-06-23 | 2027-06-30 | capacity civil
4 | ALP-EPC-10UHA-CV-CAL-0001 | HRSG Foundations and Structures - Structural and Foundation Calculation |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-10 |  | 2027-06-24 | 2027-07-01 | capacity civil
4 | ALP-EPC-00000-PC-SCH-0001 | Level 3 Project Schedule | CPM | EPC | project_control | SCH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MDL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-GE-PLN-0002 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-21 |  | 2027-07-05 | 2027-07-12 | ALP-EPC-00000-GE-PLN-0002
4 | ALP-EPC-00000-CM-CMP-0002 | Performance Test Procedure | ASME PTC 46 | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-CAL-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2027-07-14 | 2027-08-11 | 2027-08-11 | 2027-08-18 | capacity commissioning | G-OWN-TOC 00000 | 2028-08-21 | G-OWN-TOC 00000 ACCEPTED
4 | ALP-EPC-00SGY-IC-LOG-0001 | Fire Detection and Alarm - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-09-29 | 2027-10-27 | 2027-10-27 | 2027-11-03 | capacity i_and_c
4 | ALP-EPC-10HNE-IC-LOG-0001 | Stack 65 m with CEMS Platform and Silencer - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-09-29 | 2027-10-27 | 2027-10-27 | 2027-11-03 | capacity i_and_c
5 | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition |  | EPC | civil | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-SPC-0004 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-CV-002 | 2026-11-23 | G-PRC-ENQ MR-CV-002 IFR G-PRC-PO MR-CV-002 IFC
5 | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition |  | EPC | civil | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-SPC-0005 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-CV-003 | 2027-03-05 | G-PRC-ENQ MR-CV-003 IFR G-PRC-PO MR-CV-003 IFC
5 | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition |  | EPC | structural | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-SPC-0002 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-09 |  | 2026-11-09 | 2026-11-12 |  | G-PRC-ENQ MR-SS-001 | 2027-01-19 | G-PRC-ENQ MR-SS-001 IFR G-PRC-PO MR-SS-001 IFC
5 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List |  | EPC | electrical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-LST-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-EL-LST-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30 |  | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
5 | ALP-EPC-10HNE-ME-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
5 | ALP-EPC-00000-CV-SPC-0003 | Piling Works - Technical Specification |  | EPC | civil | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-CV-001 | 2027-02-01 | G-PRC-ENQ MR-CV-001 IFR G-PRC-PO MR-CV-001 IFC
5 | ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification |  | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CQA-IC-BLK-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-IC-002 | 2027-05-03 | G-PRC-ENQ MR-IC-002 IFR G-PRC-PO MR-IC-002 IFC
5 | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-016 | 2026-11-16 | G-PRC-ENQ MR-ME-016 IFR G-PRC-PO MR-ME-016 IFC
5 | ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | API 650 | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-017 | 2027-05-17 | G-PRC-ENQ MR-ME-017 IFR G-PRC-PO MR-ME-017 IFC
5 | ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-015 | 2026-11-16 | G-PRC-ENQ MR-ME-015 IFR G-PRC-PO MR-ME-015 IFC
5 | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-013 | 2027-03-29 | G-PRC-ENQ MR-ME-013 IFR G-PRC-PO MR-ME-013 IFC
5 | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-014 | 2027-03-22 | G-PRC-ENQ MR-ME-014 IFR G-PRC-PO MR-ME-014 IFC
5 | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | SWRO, demin, condensate polishing | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GCA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-012 | 2026-11-16 | G-PRC-ENQ MR-ME-012 IFR G-PRC-PO MR-ME-012 IFC
5 | ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-004 | 2027-02-01 | G-PRC-ENQ MR-ME-004 IFR G-PRC-PO MR-ME-004 IFC
5 | ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-003 | 2026-11-23 | G-PRC-ENQ MR-ME-003 IFR G-PRC-PO MR-ME-003 IFC
5 | ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-006 | 2027-04-26 | G-PRC-ENQ MR-ME-006 IFR G-PRC-PO MR-ME-006 IFC
5 | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-005 | 2027-02-01 | G-PRC-ENQ MR-ME-005 IFR G-PRC-PO MR-ME-005 IFC
5 | ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-007 | 2027-01-25 | G-PRC-ENQ MR-ME-007 IFR G-PRC-PO MR-ME-007 IFC
5 | ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-011 | 2027-04-05 | G-PRC-ENQ MR-ME-011 IFR G-PRC-PO MR-ME-011 IFC
5 | ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-008 | 2027-01-25 | G-PRC-ENQ MR-ME-008 IFR G-PRC-PO MR-ME-008 IFC
5 | ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-009 | 2026-11-16 | G-PRC-ENQ MR-ME-009 IFR G-PRC-PO MR-ME-009 IFC
5 | ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-010 | 2027-05-10 | G-PRC-ENQ MR-ME-010 IFR G-PRC-PO MR-ME-010 IFC
5 | ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification |  | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-IC-003 | 2027-05-03 | G-PRC-ENQ MR-IC-003 IFR G-PRC-PO MR-IC-003 IFC
5 | ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification |  | EPC | hvac | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-HV-001 | 2027-01-04 | G-PRC-ENQ MR-HV-001 IFR G-PRC-PO MR-HV-001 IFC
5 | ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-020 | 2027-01-11 | G-PRC-ENQ MR-ME-020 IFR G-PRC-PO MR-ME-020 IFC
5 | ALP-EPC-00SMA-ME-SPC-0001 | EOT Cranes - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-021 | 2026-11-30 | G-PRC-ENQ MR-ME-021 IFR G-PRC-PO MR-ME-021 IFC
5 | ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-019 | 2027-03-15 | G-PRC-ENQ MR-ME-019 IFR G-PRC-PO MR-ME-019 IFC
5 | ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-018 | 2027-01-25 | G-PRC-ENQ MR-ME-018 IFR G-PRC-PO MR-ME-018 IFC
5 | ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-001 | 2026-11-16 | G-PRC-ENQ MR-ME-001 IFR G-PRC-PO MR-ME-001 IFC
5 | ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification |  | EPC | mechanical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-ME-002 | 2027-02-01 | G-PRC-ENQ MR-ME-002 IFR G-PRC-PO MR-ME-002 IFC
5 | ALP-EPC-00000-GE-MRQ-0007 | Piping Specialty Items - Material Requisition | strainers, steam traps, expansion joints, sight glasses | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0007 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-07 |  | 2026-12-07 | 2026-12-10 | ALP-EPC-00000-GE-SPC-0007 | G-PRC-ENQ MR-PI-006 | 2027-07-12 | G-PRC-ENQ MR-PI-006 IFR G-PRC-PO MR-PI-006 IFC
5 | ALP-EPC-00000-GE-MRQ-0008 | Safety and Relief Valves - Material Requisition |  | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0008 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-07 |  | 2026-12-07 | 2026-12-10 | ALP-EPC-00000-GE-SPC-0008 | G-PRC-ENQ MR-PI-007 | 2027-06-14 | G-PRC-ENQ MR-PI-007 IFR G-PRC-PO MR-PI-007 IFC
5 | ALP-EPC-00000-PI-MRQ-0001 | Piping Bulk Materials - Material Requisition | carbon steel, stainless | EPC | piping | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0004 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-07 |  | 2026-12-07 | 2026-12-10 | ALP-EPC-00000-PI-SPC-0004 | G-PRC-ENQ MR-PI-001 | 2027-01-04 | G-PRC-ENQ MR-PI-001 IFR G-PRC-PO MR-PI-001 IFC
5 | ALP-EPC-00UZA-CV-CVL-0001 | Temporary Facilities and Construction Site Layout | TP-A1 | EPC | civil | CVL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-01 |  | 2026-12-01 | 2026-12-15 |  | G-CON-CWP CWP-12-CV-01 | 2027-01-18 | G-CON-CWP CWP-12-CV-01 IFC G-CON-IWP CWP-12-CV-01 IFC
5 | ALP-EPC-00000-PI-MRQ-0003 | Valves - Material Requisition | manual and check | EPC | piping | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0006 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2026-12-24 |  | 2026-12-24 | 2026-12-29 | ALP-EPC-00000-PI-SPC-0006 | G-PRC-ENQ MR-PI-003 | 2027-04-12 | G-PRC-ENQ MR-PI-003 IFR G-PRC-PO MR-PI-003 IFC
5 | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | barge, SPMT, cranes | EPC | mechanical | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-07 |  | 2026-12-21 | 2027-01-04
5 | ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | main steam, reheat | EPC | piping | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-HMB-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBD-PR-SDS-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04 |  | G-PRC-ENQ MR-PI-002 | 2026-12-21 | G-PRC-ENQ MR-PI-002 IFR G-PRC-PO MR-PI-002 IFC
5 | ALP-EPC-00000-PI-SPC-0007 | GRP CW Pipes and Fittings - Technical Specification |  | EPC | piping | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-PR-SDS-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-30 | 2026-12-28 | 2026-12-28 | 2027-01-04 |  | G-PRC-ENQ MR-PI-004 | 2026-12-21 | G-PRC-ENQ MR-PI-004 IFR G-PRC-PO MR-PI-004 IFC
5 | ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-01 | 2026-12-29 | 2026-12-29 | 2027-01-05 |  | G-CON-CWP CWP-04-CV-01 | 2027-04-05 | G-CON-CWP CWP-04-CV-01 IFC G-CON-CWP CWP-04-CV-01 IFC G-CON-IWP CWP-04-CV-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-01 | 2026-12-29 | 2026-12-29 | 2027-01-05 |  | G-CON-CWP CWP-12-CV-01 | 2027-01-18 | G-CON-CWP CWP-12-CV-01 IFC G-CON-CWP CWP-12-CV-01 IFC G-CON-IWP CWP-12-CV-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report |  | EPC | piping | M3D | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-25 | 2026-12-16 |  | 2026-12-30 | 2027-01-06 | capacity piping | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-03 | 2026-12-31 | 2026-12-31 | 2027-01-07 | capacity piping | G-CON-CWP CWP-05-ME-01 | 2027-12-20 | G-CON-CWP CWP-05-ME-01 IFC G-CON-CWP CWP-05-ME-01 IFC G-CON-IWP CWP-05-ME-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-00UZB-CV-CVL-0001 | Fencing and Gates - Civil Drawings |  | EPC | civil | CVL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-SDS-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-28 |  | 2026-12-28 | 2027-01-11 | ALP-EPC-00000-CV-RPT-0001 | G-CON-CWP CWP-12-CV-01 | 2027-01-18 | G-CON-CWP CWP-12-CV-01 IFC G-CON-IWP CWP-12-CV-01 IFC
5 | ALP-EPC-00000-EL-MRQ-0001 | Power and Control Cables - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SPC-0004 is NONE, IFR needs it at IFR |  | 2027-01-01 | 2027-01-08 |  | 2027-01-08 | 2027-01-13 | ALP-EPC-00000-EL-SPC-0004 | G-PRC-ENQ MR-EL-008 | 2027-05-03 | G-PRC-ENQ MR-EL-008 IFR G-PRC-PO MR-EL-008 IFC
5 | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-09 | 2027-01-06 | 2027-01-06 | 2027-01-13 |  | G-CON-CWP CWP-03-CV-01 | 2027-03-29 | G-CON-CWP CWP-03-CV-01 IFC G-CON-CWP CWP-03-CV-01 IFC G-CON-IWP CWP-03-CV-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-15 | 2027-01-12 | 2027-01-12 | 2027-01-19 |  | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-10 | 2026-12-15 | 2027-01-12 | 2027-01-12 | 2027-01-19 | capacity piping | G-CON-CWP CWP-07-ME-01 | 2027-12-27 | G-CON-CWP CWP-07-ME-01 IFC G-CON-CWP CWP-07-ME-01 IFC G-CON-IWP CWP-07-ME-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-04 | 2026-12-11 | 2027-01-15 | 2027-01-15 | 2027-01-22 | capacity piping | G-OWN-BDP 00000 | 2027-04-02 | G-CON-CWP CWP-02-ME-01 IFC G-CON-CWP CWP-02-ME-01 IFC G-CON-IWP CWP-02-ME-01 IFC G-OPS-AB 00000 AB G-OWN-BDP 00000 ACCEPTED
5 | ALP-EPC-00000-EL-STU-0003 | Earthing Study | IEEE 80 | EPC | electrical | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-28 |  | 2027-01-11 | 2027-01-25 | ALP-EPC-00000-CV-RPT-0001
5 | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | IEC 62305 | EPC | electrical | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-29 |  | 2027-01-12 | 2027-01-26 | capacity electrical
5 | ALP-EPC-00PAB-ME-CAL-0001 | CW Piping - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-05 |  | 2027-01-19 | 2027-01-26 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00PAC-ME-CAL-0001 | CW Pumps - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-05 |  | 2027-01-19 | 2027-01-26 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-13 | 2026-12-22 | 2027-01-19 | 2027-01-19 | 2027-01-26 | capacity piping | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-08-ME-01 IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-24 | 2026-12-23 | 2027-01-20 | 2027-01-20 | 2027-01-27 | capacity piping | G-CON-CWP CWP-10-ME-01 | 2027-10-04 | G-CON-CWP CWP-10-ME-01 IFC G-CON-CWP CWP-10-ME-01 IFC G-CON-IWP CWP-10-ME-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-06 |  | 2027-01-20 | 2027-01-27 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-07 |  | 2027-01-21 | 2027-01-28 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00GCA-ME-CAL-0001 | Demineralisation - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-07 |  | 2027-01-21 | 2027-01-28 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00LDA-ME-CAL-0001 | Condensate Polishing - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-07 |  | 2027-01-21 | 2027-01-28 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-08 |  | 2027-01-22 | 2027-01-29 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00ACA-CM-CMP-0001 | 380 kV GIS Switchyard - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-28 | 2027-01-25 | 2027-01-25 | 2027-02-01 | ALP-EPC-00000-CM-PLN-0001 | G-COM-SC-EL 00ACA | 2028-05-09 | G-COM-SC-EL 00ACA ACCEPTED
5 | ALP-EPC-00BBA-CM-CMP-0001 | MV Switchgear 10.5 kV - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-28 | 2027-01-25 | 2027-01-25 | 2027-02-01 | ALP-EPC-00000-CM-PLN-0001 | G-COM-SC-EL 00BBA | 2028-05-09 | G-COM-SC-EL 00BBA ACCEPTED
5 | ALP-EPC-00BFA-CM-CMP-0001 | LV Switchgear 0.4 kV - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-28 | 2027-01-25 | 2027-01-25 | 2027-02-01 | ALP-EPC-00000-CM-PLN-0001 | G-COM-SC-EL 00BFA | 2028-05-09 | G-COM-SC-EL 00BFA ACCEPTED
5 | ALP-EPC-00BFT-CM-CMP-0001 | LV Transformers - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-28 | 2027-01-25 | 2027-01-25 | 2027-02-01 | ALP-EPC-00000-CM-PLN-0001 | G-COM-SC-EL 00BFT | 2028-05-09 | G-COM-SC-EL 00BFT ACCEPTED
5 | ALP-EPC-00BLA-CM-CMP-0001 | Lighting and Small Power - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-28 | 2027-01-25 | 2027-01-25 | 2027-02-01 | ALP-EPC-00000-CM-PLN-0001 | G-COM-SC-EL 00BLA | 2028-05-09 | G-COM-SC-EL 00BLA ACCEPTED
5 | ALP-EPC-00BMA-CM-CMP-0001 | Emergency LV Switchgear - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-28 | 2027-01-25 | 2027-01-25 | 2027-02-01 | ALP-EPC-00000-CM-PLN-0001 | G-COM-SC-EL 00BMA | 2028-05-09 | G-COM-SC-EL 00BMA ACCEPTED
5 | ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-11 |  | 2027-01-25 | 2027-02-01 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation |  | EPC | hvac | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-11 |  | 2027-01-25 | 2027-02-01 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-27 | 2026-12-28 | 2027-01-25 | 2027-01-25 | 2027-02-01 | capacity piping | G-CON-CWP CWP-09-ME-01 | 2027-11-01 | G-CON-CWP CWP-09-ME-01 IFC G-CON-CWP CWP-09-ME-01 IFC G-CON-IWP CWP-09-ME-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-00EGC-ME-CAL-0001 | LDO Forwarding and Treatment - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-12 |  | 2027-01-26 | 2027-02-02 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00UPA-PI-LAY-0001 | Marine Works - Equipment Layout | offshore | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-29 | 2027-01-26 | 2027-01-26 | 2027-02-02 | capacity piping | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC G-OPS-AB 00000 AB
5 | ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-13 |  | 2027-01-27 | 2027-02-03 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00SGC-ME-CAL-0001 | Deluge, Spray and Foam Systems - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-13 |  | 2027-01-27 | 2027-02-03 | ALP-EPC-00000-PR-DBR-0001
5 | ALP-EPC-00BLA-GE-RPT-0001 | Cable Trays, Earthing and Lighting Materials - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-01-28 |  | 2027-01-28 | 2027-02-04 | bids MR-EL-009 | G-PRC-PO MR-EL-009 | 2027-02-08 | G-PRC-PO MR-EL-009 IFR
5 | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout |  | EPC | piping | LAY | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-24 | 2027-01-28 | 2027-01-28 | 2027-02-04 |  | G-OWN-BDP 00000 | 2027-04-02 | G-CON-CWP CWP-01-ME-01 IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC G-OPS-AB 00000 AB G-OWN-BDP 00000 ACCEPTED
5 | ALP-EPC-00SGA-ME-CAL-0001 | Fire Water System - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-15 |  | 2027-01-29 | 2027-02-05 | capacity mechanical
5 | ALP-EPC-00GMA-ME-CAL-0001 | Process Drains and Waste Water Collection - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-21 | 2027-01-18 |  | 2027-02-01 | 2027-02-08 | capacity mechanical
5 | ALP-EPC-00GUA-ME-CAL-0001 | Sanitary Waste Water Treatment - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GUA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-18 | 2027-01-19 |  | 2027-02-02 | 2027-02-09 | capacity mechanical
5 | ALP-EPC-00BRA-CM-CMP-0001 | UPS - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-12-10 | 2027-01-07 | 2027-02-04 | 2027-02-04 | 2027-02-11 | capacity commissioning | G-COM-SC-EL 00BRA | 2028-05-09 | G-COM-SC-EL 00BRA ACCEPTED
5 | ALP-EPC-00GNA-ME-CAL-0001 | Waste Water Treatment - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-25 | 2027-01-22 |  | 2027-02-05 | 2027-02-12 | capacity mechanical
5 | ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-05 | 2027-01-29 |  | 2027-02-12 | 2027-02-19 | capacity mechanical
5 | ALP-EPC-00PAA-ME-CAL-0001 | CW Intake, Screens and Outfall - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-04 | 2027-02-01 |  | 2027-02-15 | 2027-02-22 | capacity mechanical
5 | ALP-EPC-00BTA-CM-CMP-0001 | Batteries and DC 220 V - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-12-22 | 2027-01-19 | 2027-02-16 | 2027-02-16 | 2027-02-23 | capacity commissioning | G-COM-SC-EL 00BTA | 2028-05-09 | G-COM-SC-EL 00BTA ACCEPTED
5 | ALP-E09-00BLA-ME-DSH-0001 | Cable Trays, Earthing and Lighting Materials - Supplier Catalogues and Material Datasheets |  | E09 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-02-25 | 2027-02-25 | PO MR-EL-009
5 | ALP-E09-00BLA-ME-ITP-0001 | Cable Trays, Earthing and Lighting Materials - Supplier Inspection and Test Plan |  | E09 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-02-25 | 2027-02-25 | PO MR-EL-009
5 | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | NFPA 850 | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-25 | 2027-01-22 | 2027-02-19 | 2027-02-19 | 2027-02-26 | ALP-EPC-00000-HS-DBR-0001
5 | ALP-EPC-00BXA-CM-CMP-0001 | Earthing and Lightning Protection - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-01-25 | 2027-02-22 | 2027-02-22 | 2027-03-01 | capacity commissioning | G-COM-SC-EL 00BXA | 2028-05-09 | G-COM-SC-EL 00BXA ACCEPTED
5 | ALP-EPC-00XJA-CM-CMP-0001 | Emergency Diesel Generator - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-01-25 | 2027-02-22 | 2027-02-22 | 2027-03-01 | capacity commissioning | G-COM-SC-EL 00XJA | 2028-05-09 | G-COM-SC-EL 00XJA ACCEPTED
5 | ALP-EPC-10BBT-CM-CMP-0001 | GT Unit Auxiliary Transformer - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-01-25 | 2027-02-22 | 2027-02-22 | 2027-03-01 | capacity commissioning | G-COM-SC-EL 10BBT | 2028-05-09 | G-COM-SC-EL 10BBT ACCEPTED
5 | ALP-EPC-20BBT-CM-CMP-0001 | ST Unit Auxiliary Transformer - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-01-25 | 2027-02-22 | 2027-02-22 | 2027-03-01 | capacity commissioning | G-COM-SC-EL 20BBT | 2028-05-09 | G-COM-SC-EL 20BBT ACCEPTED
5 | ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-05 | 2027-02-09 |  | 2027-02-23 | 2027-03-02 | capacity mechanical
5 | ALP-EPC-00000-HS-HAZ-0001 | HAZID Report |  | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-PFD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-25 | 2027-01-27 | 2027-02-24 | 2027-02-24 | 2027-03-03 | capacity hse
5 | ALP-EPC-00QEA-ME-CAL-0001 | Compressed Air - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-02-12 |  | 2027-02-26 | 2027-03-05 | capacity mechanical
5 | ALP-EPC-10HSB-ME-CAL-0001 | Ammonia Storage and Supply - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-02-12 |  | 2027-02-26 | 2027-03-05 | capacity mechanical
5 | ALP-EPC-00CJG-GE-SPC-0001 | BOP Safety Instrumented System - Technical Specification | IEC 61511 | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-IC-BLK-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-02-01 | 2027-03-01 | 2027-03-01 | 2027-03-08 | capacity general | G-PRC-ENQ MR-IC-008 | 2027-04-12 | G-PRC-ENQ MR-IC-008 IFR G-PRC-PO MR-IC-008 IFC
5 | ALP-EPC-00CKA-GE-SPC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Specification |  | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-IC-BLK-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-02-01 | 2027-03-01 | 2027-03-01 | 2027-03-08 | capacity general | G-PRC-ENQ MR-IC-009 | 2027-04-12 | G-PRC-ENQ MR-IC-009 IFR G-PRC-PO MR-IC-009 IFC
5 | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | marine structures, buried piping and tanks | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-04 |  | 2027-03-04 | 2027-03-09 | ALP-EPC-00BXA-GE-SPC-0001 | G-PRC-ENQ MR-EL-010 | 2027-04-26 | G-PRC-ENQ MR-EL-010 IFR G-PRC-PO MR-EL-010 IFC
5 | ALP-EPC-00GKA-ME-CAL-0001 | Potable Water - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-02-16 |  | 2027-03-02 | 2027-03-09 | capacity mechanical
5 | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-26 | 2027-03-02 | 2027-03-02 | 2027-03-09 | ALP-EPC-00000-PR-DBR-0001 | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-26 | 2027-03-02 | 2027-03-02 | 2027-03-09 | ALP-EPC-00000-PR-DBR-0001 | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-02-16 |  | 2027-03-02 | 2027-03-09 | capacity mechanical
5 | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-27 | 2027-03-03 | 2027-03-03 | 2027-03-10 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00GHA-ME-CAL-0001 | Demineralised Water Storage and Distribution - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-08 | 2027-02-18 |  | 2027-03-04 | 2027-03-11 | capacity mechanical
5 | ALP-EPC-00CJA-CM-CMP-0001 | Plant DCS - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-01-08 | 2027-02-05 | 2027-03-05 | 2027-03-05 | 2027-03-12 | capacity commissioning | G-COM-SC-FF 00CJA | 2028-07-24 | G-COM-SC-FF 00CJA ACCEPTED
5 | ALP-EPC-00000-HS-STU-0001 | Noise Study | near field and environmental | EPC | hse | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-HS-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-02-15 |  | 2027-03-01 | 2027-03-15 | ALP-IEC-10MBA-HS-RPT-0001
5 | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-01-25 | 2027-03-08 | 2027-03-08 | 2027-03-15 | ALP-EPC-00000-PR-DBR-0001 | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID |  | EPC | hvac | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-02-02 | 2027-03-09 | 2027-03-09 | 2027-03-16 | ALP-EPC-00000-PR-DBR-0001 | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00PAH-ME-CAL-0001 | Condenser Tube Cleaning - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-26 |  | 2027-03-12 | 2027-03-19 | capacity mechanical
5 | ALP-EPC-10HAN-ME-CAL-0001 | HRSG Blowdown and Drains - Sizing and Hydraulic Calculation | EPC tanks and headers | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-26 |  | 2027-03-12 | 2027-03-19 | capacity mechanical
5 | ALP-EPC-00000-GE-RPT-0007 | Control Valves - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-15 |  | 2027-03-15 | 2027-03-22 | capacity general | G-PRC-PO MR-IC-005 | 2027-05-17 | G-PRC-PO MR-IC-005 IFR
5 | ALP-EPC-00000-ME-STU-0002 | Mechanical Handling and Maintenance Access Study |  | EPC | mechanical | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2026-11-19 | 2027-02-23 |  | 2027-03-09 | 2027-03-23 | capacity mechanical
5 | ALP-EPC-00CJG-CM-CMP-0001 | Safety Instrumented Systems - System Commissioning Procedure | BOP | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-01-19 | 2027-02-16 | 2027-03-16 | 2027-03-16 | 2027-03-23 | capacity commissioning | G-COM-SC-FF 00CJG | 2028-07-24 | G-COM-SC-FF 00CJG ACCEPTED
5 | ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings |  | EPC | civil | CVL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-SDS-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2027-02-16 | 2027-03-16 | 2027-03-16 | 2027-03-23 | capacity civil | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
5 | ALP-EPC-00QCA-ME-CAL-0001 | Chemical Dosing - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-03-03 |  | 2027-03-17 | 2027-03-24 | capacity mechanical
5 | ALP-EPC-00QJB-ME-CAL-0001 | Hydrogen and CO2 Supply - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-03 |  | 2027-03-17 | 2027-03-24 | capacity mechanical
5 | ALP-EPC-00QJA-ME-CAL-0001 | Nitrogen Supply - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-04 |  | 2027-03-18 | 2027-03-25 | capacity mechanical
5 | ALP-EPC-00EGB-ME-CAL-0001 | LDO Storage - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-05 |  | 2027-03-19 | 2027-03-26 | capacity mechanical
5 | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-29 | 2027-02-12 | 2027-03-19 | 2027-03-19 | 2027-03-26 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-10LAE-ME-CAL-0001 | HP Attemperation Spray Water - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-03-05 |  | 2027-03-19 | 2027-03-26 | capacity mechanical
5 | ALP-EPC-00CKA-CM-CMP-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-22 | 2027-03-22 | 2027-03-22 | 2027-03-29 | capacity commissioning | G-COM-SC-FF 00CKA | 2028-07-24 | G-COM-SC-FF 00CKA ACCEPTED
5 | ALP-EPC-00CQA-CM-CMP-0001 | Continuous Emission Monitoring - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-22 | 2027-03-22 | 2027-03-22 | 2027-03-29 | capacity commissioning | G-COM-SC-FF 00CQA | 2028-07-24 | G-COM-SC-FF 00CQA ACCEPTED
5 | ALP-EPC-00CYA-CM-CMP-0001 | Telecom, CCTV, Access Control, Security - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-22 | 2027-03-22 | 2027-03-22 | 2027-03-29 | capacity commissioning | G-COM-SC-FF 00CYA | 2028-07-24 | G-COM-SC-FF 00CYA ACCEPTED
5 | ALP-EPC-00EKC-ME-CAL-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-08 |  | 2027-03-22 | 2027-03-29 | capacity mechanical
5 | ALP-EPC-00QUA-ME-CAL-0001 | Sampling and SWAS - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-08 |  | 2027-03-22 | 2027-03-29 | capacity mechanical
5 | ALP-EPC-10LAB-ME-CAL-0001 | Feedwater Piping - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-08 |  | 2027-03-22 | 2027-03-29 | capacity mechanical
5 | ALP-EPC-10LAF-ME-CAL-0001 | Reheat Attemperation Spray Water - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-08 |  | 2027-03-22 | 2027-03-29 | capacity mechanical
5 | ALP-EPC-10LBA-ME-CAL-0001 | Main Steam Piping - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-08 |  | 2027-03-22 | 2027-03-29 | capacity mechanical
5 | ALP-EPC-10LBB-ME-CAL-0001 | Hot Reheat Piping - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-08 |  | 2027-03-22 | 2027-03-29 | capacity mechanical
5 | ALP-EPC-10LBC-ME-CAL-0001 | Cold Reheat Piping - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-08 |  | 2027-03-22 | 2027-03-29 | capacity mechanical
5 | ALP-EPC-10LBD-ME-CAL-0001 | LP Steam Piping - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-08 |  | 2027-03-22 | 2027-03-29 | capacity mechanical
5 | ALP-EPC-00LBG-ME-CAL-0001 | Auxiliary Steam - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-09 |  | 2027-03-23 | 2027-03-30 | capacity mechanical
5 | ALP-EPC-20MAN-ME-CAL-0001 | Turbine Bypass Stations and Piping - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-03-09 |  | 2027-03-23 | 2027-03-30 | capacity mechanical
5 | ALP-EPC-00000-GE-RPT-0006 | Field Instruments - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-03-24 |  | 2027-03-24 | 2027-03-31 | capacity general | G-PRC-PO MR-IC-004 | 2027-07-26 | G-PRC-PO MR-IC-004 IFR
5 | ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification |  | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-IC-BLK-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2027-02-24 | 2027-03-24 | 2027-03-24 | 2027-03-31 | capacity general | G-PRC-ENQ MR-IC-007 | 2027-05-24 | G-PRC-ENQ MR-IC-007 IFR G-PRC-PO MR-IC-007 IFC
5 | ALP-EPC-20LCA-ME-CAL-0001 | Main Condensate Piping - Sizing and Hydraulic Calculation |  | EPC | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-03-10 |  | 2027-03-24 | 2027-03-31 | capacity mechanical
5 | ALP-EPC-00000-GE-MRQ-0006 | Pipe Supports, Spring Hangers and Snubbers - Material Requisition |  | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0006 is NONE, IFR needs it at IFR |  | 2027-03-22 | 2027-03-29 |  | 2027-03-29 | 2027-04-01 | ALP-EPC-00000-GE-SPC-0006 | G-PRC-ENQ MR-PI-005 | 2027-07-12 | G-PRC-ENQ MR-PI-005 IFR G-PRC-PO MR-PI-005 IFC
5 | ALP-EPC-00BXA-GE-ITP-0001 | Cathodic Protection - Inspection and Test Plan | marine structures, buried piping and tanks | EPC | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 | 2027-04-01 | 2027-04-01 | 2027-04-08 | ALP-EPC-00BXA-GE-SPC-0001 | G-PRC-PO MR-EL-010 | 2027-06-21 | G-PRC-PO MR-EL-010 IFR
5 | ALP-EPC-00SGY-CM-CMP-0001 | Fire Detection and Alarm - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-02-05 | 2027-03-05 | 2027-04-02 | 2027-04-02 | 2027-04-09 | capacity commissioning | G-COM-SC-FF 00SGY | 2028-07-24 | G-COM-SC-FF 00SGY ACCEPTED
5 | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-15 | 2027-03-01 | 2027-04-05 | 2027-04-05 | 2027-04-12 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00SMA-CM-CMP-0001 | Cranes and Hoists - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-08 | 2027-04-05 | 2027-04-05 | 2027-04-12 | capacity commissioning | G-COM-SC-FF 00SMA | 2028-07-24 | G-COM-SC-FF 00SMA ACCEPTED
5 | ALP-EPC-00000-GE-MRQ-0003 | Instrument Installation Materials - Material Requisition | tubing, fittings, junction boxes, supports | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0003 is NONE, IFR needs it at IFR |  | 2027-04-02 | 2027-04-09 |  | 2027-04-09 | 2027-04-14 | ALP-EPC-00000-GE-SPC-0003 | G-PRC-ENQ MR-IC-010 | 2027-10-25 | G-PRC-ENQ MR-IC-010 IFR G-PRC-PO MR-IC-010 IFC
5 | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-03-04 | 2027-04-08 | 2027-04-08 | 2027-04-15 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings |  | EPC | civil | CVL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-SDS-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2027-03-11 | 2027-04-08 | 2027-04-08 | 2027-04-15 | capacity civil | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
5 | ALP-EPC-10HNE-CM-CMP-0001 | Stack 65 m with CEMS Platform and Silencer - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-11 | 2027-04-08 | 2027-04-08 | 2027-04-15 | capacity commissioning | G-COM-SC-FF 10HNE | 2028-07-24 | G-COM-SC-FF 10HNE ACCEPTED
5 | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-03-05 | 2027-04-09 | 2027-04-09 | 2027-04-16 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-03-05 | 2027-04-09 | 2027-04-09 | 2027-04-16 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-03-05 | 2027-04-09 | 2027-04-09 | 2027-04-16 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-03-05 | 2027-04-09 | 2027-04-09 | 2027-04-16 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-03-08 | 2027-04-12 | 2027-04-12 | 2027-04-19 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-I05-00000-ME-DSH-0001 | Control Valves - Supplier Catalogues and Material Datasheets |  | I05 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-03-22 | 2027-04-05 |  | 2027-04-19 | 2027-04-26 | PO MR-IC-005
5 | ALP-I05-00000-ME-ITP-0001 | Control Valves - Supplier Inspection and Test Plan |  | I05 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-03-22 | 2027-04-05 |  | 2027-04-26 | 2027-04-26 | PO MR-IC-005
5 | ALP-I04-00000-ME-DSH-0001 | Field Instruments - Supplier Catalogues and Material Datasheets |  | I04 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-29 | 2027-04-12 |  | 2027-04-26 | 2027-04-29 | PO MR-IC-004
5 | ALP-I04-00000-ME-ITP-0001 | Field Instruments - Supplier Inspection and Test Plan |  | I04 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-29 | 2027-04-12 |  | 2027-04-29 | 2027-04-29 | PO MR-IC-004
5 | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-11 | 2027-03-24 | 2027-04-28 | 2027-04-28 | 2027-05-05 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-25 | 2027-04-29 | 2027-04-29 | 2027-05-06 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-26 | 2027-04-06 | 2027-05-11 | 2027-05-11 | 2027-05-18 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00000-GE-SPC-0004 | Painting and Insulation - Technical Specification | subcontract | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-SPC-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-19 | 2027-04-16 | 2027-05-14 | 2027-05-14 | 2027-05-21 | capacity general | G-PRC-ENQ MR-ME-022 | 2027-11-15 | G-PRC-ENQ MR-ME-022 IFR G-PRC-PO MR-ME-022 IFC
5 | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-04-09 | 2027-05-14 | 2027-05-14 | 2027-05-21 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GCA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-04-09 | 2027-05-14 | 2027-05-14 | 2027-05-21 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-12 | 2027-05-17 | 2027-05-17 | 2027-05-24 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LBG-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-12 | 2027-05-17 | 2027-05-17 | 2027-05-24 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-12 | 2027-05-17 | 2027-05-17 | 2027-05-24 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-12 | 2027-05-17 | 2027-05-17 | 2027-05-24 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-13 | 2027-05-18 | 2027-05-18 | 2027-05-25 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-12 | 2027-05-24 | 2027-05-24 | 2027-05-31 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-00UPA-CV-CAL-0002 | Marine Structures Design: Hydrodynamics, Scour and Rock Protection |  | EPC | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-PR-SDS-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-05-10 |  | 2027-05-24 | 2027-05-31 | capacity civil
5 | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-23 | 2027-04-28 | 2027-06-02 | 2027-06-02 | 2027-06-09 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-24 | 2027-04-30 | 2027-06-04 | 2027-06-04 | 2027-06-11 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00000-CV-TST-0001 | Pile Load Test Procedure |  | EPC | civil | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR |  | 2027-01-20 | 2027-05-13 | 2027-06-10 | 2027-06-10 | 2027-06-17 | capacity civil
5 | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-05-06 | 2027-06-10 | 2027-06-10 | 2027-06-17 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC tanks and headers | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-06 | 2027-05-14 | 2027-06-18 | 2027-06-18 | 2027-06-25 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-17 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-17 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-17 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-17 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAF-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-18 | 2027-06-22 | 2027-06-22 | 2027-06-29 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-20MAN-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-18 | 2027-06-22 | 2027-06-22 | 2027-06-29 | capacity process | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
5 | ALP-E09-00BLA-ME-MDB-0001 | Cable Trays, Earthing and Lighting Materials - Manufacturing Record Book and Conformity Certificates |  | E09 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-04-22 | 2027-05-06 |  | 2027-05-06 | 2027-07-01 | PO MR-EL-009 | G-PRC-SHP MR-EL-009 | 2027-05-20 | G-PRC-SHP MR-EL-009 IFR
5 | ALP-EPC-00000-PR-RPT-0004 | Equipment Sparing and Redundancy Philosophy |  | EPC | process | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-STU-0002 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-14 |  | 2027-06-28 | 2027-07-05 | ALP-EPC-00000-PR-STU-0002
5 | ALP-EPC-00PAA-PR-STU-0001 | CW Intake Hydraulic Model Study and Pump Sump Model Test | ANSI/HI 9.8 | EPC | process | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-PR-SDS-0001 is NONE, IFR needs it at IFR |  | 2026-11-27 | 2027-06-07 |  | 2027-06-21 | 2027-07-05 | capacity process
5 | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-18 | 2027-06-29 | 2027-06-29 | 2027-07-06 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-18 | 2027-06-29 | 2027-06-29 | 2027-07-06 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-18 | 2027-06-29 | 2027-06-29 | 2027-07-06 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-28 | 2027-06-02 | 2027-07-14 | 2027-07-14 | 2027-07-21 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-28 | 2027-06-02 | 2027-07-14 | 2027-07-14 | 2027-07-21 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBC-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-29 | 2027-06-03 | 2027-07-15 | 2027-07-15 | 2027-07-22 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-00000-GE-SPC-0005 | Mechanical and Piping Erection - Technical Specification | subcontract | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-21 | 2027-06-18 | 2027-07-16 | 2027-07-16 | 2027-07-23 | ALP-EPC-00000-PI-SPC-0003 | G-PRC-ENQ MR-ME-023 | 2027-08-30 | G-PRC-ENQ MR-ME-023 IFR G-PRC-PO MR-ME-023 IFC
5 | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBD-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-06-07 | 2027-07-19 | 2027-07-19 | 2027-07-26 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID |  | EPC | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-05 | 2027-06-09 | 2027-07-21 | 2027-07-21 | 2027-07-28 | capacity process | G-OWN-BDP2 00000 | 2027-08-02 | G-OPS-AB 00000 AB G-OWN-BDP2 00000 ACCEPTED
5 | ALP-EPC-00000-CM-CMP-0004 | Operational Demonstration and Reliability Run Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-03-17 | 2027-08-04 | 2027-09-01 | 2027-09-01 | 2027-09-08 | capacity commissioning | G-OWN-TOC 00000 | 2028-08-21 | G-OWN-TOC 00000 ACCEPTED
5 | ALP-EPC-00000-HS-PLN-0006 | Radiation Protection Plan | industrial radiography | EPC | hse | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0003 is NONE, IFR needs it at IFR |  | 2027-06-02 | 2027-08-10 | 2027-09-07 | 2027-09-07 | 2027-09-14 | capacity hse
5 | ALP-I04-00000-ME-MDB-0001 | Field Instruments - Manufacturing Record Book and Conformity Certificates |  | I04 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-25 | 2027-09-08 |  | 2027-09-08 | 2027-11-03 | PO MR-IC-004 | G-PRC-SHP MR-IC-004 | 2027-09-22 | G-PRC-SHP MR-IC-004 IFR
5 | ALP-I05-00000-ME-MDB-0001 | Control Valves - Manufacturing Record Book and Conformity Certificates |  | I05 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-09-13 | 2027-09-27 |  | 2027-09-27 | 2027-11-22 | PO MR-IC-005 | G-PRC-SHP MR-IC-005 | 2027-10-11 | G-PRC-SHP MR-IC-005 IFR
5 | ALP-EPC-00000-CM-PRC-0001 | Punch List and Completion Procedure |  | EPC | commissioning | PRC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-23 | 2027-11-11 | 2027-12-09 | 2027-12-09 | 2027-12-16 | capacity commissioning
5 | ALP-EPC-00000-CM-PRC-0002 | System Completion, Mechanical Completion and Turnover Procedure |  | EPC | commissioning | PRC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-11-02 | 2027-11-24 | 2027-12-22 | 2027-12-22 | 2027-12-29 | capacity commissioning
5 | ALP-EPC-00000-CM-PLN-0002 | Training Plan | 60 Owner staff | EPC | commissioning | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-10-28 | 2027-11-25 | 2027-12-23 | 2027-12-23 | 2027-12-30 | capacity commissioning
5 | ALP-EPC-00000-IC-TRP-0001 | OT Cybersecurity Acceptance Test Report |  | EPC | i_and_c | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-TST-0002 is NONE, IFR needs it at IFR |  | 2028-09-18 | 2028-09-25 |  | 2028-10-09 | 2028-10-16 | after KD-020 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
5 | ALP-EPC-00000-CM-TRP-0002 | Performance Test Report incl. Uncertainty Analysis | ASME PTC 46 | EPC | commissioning | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-CMP-0002 is NONE, IFR needs it at IFR |  | 2029-03-19 | 2029-03-27 |  | 2029-04-10 | 2029-04-17 | capacity commissioning | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
6 | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition |  | EPC | civil | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-SPC-0003 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-CV-001 | 2027-02-01 | G-PRC-ENQ MR-CV-001 IFR G-PRC-PO MR-CV-001 IFC
6 | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition |  | EPC | structural | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HNE-SS-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-09 |  | 2026-11-09 | 2026-11-12 |  | G-PRC-ENQ MR-SS-002 | 2027-01-11 | G-PRC-ENQ MR-SS-002 IFR G-PRC-PO MR-SS-002 IFC
6 | ALP-EPC-00000-EL-LST-0002 | Construction Power Load List |  | EPC | electrical | LST | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZA-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-16 |  | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
6 | ALP-EPC-00CQA-IC-DSH-0001 | Continuous Emission Monitoring: Analyser - Datasheet |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00EGA-ME-DSH-0001 | LDO Unloading: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00EGB-ME-DSH-0001 | LDO Storage: Tanks - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00EGC-ME-DSH-0001 | LDO Forwarding and Treatment: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00EKA-ME-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00GBA-ME-DSH-0001 | Seawater Reverse Osmosis: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00GCA-ME-DSH-0001 | Demineralisation: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00GHA-ME-DSH-0001 | Demineralised Water Storage and Distribution: Tanks - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00GHA-ME-DSH-0002 | Demineralised Water Storage and Distribution: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00GKA-ME-DSH-0001 | Potable Water: Tank - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00GNA-ME-DSH-0001 | Waste Water Treatment: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00GUA-ME-DSH-0001 | Sanitary Waste Water Treatment: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00LDA-ME-DSH-0001 | Condensate Polishing: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00PAA-ME-DSH-0001 | CW Intake, Screens and Outfall: Filters - Datasheet | 4 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00PAC-ME-DSH-0001 | CW Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00PAH-ME-DSH-0001 | Condenser Tube Cleaning: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00PBA-ME-DSH-0001 | Electro-Chlorination: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00PGA-ME-DSH-0001 | Closed Cooling Water: Heat Exchangers - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00PGA-ME-DSH-0002 | Closed Cooling Water: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00PGA-ME-DSH-0003 | Closed Cooling Water: Tanks - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00QCA-ME-DSH-0001 | Chemical Dosing: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00QEA-ME-DSH-0001 | Compressed Air: Compressors - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00QEA-ME-DSH-0002 | Compressed Air: Filters - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00QEA-ME-DSH-0003 | Compressed Air: Tanks - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00QHA-ME-DSH-0001 | Auxiliary Boiler - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00QJA-ME-DSH-0001 | Nitrogen Supply: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00QJB-ME-DSH-0001 | Hydrogen and CO2 Supply: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00QUA-ME-DSH-0001 | Sampling and SWAS: Package - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00SAA-HV-DSH-0001 | HVAC: Package - Datasheet |  | EPC | hvac | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00SMA-ME-DSH-0001 | Cranes and Hoists - Datasheet | 6 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-10HAN-ME-DSH-0001 | HRSG Blowdown and Drains - Datasheet | EPC tanks and headers; 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-10HSB-ME-DSH-0001 | Ammonia Storage and Supply: Tanks - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-10HSB-ME-DSH-0002 | Ammonia Storage and Supply: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
6 | ALP-EPC-00000-PI-MRQ-0002 | Alloy Piping P91 / P22 - Material Requisition | main steam, reheat | EPC | piping | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0005 is NONE, IFR needs it at IFR |  | 2026-11-30 | 2026-12-07 |  | 2026-12-07 | 2026-12-10 | ALP-EPC-00000-PI-SPC-0005 | G-PRC-ENQ MR-PI-002 | 2026-12-21 | G-PRC-ENQ MR-PI-002 IFR G-PRC-PO MR-PI-002 IFC
6 | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram |  | EPC | electrical | SLD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-IEC-10BAA-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-OWN-BDP 00000 | 2027-04-02 | G-OPS-AB 00000 AB G-OWN-BDP 00000 ACCEPTED
6 | ALP-EPC-00CQA-IC-ITP-0001 | Continuous Emission Monitoring System - Inspection and Test Plan |  | EPC | i_and_c | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-IC-002 | 2027-07-12 | G-PRC-PO MR-IC-002 IFR
6 | ALP-EPC-00EGA-ME-ITP-0001 | LDO Unloading and Forwarding / Treatment Skids - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-016 | 2027-01-25 | G-PRC-PO MR-ME-016 IFR
6 | ALP-EPC-00EKA-ME-ITP-0001 | Gas Receiving and Metering Station - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-015 | 2027-01-25 | G-PRC-PO MR-ME-015 IFR
6 | ALP-EPC-00GHA-ME-ITP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-013 | 2027-05-17 | G-PRC-PO MR-ME-013 IFR
6 | ALP-EPC-00GNA-ME-ITP-0001 | Waste Water and Sanitary Treatment Packages - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-014 | 2027-05-31 | G-PRC-PO MR-ME-014 IFR
6 | ALP-EPC-00LDA-ME-ITP-0001 | Water Treatment Package - Inspection and Test Plan | SWRO, demin, condensate polishing | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-012 | 2027-02-08 | G-PRC-PO MR-ME-012 IFR
6 | ALP-EPC-00PAA-ME-ITP-0001 | Travelling Band Screens and Trash Rakes - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-004 | 2027-04-12 | G-PRC-PO MR-ME-004 IFR
6 | ALP-EPC-00PAC-ME-ITP-0001 | CW Pumps - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-003 | 2027-02-01 | G-PRC-PO MR-ME-003 IFR
6 | ALP-EPC-00PBA-ME-ITP-0001 | Electro-Chlorination Package - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-005 | 2027-04-12 | G-PRC-PO MR-ME-005 IFR
6 | ALP-EPC-00QHA-ME-ITP-0001 | Auxiliary Boiler - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-009 | 2027-01-25 | G-PRC-PO MR-ME-009 IFR
6 | ALP-EPC-00QUA-IC-ITP-0001 | Steam/Water Analysis System - Inspection and Test Plan |  | EPC | i_and_c | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-IC-003 | 2027-07-12 | G-PRC-PO MR-IC-003 IFR
6 | ALP-EPC-00SAA-HV-ITP-0001 | HVAC Plant and Equipment - Inspection and Test Plan |  | EPC | hvac | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-HV-001 | 2027-03-15 | G-PRC-PO MR-HV-001 IFR
6 | ALP-EPC-00SGA-ME-ITP-0001 | Fire Pumps and Fire Protection Systems - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-020 | 2027-03-22 | G-PRC-PO MR-ME-020 IFR
6 | ALP-EPC-00SMA-ME-ITP-0001 | EOT Cranes - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-021 | 2027-02-08 | G-PRC-PO MR-ME-021 IFR
6 | ALP-EPC-10LAC-ME-ITP-0001 | Boiler Feed Pumps - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-ME-001 | 2027-01-25 | G-PRC-PO MR-ME-001 IFR
6 | ALP-EPC-00PGA-ME-ITP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-03 | 2026-11-17 | 2026-12-08 | 2026-12-08 | 2026-12-15 | capacity mechanical | G-PRC-PO MR-ME-007 | 2027-04-05 | G-PRC-PO MR-ME-007 IFR
6 | ALP-EPC-00QEA-ME-ITP-0001 | Air Compressors and Dryers - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-04 | 2026-11-18 | 2026-12-09 | 2026-12-09 | 2026-12-16 | capacity mechanical | G-PRC-PO MR-ME-008 | 2027-04-05 | G-PRC-PO MR-ME-008 IFR
6 | ALP-EPC-10HSB-ME-ITP-0001 | Aqueous Ammonia Storage and Forwarding - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-06 | 2026-11-20 | 2026-12-11 | 2026-12-11 | 2026-12-18 | capacity mechanical | G-PRC-PO MR-ME-018 | 2027-04-05 | G-PRC-PO MR-ME-018 IFR
6 | ALP-EPC-20LCB-ME-ITP-0001 | Condensate Extraction Pumps - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-09 | 2026-11-23 | 2026-12-14 | 2026-12-14 | 2026-12-21 | capacity mechanical | G-PRC-PO MR-ME-002 | 2027-04-12 | G-PRC-PO MR-ME-002 IFR
6 | ALP-EPC-10HAN-ME-ITP-0001 | HRSG Blowdown and Drain Tanks - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-11 | 2026-11-25 | 2026-12-16 | 2026-12-16 | 2026-12-23 | capacity mechanical | G-PRC-PO MR-ME-019 | 2027-05-03 | G-PRC-PO MR-ME-019 IFR
6 | ALP-EPC-00QCA-ME-ITP-0001 | Chemical Dosing Skid - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-12 | 2026-11-26 | 2026-12-17 | 2026-12-17 | 2026-12-24 | capacity mechanical | G-PRC-PO MR-ME-011 | 2027-05-17 | G-PRC-PO MR-ME-011 IFR
6 | ALP-EPC-00PAH-ME-ITP-0001 | Condenser Tube Cleaning System - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-16 | 2026-11-30 | 2026-12-21 | 2026-12-21 | 2026-12-28 | capacity mechanical | G-PRC-PO MR-ME-006 | 2027-07-05 | G-PRC-PO MR-ME-006 IFR
6 | ALP-EPC-00QJA-ME-ITP-0001 | Nitrogen, Hydrogen and CO2 Supply - Inspection and Test Plan |  | EPC | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-16 | 2026-11-30 | 2026-12-21 | 2026-12-21 | 2026-12-28 | capacity mechanical | G-PRC-PO MR-ME-010 | 2027-06-28 | G-PRC-PO MR-ME-010 IFR
6 | ALP-EPC-00000-GE-RPT-0002 | Civil and Building Works - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0002 is NONE, IFR needs it at IFR |  | 2026-12-03 | 2026-12-24 |  | 2026-12-24 | 2026-12-31 | bids MR-CV-002 | G-PRC-PO MR-CV-002 | 2027-01-11 | G-PRC-PO MR-CV-002 IFR
6 | ALP-C02-00000-GE-ITP-0001 | Civil and Building Works - Subcontractor Inspection and Test Plans |  | C02 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-07 |  | 2027-01-21 | 2027-01-21 | PO MR-CV-002
6 | ALP-C02-00000-GE-MOS-0001 | Civil and Building Works - Subcontractor Method Statements, Part 1 of 6 |  | C02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-07 |  | 2027-01-21 | 2027-01-21 | PO MR-CV-002
6 | ALP-C02-00000-GE-MOS-0002 | Civil and Building Works - Subcontractor Method Statements, Part 2 of 6 |  | C02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-07 |  | 2027-01-21 | 2027-01-21 | PO MR-CV-002
6 | ALP-C02-00000-GE-MOS-0003 | Civil and Building Works - Subcontractor Method Statements, Part 3 of 6 |  | C02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-07 |  | 2027-01-21 | 2027-01-21 | PO MR-CV-002
6 | ALP-C02-00000-GE-MOS-0004 | Civil and Building Works - Subcontractor Method Statements, Part 4 of 6 |  | C02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-07 |  | 2027-01-21 | 2027-01-21 | PO MR-CV-002
6 | ALP-C02-00000-GE-MOS-0005 | Civil and Building Works - Subcontractor Method Statements, Part 5 of 6 |  | C02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-07 |  | 2027-01-21 | 2027-01-21 | PO MR-CV-002
6 | ALP-C02-00000-GE-MOS-0006 | Civil and Building Works - Subcontractor Method Statements, Part 6 of 6 |  | C02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-07 |  | 2027-01-21 | 2027-01-21 | PO MR-CV-002
6 | ALP-EPC-00000-GE-RPT-0011 | Piping Bulk Materials - Technical Bid Evaluation | carbon steel, stainless | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-01-28 |  | 2027-01-28 | 2027-02-04 | bids MR-PI-001 | G-PRC-PO MR-PI-001 | 2027-02-22 | G-PRC-PO MR-PI-001 IFR
6 | ALP-EPC-00UPC-CV-ARC-0001 | CW Pump House - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-03 | 2027-01-05 | 2027-02-02 | 2027-02-02 | 2027-02-09 | ALP-EPC-00UPC-PI-LAY-0001 | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
6 | ALP-EPC-00000-GE-RPT-0016 | Structural Steel Supply and Fabrication - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-13 | 2027-02-03 |  | 2027-02-03 | 2027-02-10 | capacity general | G-PRC-PO MR-SS-001 | 2027-03-23 | G-PRC-PO MR-SS-001 IFR
6 | ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UAC-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-01 | 2027-01-07 | 2027-02-04 | 2027-02-04 | 2027-02-11 | ALP-EPC-00UAC-PI-LAY-0001 | G-CON-CWP CWP-04-SS-01 | 2027-05-31 | G-CON-CWP CWP-04-SS-01 IFC G-CON-IWP CWP-04-SS-01 IFC
6 | ALP-EPC-00EGA-ME-DSH-0002 | LDO Unloading: Filters - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00EGA-ME-DSH-0004 | LDO Unloading: Tank - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00GBA-ME-DSH-0004 | Seawater Reverse Osmosis: Tank - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00GBA-ME-CAL-0001
6 | ALP-EPC-00GCA-ME-DSH-0003 | Demineralisation: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00LDA-ME-DSH-0002 | Condensate Polishing: Filters - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00PAB-ME-DSH-0001 | CW Piping: Valves - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0007 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00QHA-ME-DSH-0002 | Auxiliary Boiler: Fan - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00QHA-ME-DSH-0003 | Auxiliary Boiler: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00QHA-ME-DSH-0004 | Auxiliary Boiler: Tanks - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00UPC-CV-FND-0002 | CW Pump House - Piling Layout and Pile Schedule |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR |  | 2026-12-21 | 2027-01-19 | 2027-02-16 | 2027-02-16 | 2027-02-23 | ALP-EPC-00000-CV-SPC-0002 | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
6 | ALP-EPC-20UMB-CV-ARC-0001 | Steam Turbine Hall - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-11 | 2027-01-19 | 2027-02-16 | 2027-02-16 | 2027-02-23 | ALP-EPC-20UMB-PI-LAY-0001 | G-CON-CWP CWP-02-SS-01 | 2027-07-12 | G-CON-CWP CWP-02-SS-01 IFC G-CON-IWP CWP-02-SS-01 IFC
6 | ALP-EPC-00EGA-ME-DSH-0003 | LDO Unloading: Pumps - Datasheet | 4 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00EGC-ME-DSH-0002 | LDO Forwarding and Treatment: Filters - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-12 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00EGC-ME-CAL-0001
6 | ALP-EPC-00EGC-ME-DSH-0003 | LDO Forwarding and Treatment: Pumps - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-12 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00EGC-ME-CAL-0001
6 | ALP-EPC-00EKA-ME-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station: Filters - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-13 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00EKA-ME-CAL-0001
6 | ALP-EPC-00EKA-ME-DSH-0003 | Gas Receiving, Filtration and Fiscal Metering Station: Heat Exchangers - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-13 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00EKA-ME-CAL-0001
6 | ALP-EPC-00EKA-ME-DSH-0004 | Gas Receiving, Filtration and Fiscal Metering Station: Tank - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-13 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00EKA-ME-CAL-0001
6 | ALP-EPC-00GBA-ME-DSH-0002 | Seawater Reverse Osmosis: Filters - Datasheet | 5 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00GBA-ME-CAL-0001
6 | ALP-EPC-00GBA-ME-DSH-0003 | Seawater Reverse Osmosis: Pumps - Datasheet | 6 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00GBA-ME-CAL-0001
6 | ALP-EPC-00GCA-ME-DSH-0002 | Demineralisation: Filters - Datasheet | 4 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-27 | 2027-02-17 | 2027-02-17 | 2027-02-24 | ALP-EPC-00000-ME-DBR-0001
6 | ALP-EPC-00UZB-EL-ELY-0001 | Fencing and Gates - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZB-CV-CVL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2026-12-29 | 2027-01-27 |  | 2027-02-10 | 2027-02-24 | ALP-EPC-00000-EL-STU-0004 | G-CON-CWP CWP-12-EL-01 | 2027-05-17 | G-CON-CWP CWP-12-EL-01 IFC G-CON-IWP CWP-12-EL-01 IFC
6 | ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-09 | 2027-01-21 | 2027-02-18 | 2027-02-18 | 2027-02-25 | ALP-EPC-00UBA-PI-LAY-0001 | G-CON-CWP CWP-03-SS-01 | 2027-05-24 | G-CON-CWP CWP-03-SS-01 IFC G-CON-IWP CWP-03-SS-01 IFC
6 | ALP-P01-00000-ME-DSH-0001 | Piping Bulk Materials - Supplier Catalogues and Material Datasheets | carbon steel, stainless | P01 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-02-25 | 2027-02-25 | PO MR-PI-001
6 | ALP-P01-00000-ME-ITP-0001 | Piping Bulk Materials - Supplier Inspection and Test Plan | carbon steel, stainless | P01 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-02-25 | 2027-02-25 | PO MR-PI-001
6 | ALP-EPC-00UBF-CV-FND-0002 | Transformer Bays - Piling Layout and Pile Schedule |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-22 | 2027-02-19 | 2027-02-19 | 2027-02-26 | ALP-EPC-10UMA-PI-LAY-0001 | G-CON-CWP CWP-01-CV-01 | 2027-03-22 | G-CON-CWP CWP-01-CV-01 IFC G-CON-IWP CWP-01-CV-01 IFC
6 | ALP-EPC-10UHN-CV-FND-0002 | Stack Foundation - Piling Layout and Pile Schedule |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-22 | 2027-02-19 | 2027-02-19 | 2027-02-26 | ALP-EPC-10UMA-PI-LAY-0001 | G-CON-CWP CWP-01-CV-01 | 2027-03-22 | G-CON-CWP CWP-01-CV-01 IFC G-CON-IWP CWP-01-CV-01 IFC
6 | ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-15 | 2027-01-25 | 2027-02-22 | 2027-02-22 | 2027-03-01 | ALP-EPC-00UGA-PI-LAY-0001 | G-CON-CWP CWP-07-SS-01 | 2027-06-14 | G-CON-CWP CWP-07-SS-01 IFC G-CON-IWP CWP-07-SS-01 IFC
6 | ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-15 | 2027-01-25 | 2027-02-22 | 2027-02-22 | 2027-03-01 | ALP-EPC-00UCA-PI-LAY-0001 | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
6 | ALP-EPC-10UHA-CV-FND-0002 | HRSG Foundations and Structures - Piling Layout and Pile Schedule |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-26 | 2027-02-23 | 2027-02-23 | 2027-03-02 | ALP-EPC-10UMA-PI-LAY-0001 | G-CON-CWP CWP-01-CV-01 | 2027-03-22 | G-CON-CWP CWP-01-CV-01 IFC G-CON-IWP CWP-01-CV-01 IFC
6 | ALP-EPC-00000-ME-LST-0001 | Heavy and Oversized Piece List | power island and BOP | EPC | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-STU-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-02-03 |  | 2027-02-17 | 2027-03-03 | capacity mechanical | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
6 | ALP-EPC-00UQA-CV-ARC-0001 | Utility Building - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-22 | 2027-01-27 | 2027-02-24 | 2027-02-24 | 2027-03-03 | capacity civil | G-CON-CWP CWP-08-SS-01 | 2027-06-29 | G-CON-CWP CWP-08-SS-01 IFC G-CON-IWP CWP-08-SS-01 IFC
6 | ALP-S01-00000-GE-ITP-0001 | Structural Steel Supply and Fabrication - Subcontractor Inspection and Test Plans |  | S01 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-02-17 |  | 2027-03-03 | 2027-03-03 | PO MR-SS-001
6 | ALP-S01-00000-GE-MOS-0001 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 1 of 6 |  | S01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-02-17 |  | 2027-03-03 | 2027-03-03 | PO MR-SS-001
6 | ALP-S01-00000-GE-MOS-0002 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 2 of 6 |  | S01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-02-17 |  | 2027-03-03 | 2027-03-03 | PO MR-SS-001
6 | ALP-S01-00000-GE-MOS-0003 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 3 of 6 |  | S01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-02-17 |  | 2027-03-03 | 2027-03-03 | PO MR-SS-001
6 | ALP-S01-00000-GE-MOS-0004 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 4 of 6 |  | S01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-02-17 |  | 2027-03-03 | 2027-03-03 | PO MR-SS-001
6 | ALP-S01-00000-GE-MOS-0005 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 5 of 6 |  | S01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-02-17 |  | 2027-03-03 | 2027-03-03 | PO MR-SS-001
6 | ALP-S01-00000-GE-MOS-0006 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 6 of 6 |  | S01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-02-17 |  | 2027-03-03 | 2027-03-03 | PO MR-SS-001
6 | ALP-EPC-00GMA-ME-DSH-0004 | Process Drains and Waste Water Collection: Filter - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-04 | 2027-02-25 | 2027-02-25 | 2027-03-04 | capacity mechanical
6 | ALP-EPC-10UMA-CV-FND-0001 | Gas Turbine Hall - Piling Layout and Pile Schedule |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-28 | 2027-02-25 | 2027-02-25 | 2027-03-04 | ALP-EPC-10UMA-PI-LAY-0001 | G-CON-CWP CWP-01-CV-01 | 2027-03-22 | G-CON-CWP CWP-01-CV-01 IFC G-CON-IWP CWP-01-CV-01 IFC
6 | ALP-EPC-00SAA-ME-DSH-0001 | HVAC: Compressors - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-21 | 2027-02-05 | 2027-02-26 | 2027-02-26 | 2027-03-05 | capacity mechanical
6 | ALP-EPC-00ACA-CM-OMM-0001 | 380 kV GIS Switchyard - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-02-08 |  | 2027-02-22 | 2027-03-08 | ALP-EPC-00ACA-CM-CMP-0001 | G-COM-SC-EL 00ACA | 2028-05-09 | G-COM-SC-EL 00ACA IFR G-OPS-HO-EL 00ACA IFC
6 | ALP-EPC-00BBA-CM-OMM-0001 | MV Switchgear 10.5 kV - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-02-08 |  | 2027-02-22 | 2027-03-08 | ALP-EPC-00BBA-CM-CMP-0001 | G-COM-SC-EL 00BBA | 2028-05-09 | G-COM-SC-EL 00BBA IFR G-OPS-HO-EL 00BBA IFC
6 | ALP-EPC-00BFA-CM-OMM-0001 | LV Switchgear 0.4 kV - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-02-08 |  | 2027-02-22 | 2027-03-08 | ALP-EPC-00BFA-CM-CMP-0001 | G-COM-SC-EL 00BFA | 2028-05-09 | G-COM-SC-EL 00BFA IFR G-OPS-HO-EL 00BFA IFC
6 | ALP-EPC-00BFT-CM-OMM-0001 | LV Transformers - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-02-08 |  | 2027-02-22 | 2027-03-08 | ALP-EPC-00BFT-CM-CMP-0001 | G-COM-SC-EL 00BFT | 2028-05-09 | G-COM-SC-EL 00BFT IFR G-OPS-HO-EL 00BFT IFC
6 | ALP-EPC-00GMA-ME-DSH-0006 | Process Drains and Waste Water Collection: Tank - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-08 | 2027-03-01 | 2027-03-01 | 2027-03-08 | capacity mechanical
6 | ALP-EPC-00SAA-ME-DSH-0003 | HVAC: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-08 | 2027-03-01 | 2027-03-01 | 2027-03-08 | capacity mechanical
6 | ALP-EPC-10UMA-CV-ARC-0001 | Gas Turbine Hall - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-02-01 | 2027-03-01 | 2027-03-01 | 2027-03-08 | ALP-EPC-10UMA-PI-LAY-0001 | G-CON-CWP CWP-01-SS-01 | 2027-07-12 | G-CON-CWP CWP-01-SS-01 IFC G-CON-IWP CWP-01-SS-01 IFC
6 | ALP-EPC-20UMB-CV-FND-0001 | Steam Turbine Hall - Piling Layout and Pile Schedule |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-IEC-20MAA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-02-01 | 2027-03-01 | 2027-03-01 | 2027-03-08 | ALP-IEC-20MAA-CV-CAL-0001 | G-CON-CWP CWP-02-CV-01 | 2027-03-22 | G-CON-CWP CWP-02-CV-01 IFC G-CON-IWP CWP-02-CV-01 IFC
6 | ALP-EPC-00BLA-CM-OMM-0001 | Lighting and Small Power - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BLA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2026-12-29 | 2027-02-09 |  | 2027-02-23 | 2027-03-09 | capacity commissioning | G-COM-SC-EL 00BLA | 2028-05-09 | G-COM-SC-EL 00BLA IFR G-OPS-HO-EL 00BLA IFC
6 | ALP-EPC-00SGC-ME-DSH-0001 | Deluge, Spray and Foam Systems: Tank - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-13 | 2027-02-09 | 2027-03-02 | 2027-03-02 | 2027-03-09 | capacity mechanical
6 | ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-15 | 2027-02-02 | 2027-03-02 | 2027-03-02 | 2027-03-09 | ALP-EPC-00UCA-PI-LAY-0001 | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
6 | ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-15 | 2027-02-02 | 2027-03-02 | 2027-03-02 | 2027-03-09 | ALP-EPC-00UCA-PI-LAY-0001 | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
6 | ALP-EPC-00GMA-ME-DSH-0005 | Process Drains and Waste Water Collection: Pumps - Datasheet | 6 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-10 | 2027-03-03 | 2027-03-03 | 2027-03-10 | capacity mechanical
6 | ALP-EPC-00GNA-ME-DSH-0002 | Waste Water Treatment: Pumps - Datasheet | 6 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-10 | 2027-03-03 | 2027-03-03 | 2027-03-10 | capacity mechanical
6 | ALP-EPC-00GUA-ME-DSH-0002 | Sanitary Waste Water Treatment: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GUA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-10 | 2027-03-03 | 2027-03-03 | 2027-03-10 | capacity mechanical
6 | ALP-EPC-00SAA-ME-DSH-0002 | HVAC: Fans - Datasheet | 18 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-02-10 | 2027-03-03 | 2027-03-03 | 2027-03-10 | capacity mechanical
6 | ALP-EPC-00EGC-IC-DSH-0002 | LDO Forwarding and Treatment - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-12 | 2027-03-05 | 2027-03-05 | 2027-03-12 | ALP-EPC-00EGC-PR-PID-0001
6 | ALP-EPC-00EKA-IC-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-12 | 2027-03-05 | 2027-03-05 | 2027-03-12 | ALP-EPC-00EKA-PR-PID-0001
6 | ALP-EPC-00GNA-ME-DSH-0003 | Waste Water Treatment: Tanks - Datasheet | 4 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-12 | 2027-03-05 | 2027-03-05 | 2027-03-12 | capacity mechanical
6 | ALP-EPC-00PBA-ME-DSH-0002 | Electro-Chlorination: Fans - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-29 | 2027-02-12 | 2027-03-05 | 2027-03-05 | 2027-03-12 | ALP-EPC-00PBA-ME-CAL-0001
6 | ALP-EPC-00PBA-ME-DSH-0003 | Electro-Chlorination: Filters - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-29 | 2027-02-12 | 2027-03-05 | 2027-03-05 | 2027-03-12 | ALP-EPC-00PBA-ME-CAL-0001
6 | ALP-EPC-00PBA-ME-DSH-0005 | Electro-Chlorination: Tanks - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-29 | 2027-02-12 | 2027-03-05 | 2027-03-05 | 2027-03-12 | ALP-EPC-00PBA-ME-CAL-0001
6 | ALP-EPC-00SGC-ME-DSH-0002 | Deluge, Spray and Foam Systems: Valves - Datasheet | 10 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-12 | 2027-03-05 | 2027-03-05 | 2027-03-12 | capacity mechanical
6 | ALP-EPC-00BMA-CM-OMM-0001 | Emergency LV Switchgear - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BMA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-01-04 | 2027-02-15 |  | 2027-03-01 | 2027-03-15 | capacity commissioning | G-COM-SC-EL 00BMA | 2028-05-09 | G-COM-SC-EL 00BMA IFR G-OPS-HO-EL 00BMA IFC
6 | ALP-EPC-00CJG-IC-DSH-0001 | Safety Instrumented Systems: Control System - Datasheet | BOP | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CJG-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-15 | 2027-03-08 | 2027-03-08 | 2027-03-15 | ALP-EPC-00CJG-GE-SPC-0001
6 | ALP-EPC-00CKA-IC-DSH-0001 | Historian, Performance Monitoring and Operator Training Simulator: Control System - Datasheet |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CKA-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-15 | 2027-03-08 | 2027-03-08 | 2027-03-15 | ALP-EPC-00CKA-GE-SPC-0001
6 | ALP-EPC-00PAA-ME-DSH-0002 | CW Intake, Screens and Outfall: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-15 | 2027-03-08 | 2027-03-08 | 2027-03-15 | ALP-EPC-00PAA-ME-CAL-0001
6 | ALP-EPC-00PAA-ME-DSH-0003 | CW Intake, Screens and Outfall: Valves - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-15 | 2027-03-08 | 2027-03-08 | 2027-03-15 | ALP-EPC-00PAA-ME-CAL-0001
6 | ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UZA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-18 | 2027-02-15 |  | 2027-03-01 | 2027-03-15 | ALP-EPC-00000-PI-SPC-0002 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
6 | ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-16 |  | 2027-03-02 | 2027-03-16 | ALP-EPC-00EKA-PR-PID-0001
6 | ALP-EPC-00PBA-ME-DSH-0004 | Electro-Chlorination: Pumps - Datasheet | 4 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-29 | 2027-02-16 | 2027-03-09 | 2027-03-09 | 2027-03-16 | ALP-EPC-00PBA-ME-CAL-0001
6 | ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings |  | EPC | civil | CVL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-STU-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-SDS-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-SDS-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-02-09 | 2027-03-09 | 2027-03-09 | 2027-03-16 | capacity civil | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
6 | ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-17 |  | 2027-03-03 | 2027-03-17 | ALP-EPC-00SGA-PR-PID-0001
6 | ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-17 |  | 2027-03-03 | 2027-03-17 | ALP-EPC-00SGC-PR-PID-0001
6 | ALP-EPC-00BRA-CM-OMM-0001 | UPS - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-02-18 |  | 2027-03-04 | 2027-03-18 | ALP-EPC-00BRA-CM-CMP-0001 | G-COM-SC-EL 00BRA | 2028-05-09 | G-COM-SC-EL 00BRA IFR G-OPS-HO-EL 00BRA IFC
6 | ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-18 |  | 2027-03-04 | 2027-03-18 | ALP-EPC-00EGC-PR-PID-0001
6 | ALP-EPC-00UPA-GE-RPT-0001 | Marine Works - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-11 | 2027-03-18 | capacity general | G-PRC-PO MR-CV-003 | 2027-05-14 | G-PRC-PO MR-CV-003 IFR
6 | ALP-EPC-00000-GE-RPT-0003 | Power and Control Cables - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-15 |  | 2027-03-15 | 2027-03-22 | capacity general | G-PRC-PO MR-EL-008 | 2027-06-21 | G-PRC-PO MR-EL-008 IFR
6 | ALP-EPC-00000-GE-RPT-0012 | Valves - Technical Bid Evaluation | manual and check | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-15 |  | 2027-03-15 | 2027-03-22 | capacity general | G-PRC-PO MR-PI-003 | 2027-06-14 | G-PRC-PO MR-PI-003 IFR
6 | ALP-EPC-00EKA-IC-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-22 | 2027-03-15 | 2027-03-15 | 2027-03-22 | ALP-EPC-00EKA-PR-PID-0001
6 | ALP-EPC-00PGA-ME-DSH-0004 | Closed Cooling Water: Filter - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 | 2027-03-16 | 2027-03-16 | 2027-03-23 | ALP-EPC-00PGA-ME-CAL-0001
6 | ALP-EPC-00EGC-IC-DSH-0001 | LDO Forwarding and Treatment - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-24 | 2027-03-17 | 2027-03-17 | 2027-03-24 | ALP-EPC-00EGC-PR-PID-0001
6 | ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-02-24 |  | 2027-03-10 | 2027-03-24 | ALP-EPC-00SAA-HV-PID-0001
6 | ALP-EPC-00UCA-CV-FND-0001 | Control Building - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-17 | 2027-03-17 | 2027-03-17 | 2027-03-24 | ALP-EPC-00000-CV-CAL-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
6 | ALP-EPC-00USA-CV-FND-0001 | Workshop and Warehouse - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-17 | 2027-03-17 | 2027-03-17 | 2027-03-24 | ALP-EPC-00000-CV-CAL-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
6 | ALP-EPC-00UYA-CV-FND-0001 | Administration Building - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-17 | 2027-03-17 | 2027-03-17 | 2027-03-24 | ALP-EPC-00000-CV-CAL-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
6 | ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UAC-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-18 | 2027-03-18 | 2027-03-18 | 2027-03-25 | ALP-EPC-00000-CV-CAL-0001 | G-CON-CWP CWP-04-CV-01 | 2027-04-05 | G-CON-CWP CWP-04-CV-01 IFC G-CON-IWP CWP-04-CV-01 IFC
6 | ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-18 | 2027-03-18 | 2027-03-18 | 2027-03-25 | ALP-EPC-00000-CV-CAL-0001 | G-CON-CWP CWP-03-CV-01 | 2027-03-29 | G-CON-CWP CWP-03-CV-01 IFC G-CON-IWP CWP-03-CV-01 IFC
6 | ALP-EPC-00000-ME-RPT-0001 | Abnormal Load Route Survey and Transport Drawings |  | EPC | mechanical | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-STU-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-03-05 |  | 2027-03-19 | 2027-03-26 | capacity mechanical
6 | ALP-EPC-00SAA-IC-DSH-0002 | HVAC - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-02-26 | 2027-03-19 | 2027-03-19 | 2027-03-26 | capacity i_and_c
6 | ALP-EPC-00CJG-GE-ITP-0001 | BOP Safety Instrumented System - Inspection and Test Plan | IEC 61511 | EPC | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-03-01 | 2027-03-22 | 2027-03-22 | 2027-03-29 | capacity general | G-PRC-PO MR-IC-008 | 2027-06-07 | G-PRC-PO MR-IC-008 IFR
6 | ALP-EPC-00BTA-CM-OMM-0001 | Batteries and DC 220 V - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BTA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-01-19 | 2027-03-02 |  | 2027-03-16 | 2027-03-30 | ALP-EPC-00BTA-CM-CMP-0001 | G-COM-SC-EL 00BTA | 2028-05-09 | G-COM-SC-EL 00BTA IFR G-OPS-HO-EL 00BTA IFC
6 | ALP-EPC-00GKA-ME-DSH-0002 | Potable Water: Filters - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-03-02 | 2027-03-23 | 2027-03-23 | 2027-03-30 | ALP-EPC-00GKA-ME-CAL-0001
6 | ALP-EPC-00PGA-IC-DSH-0002 | Closed Cooling Water - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-02 | 2027-03-23 | 2027-03-23 | 2027-03-30 | ALP-EPC-00PGA-PR-PID-0001
6 | ALP-EPC-00GKA-ME-DSH-0003 | Potable Water: Pumps - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-03-03 | 2027-03-24 | 2027-03-24 | 2027-03-31 | ALP-EPC-00GKA-ME-CAL-0001
6 | ALP-EPC-00SAA-IC-DSH-0001 | HVAC - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-03 | 2027-03-24 | 2027-03-24 | 2027-03-31 | capacity i_and_c
6 | ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-23 | 2027-03-03 |  | 2027-03-17 | 2027-03-31 | ALP-EPC-00UEG-PI-LAY-0001 | G-CON-CWP CWP-10-PI-01 | 2027-12-27 | G-CON-CWP CWP-10-PI-01 IFC G-CON-IWP CWP-10-PI-01 IFC
6 | ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-02-24 | 2027-03-24 | 2027-03-24 | 2027-03-31 | ALP-EPC-00000-CV-CAL-0001 | G-CON-CWP CWP-07-CV-01 | 2027-04-05 | G-CON-CWP CWP-07-CV-01 IFC G-CON-IWP CWP-07-CV-01 IFC
6 | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-18 | 2027-03-03 |  | 2027-03-17 | 2027-03-31 | capacity piping | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC
6 | ALP-EPC-00CKA-GE-ITP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Inspection and Test Plan |  | EPC | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-08 | 2027-03-29 | 2027-03-29 | 2027-04-05 | capacity general | G-PRC-PO MR-IC-009 | 2027-06-21 | G-PRC-PO MR-IC-009 IFR
6 | ALP-EPC-00PGA-IC-CNR-0001 | Closed Cooling Water - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-08 |  | 2027-03-22 | 2027-04-05 | ALP-EPC-00PGA-PR-PID-0001
6 | ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-03-08 |  | 2027-03-22 | 2027-04-05 | ALP-EPC-00UEK-PI-LAY-0001 | G-CON-CWP CWP-09-PI-01 | 2027-11-29 | G-CON-CWP CWP-09-PI-01 IFC G-CON-IWP CWP-09-PI-01 IFC
6 | ALP-EPC-00XJA-CM-OMM-0001 | Emergency Diesel Generator - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-03-08 |  | 2027-03-22 | 2027-04-05 | ALP-EPC-00XJA-CM-CMP-0001 | G-COM-SC-EL 00XJA | 2028-05-09 | G-COM-SC-EL 00XJA IFR G-OPS-HO-EL 00XJA IFC
6 | ALP-EPC-10BBT-CM-OMM-0001 | GT Unit Auxiliary Transformer - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-03-08 |  | 2027-03-22 | 2027-04-05 | ALP-EPC-10BBT-CM-CMP-0001 | G-COM-SC-EL 10BBT | 2028-05-09 | G-COM-SC-EL 10BBT IFR G-OPS-HO-EL 10BBT IFC
6 | ALP-EPC-20BBT-CM-OMM-0001 | ST Unit Auxiliary Transformer - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20BBT-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-03-08 |  | 2027-03-22 | 2027-04-05 | ALP-EPC-20BBT-CM-CMP-0001 | G-COM-SC-EL 20BBT | 2028-05-09 | G-COM-SC-EL 20BBT IFR G-OPS-HO-EL 20BBT IFC
6 | ALP-EPC-00000-ME-PLN-0001 | Marine Operations Plan | heavy-lift barge, harbour master approval | EPC | mechanical | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-STU-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-03-03 | 2027-03-31 | 2027-03-31 | 2027-04-07 | capacity mechanical
6 | ALP-EPC-00CYA-IC-DSH-0001 | Telecom, CCTV, Access Control, Security - Datasheet |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CYA-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-03-10 | 2027-03-31 | 2027-03-31 | 2027-04-07 | ALP-EPC-00CYA-GE-SPC-0001
6 | ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification |  | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-IC-BLK-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-03-03 | 2027-03-31 | 2027-03-31 | 2027-04-07 | capacity general | G-PRC-ENQ MR-IC-006 | 2027-05-24 | G-PRC-ENQ MR-IC-006 IFR G-PRC-PO MR-IC-006 IFC
6 | ALP-C03-00UPA-GE-ITP-0001 | Marine Works - Subcontractor Inspection and Test Plans |  | C03 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-04-08 | PO MR-CV-003
6 | ALP-C03-00UPA-GE-MOS-0001 | Marine Works - Subcontractor Method Statements, Part 1 of 6 |  | C03 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-04-08 | PO MR-CV-003
6 | ALP-C03-00UPA-GE-MOS-0002 | Marine Works - Subcontractor Method Statements, Part 2 of 6 |  | C03 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-04-08 | PO MR-CV-003
6 | ALP-C03-00UPA-GE-MOS-0003 | Marine Works - Subcontractor Method Statements, Part 3 of 6 |  | C03 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-04-08 | PO MR-CV-003
6 | ALP-C03-00UPA-GE-MOS-0004 | Marine Works - Subcontractor Method Statements, Part 4 of 6 |  | C03 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-04-08 | PO MR-CV-003
6 | ALP-C03-00UPA-GE-MOS-0005 | Marine Works - Subcontractor Method Statements, Part 5 of 6 |  | C03 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-04-08 | PO MR-CV-003
6 | ALP-C03-00UPA-GE-MOS-0006 | Marine Works - Subcontractor Method Statements, Part 6 of 6 |  | C03 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-04-08 | PO MR-CV-003
6 | ALP-EPC-00000-GE-RPT-0015 | Safety and Relief Valves - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0008 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-01 |  | 2027-04-01 | 2027-04-08 | capacity general | G-PRC-PO MR-PI-007 | 2027-08-02 | G-PRC-PO MR-PI-007 IFR
6 | ALP-EPC-00PAH-ME-DSH-0002 | Condenser Tube Cleaning: Filters - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-26 | 2027-03-12 | 2027-04-02 | 2027-04-02 | 2027-04-09 | ALP-EPC-00PAH-ME-CAL-0001
6 | ALP-EPC-00PAH-ME-DSH-0003 | Condenser Tube Cleaning: Pumps - Datasheet | 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-26 | 2027-03-12 | 2027-04-02 | 2027-04-02 | 2027-04-09 | ALP-EPC-00PAH-ME-CAL-0001
6 | ALP-EPC-00PGA-IC-DSH-0001 | Closed Cooling Water - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-12 | 2027-04-02 | 2027-04-02 | 2027-04-09 | ALP-EPC-00PGA-PR-PID-0001
6 | ALP-EPC-10HAN-ME-DSH-0002 | HRSG Blowdown and Drains: Pumps - Datasheet | EPC tanks and headers; 2 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-26 | 2027-03-12 | 2027-04-02 | 2027-04-02 | 2027-04-09 | ALP-EPC-10HAN-ME-CAL-0001
6 | ALP-E08-00000-ME-DSH-0001 | Power and Control Cables - Supplier Catalogues and Material Datasheets |  | E08 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-03-29 |  | 2027-04-12 | 2027-04-12 | PO MR-EL-008
6 | ALP-E08-00000-ME-ITP-0001 | Power and Control Cables - Supplier Inspection and Test Plan |  | E08 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-03-29 |  | 2027-04-12 | 2027-04-12 | PO MR-EL-008
6 | ALP-EPC-00000-GE-RPT-0014 | Piping Specialty Items - Technical Bid Evaluation | strainers, steam traps, expansion joints, sight glasses | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0007 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-04-05 |  | 2027-04-05 | 2027-04-12 | capacity general | G-PRC-PO MR-PI-006 | 2027-08-30 | G-PRC-PO MR-PI-006 IFR
6 | ALP-EPC-00GBA-IC-DSH-0002 | Seawater Reverse Osmosis - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-03-17 | 2027-04-07 | 2027-04-07 | 2027-04-14 | ALP-EPC-00GBA-PR-PID-0001
6 | ALP-EPC-00CYA-GE-ITP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Inspection and Test Plan |  | EPC | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-18 | 2027-04-08 | 2027-04-08 | 2027-04-15 | capacity general | G-PRC-PO MR-IC-007 | 2027-07-19 | G-PRC-PO MR-IC-007 IFR
6 | ALP-EPC-00QCA-ME-DSH-0003 | Chemical Dosing: Tanks - Datasheet | 3 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-03-18 | 2027-04-08 | 2027-04-08 | 2027-04-15 | ALP-EPC-00QCA-ME-CAL-0001
6 | ALP-EPC-00QJA-ME-DSH-0002 | Nitrogen Supply: Tank - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-18 | 2027-04-08 | 2027-04-08 | 2027-04-15 | ALP-EPC-00QJA-ME-CAL-0001
6 | ALP-EPC-00PBA-IC-DSH-0002 | Electro-Chlorination - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-03-19 | 2027-04-09 | 2027-04-09 | 2027-04-16 | ALP-EPC-00PBA-PR-PID-0001
6 | ALP-EPC-00QCA-ME-DSH-0002 | Chemical Dosing: Pumps - Datasheet | 6 items | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-03-19 | 2027-04-09 | 2027-04-09 | 2027-04-16 | ALP-EPC-00QCA-ME-CAL-0001
6 | ALP-EPC-00GNA-IC-DSH-0002 | Waste Water Treatment - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-03-22 | 2027-04-12 | 2027-04-12 | 2027-04-19 | ALP-EPC-00GNA-PR-PID-0001
6 | ALP-EPC-00QUA-ME-DSH-0002 | Sampling and SWAS: Heat Exchanger - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-IC-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-03-22 | 2027-04-12 | 2027-04-12 | 2027-04-19 | ALP-EPC-00QUA-ME-CAL-0001
6 | ALP-EPC-00GBA-IC-CNR-0001 | Seawater Reverse Osmosis - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-03-23 |  | 2027-04-06 | 2027-04-20 | ALP-EPC-00GBA-PR-PID-0001
6 | ALP-EPC-00UPC-SS-STL-0001 | CW Pump House - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-16 | 2027-04-13 | 2027-04-13 | 2027-04-20 | ALP-EPC-00UPC-CV-CAL-0001 | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
6 | ALP-P03-00000-ME-DSH-0001 | Valves - Supplier Catalogues and Material Datasheets | manual and check | P03 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-01 |  | 2027-04-15 | 2027-04-20 | PO MR-PI-003
6 | ALP-P03-00000-ME-ITP-0001 | Valves - Supplier Inspection and Test Plan | manual and check | P03 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-01 |  | 2027-04-20 | 2027-04-20 | PO MR-PI-003
6 | ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-17 | 2027-04-14 | 2027-04-14 | 2027-04-21 | capacity civil | G-CON-CWP CWP-08-CV-01 | 2027-05-04 | G-CON-CWP CWP-08-CV-01 IFC G-CON-IWP CWP-08-CV-01 IFC
6 | ALP-EPC-00CJA-CM-OMM-0001 | Plant DCS - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-25 |  | 2027-04-08 | 2027-04-22 | capacity commissioning | G-COM-SC-FF 00CJA | 2028-07-24 | G-COM-SC-FF 00CJA IFR G-OPS-HO-FF 00CJA IFC
6 | ALP-EPC-00GMA-IC-CNR-0001 | Process Drains and Waste Water Collection - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-25 |  | 2027-04-08 | 2027-04-22 | ALP-EPC-00GMA-PR-PID-0001
6 | ALP-EPC-00GNA-IC-CNR-0001 | Waste Water Treatment - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-03-26 |  | 2027-04-09 | 2027-04-23 | ALP-EPC-00GNA-PR-PID-0001
6 | ALP-EPC-00PAA-IC-CNR-0001 | CW Intake, Screens and Outfall - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-03-26 |  | 2027-04-09 | 2027-04-23 | ALP-EPC-00PAA-PR-PID-0001
6 | ALP-EPC-00PBA-IC-CNR-0001 | Electro-Chlorination - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-03-26 |  | 2027-04-09 | 2027-04-23 | ALP-EPC-00PBA-PR-PID-0001
6 | ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-03-26 |  | 2027-04-09 | 2027-04-23 | ALP-EPC-00QCA-PR-PID-0001
6 | ALP-EPC-00UAC-SS-STL-0002 | GIS Building - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UAC-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-19 | 2027-04-16 | 2027-04-16 | 2027-04-23 | ALP-EPC-00UAC-CV-CAL-0001 | G-CON-CWP CWP-04-SS-01 | 2027-05-31 | G-CON-CWP CWP-04-SS-01 IFC G-CON-IWP CWP-04-SS-01 IFC
6 | ALP-EPC-00GBA-IC-DSH-0001 | Seawater Reverse Osmosis - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-03-29 | 2027-04-19 | 2027-04-19 | 2027-04-26 | ALP-EPC-00GBA-PR-PID-0001
6 | ALP-EPC-00QEA-IC-CNR-0001 | Compressed Air - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-03-29 |  | 2027-04-12 | 2027-04-26 | ALP-EPC-00QEA-PR-PID-0001
6 | ALP-EPC-00UZC-EL-ELY-0001 | Site Drainage and Culverts - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZC-CV-CVL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-03-29 |  | 2027-04-12 | 2027-04-26 | ALP-EPC-00UZC-CV-CVL-0001 | G-CON-CWP CWP-12-EL-01 | 2027-05-17 | G-CON-CWP CWP-12-EL-01 IFC G-CON-IWP CWP-12-EL-01 IFC
6 | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | subcontract | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0004 is NONE, IFR needs it at IFR |  | 2027-04-16 | 2027-04-23 |  | 2027-04-23 | 2027-04-28 | ALP-EPC-00000-GE-SPC-0004 | G-PRC-ENQ MR-ME-022 | 2027-11-15 | G-PRC-ENQ MR-ME-022 IFR G-PRC-PO MR-ME-022 IFC
6 | ALP-EPC-00GMA-IC-DSH-0001 | Process Drains and Waste Water Collection - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-04-01 | 2027-04-22 | 2027-04-22 | 2027-04-29 | ALP-EPC-00GMA-PR-PID-0001
6 | ALP-P07-00000-ME-DSH-0001 | Safety and Relief Valves - Supplier Catalogues and Material Datasheets |  | P07 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0008 is NONE, IFR needs it at IFR |  | 2027-04-01 | 2027-04-15 |  | 2027-04-29 | 2027-04-29 | PO MR-PI-007
6 | ALP-P07-00000-ME-ITP-0001 | Safety and Relief Valves - Supplier Inspection and Test Plan |  | P07 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0008 is NONE, IFR needs it at IFR |  | 2027-04-01 | 2027-04-15 |  | 2027-04-29 | 2027-04-29 | PO MR-PI-007
6 | ALP-EPC-00CJG-CM-OMM-0001 | Safety Instrumented Systems - Operating Procedures | English / Turkish; BOP | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-04-02 |  | 2027-04-16 | 2027-04-30 | capacity commissioning | G-COM-SC-FF 00CJG | 2028-07-24 | G-COM-SC-FF 00CJG IFR G-OPS-HO-FF 00CJG IFC
6 | ALP-EPC-00GNA-IC-DSH-0001 | Waste Water Treatment - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-02 | 2027-04-23 | 2027-04-23 | 2027-04-30 | ALP-EPC-00GNA-PR-PID-0001
6 | ALP-EPC-00PAA-IC-DSH-0001 | CW Intake, Screens and Outfall - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-02 | 2027-04-23 | 2027-04-23 | 2027-04-30 | ALP-EPC-00PAA-PR-PID-0001
6 | ALP-EPC-00PBA-IC-DSH-0001 | Electro-Chlorination - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-02 | 2027-04-23 | 2027-04-23 | 2027-04-30 | ALP-EPC-00PBA-PR-PID-0001
6 | ALP-EPC-00QEA-IC-DSH-0002 | Compressed Air - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-09 | 2027-04-02 | 2027-04-23 | 2027-04-23 | 2027-04-30 | capacity i_and_c
6 | ALP-EPC-00000-HS-RPT-0002 | Constructability and Maintainability Review | AWP input | EPC | hse | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-STU-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-04-12 |  | 2027-04-26 | 2027-05-03 | capacity hse
6 | ALP-P06-00000-ME-DSH-0001 | Piping Specialty Items - Supplier Catalogues and Material Datasheets | strainers, steam traps, expansion joints, sight glasses | P06 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0007 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-04-19 |  | 2027-05-03 | 2027-05-03 | PO MR-PI-006
6 | ALP-P06-00000-ME-ITP-0001 | Piping Specialty Items - Supplier Inspection and Test Plan | strainers, steam traps, expansion joints, sight glasses | P06 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0007 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-04-19 |  | 2027-05-03 | 2027-05-03 | PO MR-PI-006
6 | ALP-EPC-00QCA-IC-DSH-0001 | Chemical Dosing - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-06 | 2027-04-27 | 2027-04-27 | 2027-05-04 | capacity i_and_c
6 | ALP-EPC-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-30 | 2027-04-27 | 2027-04-27 | 2027-05-04 | ALP-EPC-00UEG-CV-CAL-0001 | G-CON-CWP CWP-10-CV-01 | 2027-06-03 | G-CON-CWP CWP-10-CV-01 IFC G-CON-IWP CWP-10-CV-01 IFC
6 | ALP-EPC-00EGA-IC-DSH-0002 | LDO Unloading - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 | 2027-04-29 | 2027-04-29 | 2027-05-06 | ALP-EPC-00EGA-PR-PID-0001
6 | ALP-EPC-00CKA-CM-OMM-0001 | Historian, Performance Monitoring and Operator Training Simulator - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-04-09 |  | 2027-04-23 | 2027-05-07 | capacity commissioning | G-COM-SC-FF 00CKA | 2028-07-24 | G-COM-SC-FF 00CKA IFR G-OPS-HO-FF 00CKA IFC
6 | ALP-EPC-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZD-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-04-07 | 2027-05-05 | 2027-05-05 | 2027-05-12 | ALP-EPC-00UZD-CV-CAL-0001 | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
6 | ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-15 |  | 2027-04-29 | 2027-05-13 | ALP-EPC-00EGA-PR-PID-0001
6 | ALP-EPC-00QHA-IC-CNR-0001 | Auxiliary Boiler - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-03-24 | 2027-04-15 |  | 2027-04-29 | 2027-05-13 | ALP-EPC-00QHA-PR-PID-0001
6 | ALP-EPC-00UBA-SS-STL-0002 | Electrical Building - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-04-08 | 2027-05-06 | 2027-05-06 | 2027-05-13 | ALP-EPC-00UBA-CV-CAL-0001 | G-CON-CWP CWP-03-SS-01 | 2027-05-24 | G-CON-CWP CWP-03-SS-01 IFC G-CON-IWP CWP-03-SS-01 IFC
6 | ALP-EPC-00000-HS-RPT-0006 | Occupational Health and Safety Risk Assessment | design phase | EPC | hse | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0001 is NONE, IFR needs it at IFR |  | 2027-04-02 | 2027-04-23 |  | 2027-05-07 | 2027-05-14 | capacity hse
6 | ALP-EPC-00CQA-CM-OMM-0001 | Continuous Emission Monitoring - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-04-16 |  | 2027-04-30 | 2027-05-14 | capacity commissioning | G-COM-SC-FF 00CQA | 2028-07-24 | G-COM-SC-FF 00CQA IFR G-OPS-HO-FF 00CQA IFC
6 | ALP-EPC-00UGA-SS-STL-0002 | Water Treatment Building and Basins - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-04-09 | 2027-05-07 | 2027-05-07 | 2027-05-14 | ALP-EPC-00UGA-CV-CAL-0001 | G-CON-CWP CWP-07-SS-01 | 2027-06-14 | G-CON-CWP CWP-07-SS-01 IFC G-CON-IWP CWP-07-SS-01 IFC
6 | ALP-EPC-00UZD-CV-FND-0001 | Pipe Racks and Pipe Sleepers - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-04-09 | 2027-05-07 | 2027-05-07 | 2027-05-14 | capacity civil | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
6 | ALP-EPC-00UZE-EL-ELY-0001 | Cable Trenches and Duct Banks - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZE-CV-CVL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-16 |  | 2027-04-30 | 2027-05-14 | ALP-EPC-00UZE-CV-CVL-0001 | G-CON-CWP CWP-12-EL-01 | 2027-05-17 | G-CON-CWP CWP-12-EL-01 IFC G-CON-IWP CWP-12-EL-01 IFC
6 | ALP-EPC-00CYA-CM-OMM-0001 | Telecom, CCTV, Access Control, Security - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-04-19 |  | 2027-05-03 | 2027-05-17 | capacity commissioning | G-COM-SC-FF 00CYA | 2028-07-24 | G-COM-SC-FF 00CYA IFR G-OPS-HO-FF 00CYA IFC
6 | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-22 | 2027-04-19 |  | 2027-05-03 | 2027-05-17 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
6 | ALP-EPC-00BXA-GE-RPT-0001 | Cathodic Protection - Technical Bid Evaluation | marine structures, buried piping and tanks | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-20 | 2027-05-11 |  | 2027-05-11 | 2027-05-18 | bids MR-EL-010 | G-PRC-PO MR-EL-010 | 2027-06-21 | G-PRC-PO MR-EL-010 IFR
6 | ALP-EPC-00UBA-HV-GAD-0001 | Electrical Building and Emergency Power - HVAC Layouts |  | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-04-21 |  | 2027-05-05 | 2027-05-19 | capacity hvac | G-CON-CWP CWP-03-HV-01 | 2027-10-11 | G-CON-CWP CWP-03-HV-01 IFC G-CON-IWP CWP-03-HV-01 IFC
6 | ALP-EPC-00EGA-IC-DSH-0001 | LDO Unloading - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-22 | 2027-05-13 | 2027-05-13 | 2027-05-20 | ALP-EPC-00EGA-PR-PID-0001
6 | ALP-EPC-00EKC-IC-DSH-0002 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-04-23 | 2027-05-14 | 2027-05-14 | 2027-05-21 | ALP-EPC-00EKC-PR-PID-0001
6 | ALP-EPC-00EGA-PR-DSH-0001 | LDO Unloading - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-04-26 | 2027-05-17 | 2027-05-17 | 2027-05-24 | capacity process
6 | ALP-EPC-00GHA-IC-DSH-0002 | Demineralised Water Storage and Distribution - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-04-26 | 2027-05-17 | 2027-05-17 | 2027-05-24 | ALP-EPC-00GHA-PR-PID-0001
6 | ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-06 | 2027-04-27 |  | 2027-05-11 | 2027-05-25 | ALP-EPC-00EGB-PR-PID-0001
6 | ALP-EPC-00GCA-IC-DSH-0002 | Demineralisation - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-04-27 | 2027-05-18 | 2027-05-18 | 2027-05-25 | ALP-EPC-00GCA-PR-PID-0001
6 | ALP-EPC-00LBG-IC-DSH-0002 | Auxiliary Steam - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-04-28 | 2027-05-19 | 2027-05-19 | 2027-05-26 | ALP-EPC-00LBG-PR-PID-0001
6 | ALP-EPC-00LDA-IC-DSH-0002 | Condensate Polishing - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-13 | 2027-04-29 | 2027-05-20 | 2027-05-20 | 2027-05-27 | capacity i_and_c
6 | ALP-EPC-00UCA-HV-GAD-0001 | Control, Administration and Workshop Buildings - HVAC Layouts |  | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-29 | 2027-04-29 |  | 2027-05-13 | 2027-05-27 | capacity hvac | G-CON-CWP CWP-11-HV-01 | 2027-11-08 | G-CON-CWP CWP-11-HV-01 IFC G-CON-IWP CWP-11-HV-01 IFC
6 | ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-22 | 2027-05-20 | 2027-05-20 | 2027-05-27 | capacity civil | G-CON-CWP CWP-10-CV-01 | 2027-06-03 | G-CON-CWP CWP-10-CV-01 IFC G-CON-IWP CWP-10-CV-01 IFC
6 | ALP-EPC-10UMA-HV-GAD-0001 | Power Block - GT and HRSG - HVAC Layouts |  | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-18 | 2027-04-29 |  | 2027-05-13 | 2027-05-27 | capacity hvac | G-CON-CWP CWP-01-HV-01 | 2027-11-01 | G-CON-CWP CWP-01-HV-01 IFC G-CON-IWP CWP-01-HV-01 IFC
6 | ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-04-30 |  | 2027-05-14 | 2027-05-28 | ALP-EPC-00EKC-PR-PID-0001
6 | ALP-EPC-00GCA-IC-CNR-0001 | Demineralisation - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GCA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-04-30 |  | 2027-05-14 | 2027-05-28 | ALP-EPC-00GCA-PR-PID-0001
6 | ALP-EPC-00GHA-IC-CNR-0001 | Demineralised Water Storage and Distribution - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-03 |  | 2027-05-17 | 2027-05-31 | ALP-EPC-00GHA-PR-PID-0001
6 | ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-03 |  | 2027-05-17 | 2027-05-31 | ALP-EPC-00LBG-PR-PID-0001
6 | ALP-EPC-00LDA-IC-CNR-0001 | Condensate Polishing - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-03 |  | 2027-05-17 | 2027-05-31 | ALP-EPC-00LDA-PR-PID-0001
6 | ALP-EPC-00PAB-IC-CNR-0001 | CW Piping - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-03 |  | 2027-05-17 | 2027-05-31 | ALP-EPC-00PAB-PR-PID-0001
6 | ALP-EPC-00PAC-IC-CNR-0001 | CW Pumps - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-03 |  | 2027-05-17 | 2027-05-31 | ALP-EPC-00PAC-PR-PID-0001
6 | ALP-EPC-00EGB-IC-DSH-0001 | LDO Storage - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-06 | 2027-05-04 | 2027-05-25 | 2027-05-25 | 2027-06-01 | ALP-EPC-00EGB-PR-PID-0001
6 | ALP-EPC-00PAH-IC-CNR-0001 | Condenser Tube Cleaning - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-13 | 2027-05-04 |  | 2027-05-18 | 2027-06-01 | ALP-EPC-00PAH-PR-PID-0001
6 | ALP-EPC-00000-GE-RPT-0013 | Pipe Supports, Spring Hangers and Snubbers - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0006 is NONE, IFR needs it at IFR |  | 2027-05-06 | 2027-05-27 |  | 2027-05-27 | 2027-06-03 | bids MR-PI-005 | G-PRC-PO MR-PI-005 | 2027-08-30 | G-PRC-PO MR-PI-005 IFR
6 | ALP-EPC-00EKC-IC-DSH-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-07 | 2027-05-28 | 2027-05-28 | 2027-06-04 | ALP-EPC-00EKC-PR-PID-0001
6 | ALP-EPC-00GCA-IC-DSH-0001 | Demineralisation - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-07 | 2027-05-28 | 2027-05-28 | 2027-06-04 | ALP-EPC-00GCA-PR-PID-0001
6 | ALP-EPC-00GHA-IC-DSH-0001 | Demineralised Water Storage and Distribution - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-10 | 2027-05-31 | 2027-05-31 | 2027-06-07 | ALP-EPC-00GHA-PR-PID-0001
6 | ALP-EPC-00LBG-IC-DSH-0001 | Auxiliary Steam - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-10 | 2027-05-31 | 2027-05-31 | 2027-06-07 | ALP-EPC-00LBG-PR-PID-0001
6 | ALP-E10-00BXA-ME-ITP-0001 | Cathodic Protection - Supplier Inspection and Test Plan | marine structures, buried piping and tanks | E10 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-11 | 2027-05-25 |  | 2027-06-08 | 2027-06-08 | PO MR-EL-010 | G-PRC-FAB MR-EL-010 | 2027-08-04 | G-PRC-FAB MR-EL-010 ACCEPTED
6 | ALP-EPC-00LDA-IC-DSH-0001 | Condensate Polishing - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-13 | 2027-05-11 | 2027-06-01 | 2027-06-01 | 2027-06-08 | capacity i_and_c
6 | ALP-EPC-00PAB-IC-DSH-0001 | CW Piping - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-05-11 | 2027-06-01 | 2027-06-01 | 2027-06-08 | capacity i_and_c
6 | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-05-11 |  | 2027-05-25 | 2027-06-08 | capacity piping | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC
6 | ALP-EPC-00000-GE-RPT-0008 | Instrument Installation Materials - Technical Bid Evaluation | tubing, fittings, junction boxes, supports | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-05-12 | 2027-06-02 |  | 2027-06-02 | 2027-06-09 | bids MR-IC-010 | G-PRC-PO MR-IC-010 | 2027-11-29 | G-PRC-PO MR-IC-010 IFR
6 | ALP-EPC-00UZF-CV-RPT-0001 | Temporary Barge Landing Design Report and Removal Plan |  | EPC | civil | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-STU-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-05-19 |  | 2027-06-02 | 2027-06-09 | capacity civil
6 | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-05-12 |  | 2027-05-26 | 2027-06-09 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
6 | ALP-EPC-00000-CV-TRP-0001 | Pile Load Test Report and Pile Design Confirmation |  | EPC | civil | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-TST-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-05-20 |  | 2027-06-03 | 2027-06-10 | ALP-EPC-00000-CV-TST-0001 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
6 | ALP-EPC-00PAC-IC-DSH-0001 | CW Pumps - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-05-13 | 2027-06-03 | 2027-06-03 | 2027-06-10 | capacity i_and_c
6 | ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report |  | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-07 | 2027-06-04 | 2027-06-04 | 2027-06-11 | ALP-EPC-00EKC-PR-PID-0001
6 | ALP-EPC-00PAH-IC-DSH-0001 | Condenser Tube Cleaning - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-04-16 | 2027-05-14 | 2027-06-04 | 2027-06-04 | 2027-06-11 | capacity i_and_c
6 | ALP-EPC-00UCA-SS-STL-0002 | Control Building - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-31 | 2027-05-07 | 2027-06-04 | 2027-06-04 | 2027-06-11 | ALP-EPC-00UCA-CV-CAL-0001 | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
6 | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-05-14 |  | 2027-05-28 | 2027-06-11 | capacity piping | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC
6 | ALP-EPC-00UZC-CV-RBR-0001 | Site Drainage and Culverts - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZC-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-24 |  | 2027-06-07 | 2027-06-14 | capacity civil | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
6 | ALP-EPC-00EGC-PR-DSH-0001 | LDO Forwarding and Treatment - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-05-18 | 2027-06-08 | 2027-06-08 | 2027-06-15 | capacity process
6 | ALP-EPC-00UQA-SS-STL-0001 | Utility Building - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-03-29 | 2027-05-11 | 2027-06-08 | 2027-06-08 | 2027-06-15 | ALP-EPC-00UQA-CV-CAL-0001 | G-CON-CWP CWP-08-SS-01 | 2027-06-29 | G-CON-CWP CWP-08-SS-01 IFC G-CON-IWP CWP-08-SS-01 IFC
6 | ALP-EPC-00USA-SS-STL-0002 | Workshop and Warehouse - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00USA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-03-31 | 2027-05-11 | 2027-06-08 | 2027-06-08 | 2027-06-15 | ALP-EPC-00USA-CV-CAL-0001 | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
6 | ALP-EPC-00UYA-SS-STL-0002 | Administration Building - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UYA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-04-02 | 2027-05-11 | 2027-06-08 | 2027-06-08 | 2027-06-15 | capacity structural | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
6 | ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-28 | 2027-05-19 |  | 2027-06-02 | 2027-06-16 | ALP-EPC-00QJA-PR-PID-0001
6 | ALP-EPC-00UZE-CV-RBR-0001 | Cable Trenches and Duct Banks - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZE-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-27 |  | 2027-06-10 | 2027-06-17 | capacity civil | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
6 | ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-05-21 |  | 2027-06-04 | 2027-06-18 | ALP-EPC-00QJB-PR-PID-0001
6 | ALP-E10-00BXA-ME-TST-0001 | Cathodic Protection - Factory Acceptance Test Procedure | marine structures, buried piping and tanks | E10 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-20 | 2027-05-11 |  | 2027-06-08 | 2027-06-22 | PO MR-EL-010 | G-PRC-FAT MR-EL-010 | 2027-08-03 | G-PRC-FAT MR-EL-010 ACCEPTED
6 | ALP-EPC-00EGB-PR-DSH-0001 | LDO Storage - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-06 | 2027-05-26 | 2027-06-16 | 2027-06-16 | 2027-06-23 | capacity process
6 | ALP-EPC-00EKC-PR-DSH-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-04-26 | 2027-05-26 | 2027-06-16 | 2027-06-16 | 2027-06-23 | capacity process
6 | ALP-P05-00000-ME-DSH-0001 | Pipe Supports, Spring Hangers and Snubbers - Supplier Catalogues and Material Datasheets |  | P05 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0006 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-10 |  | 2027-06-24 | 2027-06-24 | PO MR-PI-005
6 | ALP-P05-00000-ME-ITP-0001 | Pipe Supports, Spring Hangers and Snubbers - Supplier Inspection and Test Plan |  | P05 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0006 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-10 |  | 2027-06-24 | 2027-06-24 | PO MR-PI-005
6 | ALP-EPC-00GCA-PR-DSH-0001 | Demineralisation - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-14 | 2027-05-28 | 2027-06-18 | 2027-06-18 | 2027-06-25 | capacity process
6 | ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-06 | 2027-05-28 |  | 2027-06-11 | 2027-06-25 | ALP-EPC-00QUA-PR-PID-0001
6 | ALP-EPC-00GBA-PR-DSH-0001 | Seawater Reverse Osmosis - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-05-31 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity process
6 | ALP-EPC-00GHA-PR-DSH-0001 | Demineralised Water Storage and Distribution - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-05-31 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity process
6 | ALP-EPC-00LDA-PR-DSH-0001 | Condensate Polishing - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-05-31 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity process
6 | ALP-EPC-00QEA-IC-DSH-0001 | Compressed Air - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-12 | 2027-05-31 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity i_and_c
6 | ALP-EPC-00UEK-CV-ARC-0001 | Gas Station Structures - Architectural Drawings |  | EPC | civil | ARC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-13 | 2027-05-24 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity civil | G-CON-CWP CWP-09-CV-01 | 2027-08-04 | G-CON-CWP CWP-09-CV-01 IFC G-CON-IWP CWP-09-CV-01 IFC
6 | ALP-E10-00BXA-IC-IOL-0001 | Cathodic Protection - Supplier I/O List, Control Philosophy and Interface Signals | marine structures, buried piping and tanks | E10 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-08 |  | 2027-06-22 | 2027-06-29 | PO MR-EL-010
6 | ALP-EPC-00LBG-PR-DSH-0001 | Auxiliary Steam - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-01 | 2027-06-22 | 2027-06-22 | 2027-06-29 | capacity process
6 | ALP-EPC-00SAA-PR-DSH-0001 | HVAC - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-01 | 2027-06-22 | 2027-06-22 | 2027-06-29 | capacity process
6 | ALP-EPC-00SGA-PR-CAL-0001 | Fire Water Network Hydraulic Calculation |  | EPC | process | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-08 |  | 2027-06-22 | 2027-06-29 | capacity process
6 | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | subcontract | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0005 is NONE, IFR needs it at IFR |  | 2027-06-18 | 2027-06-25 |  | 2027-06-25 | 2027-06-30 | ALP-EPC-00000-GE-SPC-0005 | G-PRC-ENQ MR-ME-023 | 2027-08-30 | G-PRC-ENQ MR-ME-023 IFR G-PRC-PO MR-ME-023 IFC
6 | ALP-EPC-00PGA-PR-DSH-0001 | Closed Cooling Water - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-02 | 2027-06-23 | 2027-06-23 | 2027-06-30 | capacity process
6 | ALP-EPC-00QJA-PR-DSH-0001 | Nitrogen Supply - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-02 | 2027-06-23 | 2027-06-23 | 2027-06-30 | capacity process
6 | ALP-EPC-00QJB-PR-DSH-0001 | Hydrogen and CO2 Supply - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-02 | 2027-06-23 | 2027-06-23 | 2027-06-30 | capacity process
6 | ALP-EPC-00UZF-CV-FND-0002 | Temporary Barge Landing - Piling Layout and Pile Schedule |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-SPC-0002 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-26 | 2027-06-23 | 2027-06-23 | 2027-06-30 | capacity civil | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
6 | ALP-I10-00000-ME-DSH-0001 | Instrument Installation Materials - Supplier Catalogues and Material Datasheets | tubing, fittings, junction boxes, supports | I10 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-06-02 | 2027-06-16 |  | 2027-06-30 | 2027-06-30 | PO MR-IC-010
6 | ALP-I10-00000-ME-ITP-0001 | Instrument Installation Materials - Supplier Inspection and Test Plan | tubing, fittings, junction boxes, supports | I10 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-06-02 | 2027-06-16 |  | 2027-06-30 | 2027-06-30 | PO MR-IC-010
6 | ALP-EPC-00QCA-PR-DSH-0001 | Chemical Dosing - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-03 | 2027-06-24 | 2027-06-24 | 2027-07-01 | capacity process
6 | ALP-EPC-00QEA-PR-DSH-0001 | Compressed Air - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-03 | 2027-06-24 | 2027-06-24 | 2027-07-01 | capacity process
6 | ALP-EPC-00QHA-PR-DSH-0001 | Auxiliary Boiler - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-03 | 2027-06-24 | 2027-06-24 | 2027-07-01 | capacity process
6 | ALP-EPC-00EKA-PR-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-04 | 2027-06-25 | 2027-06-25 | 2027-07-02 | capacity process
6 | ALP-EPC-00GKA-IC-DSH-0001 | Potable Water - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-04 | 2027-06-25 | 2027-06-25 | 2027-07-02 | ALP-EPC-00GKA-PR-PID-0001
6 | ALP-EPC-00GUA-IC-DSH-0001 | Sanitary Waste Water Treatment - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-04 | 2027-06-25 | 2027-06-25 | 2027-07-02 | ALP-EPC-00GUA-PR-PID-0001
6 | ALP-EPC-00UEK-SS-STL-0001 | Gas Station Structures - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-28 | 2027-06-25 | 2027-06-25 | 2027-07-02 | ALP-EPC-00UEK-CV-CAL-0001 | G-CON-CWP CWP-09-CV-01 | 2027-08-04 | G-CON-CWP CWP-09-CV-01 IFC G-CON-IWP CWP-09-CV-01 IFC
6 | ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | EPC tanks and headers | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-14 | 2027-06-04 |  | 2027-06-18 | 2027-07-02 | ALP-EPC-10HAN-PR-PID-0001
6 | ALP-EPC-00GKA-IC-CNR-0001 | Potable Water - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-07 |  | 2027-06-21 | 2027-07-05 | ALP-EPC-00GKA-PR-PID-0001
6 | ALP-EPC-00GUA-IC-CNR-0001 | Sanitary Waste Water Treatment - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-07 |  | 2027-06-21 | 2027-07-05 | ALP-EPC-00GUA-PR-PID-0001
6 | ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-04-28 | 2027-05-31 | 2027-06-28 | 2027-06-28 | 2027-07-05 | capacity civil | G-CON-CWP CWP-09-CV-01 | 2027-08-04 | G-CON-CWP CWP-09-CV-01 IFC G-CON-IWP CWP-09-CV-01 IFC
6 | ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-07 |  | 2027-06-21 | 2027-07-05 | ALP-EPC-10HSB-PR-PID-0001
6 | ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-07 |  | 2027-06-21 | 2027-07-05 | ALP-EPC-10LAE-PR-PID-0001
6 | ALP-EPC-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-05-31 | 2027-06-28 | 2027-06-28 | 2027-07-05 | ALP-EPC-10UMA-CV-CAL-0001 | G-CON-CWP CWP-01-SS-01 | 2027-07-12 | G-CON-CWP CWP-01-SS-01 IFC G-CON-IWP CWP-01-SS-01 IFC
6 | ALP-EPC-00UBF-SS-STL-0001 | Transformer Bays - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBF-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-06-01 | 2027-06-29 | 2027-06-29 | 2027-07-06 | ALP-EPC-00UBF-CV-CAL-0001 | G-CON-CWP CWP-01-SS-01 | 2027-07-12 | G-CON-CWP CWP-01-SS-01 IFC G-CON-IWP CWP-01-SS-01 IFC
6 | ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-08 |  | 2027-06-22 | 2027-07-06 | ALP-EPC-10LAB-PR-PID-0001
6 | ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAF-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-08 |  | 2027-06-22 | 2027-07-06 | ALP-EPC-10LAF-PR-PID-0001
6 | ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-08 |  | 2027-06-22 | 2027-07-06 | ALP-EPC-20LCA-PR-PID-0001
6 | ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-20MAN-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-08 |  | 2027-06-22 | 2027-07-06 | ALP-EPC-20MAN-PR-PID-0001
6 | ALP-EPC-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-06-01 | 2027-06-29 | 2027-06-29 | 2027-07-06 | capacity structural | G-CON-CWP CWP-02-SS-01 | 2027-07-12 | G-CON-CWP CWP-02-SS-01 IFC G-CON-IWP CWP-02-SS-01 IFC
6 | ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | aux boiler, air, N2, H2, CCW | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-06-02 | 2027-06-30 | 2027-06-30 | 2027-07-07 | capacity hse
6 | ALP-EPC-00SGA-PR-DSH-0001 | Fire Water System - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-09 | 2027-06-30 | 2027-06-30 | 2027-07-07 | capacity process
6 | ALP-EPC-10HAN-PR-DSH-0001 | HRSG Blowdown and Drains - Safety / Relief Valve Sizing and Datasheets | EPC tanks and headers | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-26 | 2027-06-09 | 2027-06-30 | 2027-06-30 | 2027-07-07 | capacity process
6 | ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-09 |  | 2027-06-23 | 2027-07-07 | ALP-EPC-10LAC-PR-PID-0001
6 | ALP-EPC-10LAB-PR-DSH-0001 | Feedwater Piping - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-10 | 2027-07-01 | 2027-07-01 | 2027-07-08 | capacity process
6 | ALP-EPC-10LAC-PR-DSH-0001 | Boiler Feed Pumps - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-10 | 2027-07-01 | 2027-07-01 | 2027-07-08 | capacity process
6 | ALP-EPC-10HSB-PR-DSH-0001 | Ammonia Storage and Supply - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-26 | 2027-06-11 | 2027-07-02 | 2027-07-02 | 2027-07-09 | capacity process
6 | ALP-EPC-20LCA-PR-DSH-0001 | Main Condensate Piping - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-28 | 2027-06-11 | 2027-07-02 | 2027-07-02 | 2027-07-09 | capacity process
6 | ALP-EPC-00QHA-IC-DSH-0002 | Auxiliary Boiler - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-24 | 2027-06-14 | 2027-07-05 | 2027-07-05 | 2027-07-12 | capacity i_and_c
6 | ALP-EPC-20MAN-PR-DSH-0001 | Turbine Bypass Stations and Piping - Safety / Relief Valve Sizing and Datasheets |  | EPC | process | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-14 | 2027-07-05 | 2027-07-05 | 2027-07-12 | capacity process
6 | ALP-EPC-00QHA-IC-DSH-0001 | Auxiliary Boiler - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-24 | 2027-06-18 | 2027-07-09 | 2027-07-09 | 2027-07-16 | capacity i_and_c
6 | ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report |  | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-14 | 2027-07-12 | 2027-07-12 | 2027-07-19 | ALP-EPC-10HSB-PR-PID-0001
6 | ALP-EPC-00QJA-IC-DSH-0002 | Nitrogen Supply - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-21 | 2027-07-12 | 2027-07-12 | 2027-07-19 | capacity i_and_c
6 | ALP-E10-00BXA-ME-LST-0001 | Cathodic Protection - Spare Parts and Special Tools Lists | marine structures, buried piping and tanks | E10 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-01 | 2027-06-22 |  | 2027-07-06 | 2027-07-20 | PO MR-EL-010
6 | ALP-E10-00BXA-ME-PRC-0001 | Cathodic Protection - Supplier Installation and Erection Manual | marine structures, buried piping and tanks | E10 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-08 |  | 2027-06-22 | 2027-07-20 | PO MR-EL-010
6 | ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report |  | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-15 | 2027-07-13 | 2027-07-13 | 2027-07-20 | capacity hse
6 | ALP-EPC-00PAB-PR-STU-0001 | CW System Hydraulic Transient Analysis | surge / water hammer | EPC | process | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-ME-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-ME-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-22 |  | 2027-07-06 | 2027-07-20 | capacity process
6 | ALP-EPC-00QJB-IC-DSH-0002 | Hydrogen and CO2 Supply - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-06-22 | 2027-07-13 | 2027-07-13 | 2027-07-20 | capacity i_and_c
6 | ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-06-02 | 2027-06-23 |  | 2027-07-07 | 2027-07-21 | ALP-EPC-10LBA-PR-PID-0001
6 | ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBB-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-06-02 | 2027-06-23 |  | 2027-07-07 | 2027-07-21 | ALP-EPC-10LBB-PR-PID-0001
6 | ALP-EPC-00GKA-PI-PPL-0001 | Potable Water - Underground Piping Drawings |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZC-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-24 |  | 2027-07-08 | 2027-07-22 | ALP-EPC-00GKA-PR-PID-0001 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-COM-MC-FF 00GKA IFC G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
6 | ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBC-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-06-03 | 2027-06-24 |  | 2027-07-08 | 2027-07-22 | ALP-EPC-10LBC-PR-PID-0001
6 | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR |  | 2027-04-16 | 2027-06-28 |  | 2027-07-12 | 2027-07-26 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
6 | ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBD-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-28 |  | 2027-07-12 | 2027-07-26 | ALP-EPC-10LBD-PR-PID-0001
6 | ALP-EPC-00GMA-PI-PPL-0001 | Process Drains and Waste Water Collection - Underground Piping Drawings |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZC-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2027-05-12 | 2027-06-29 |  | 2027-07-13 | 2027-07-27 | capacity piping | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-COM-MC-FF 00GMA IFC G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
6 | ALP-EPC-00PAB-PI-PPL-0001 | CW Piping - Underground Piping Drawings |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZC-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2027-05-14 | 2027-06-29 |  | 2027-07-13 | 2027-07-27 | capacity piping | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PAB IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC
6 | ALP-EPC-00000-IC-LST-0001 | Instrument Index |  | EPC | i_and_c | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-30 |  | 2027-07-14 | 2027-07-28 | ALP-EPC-20LCB-PR-PID-0001 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
6 | ALP-EPC-00000-PR-LST-0002 | Line List |  | EPC | process | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-30 |  | 2027-07-14 | 2027-07-28 | ALP-EPC-20LCB-PR-PID-0001 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
6 | ALP-EPC-00SGA-IC-DSH-0001 | Fire Water System - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-06-30 | 2027-07-21 | 2027-07-21 | 2027-07-28 | capacity i_and_c
6 | ALP-EPC-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Structure Drawings |  | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-SS-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-05-21 | 2027-06-23 | 2027-07-21 | 2027-07-21 | 2027-07-28 | ALP-EPC-00UZF-CV-CAL-0001 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
6 | ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative |  | EPC | i_and_c | CNR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-30 |  | 2027-07-14 | 2027-07-28 | ALP-EPC-20LCB-PR-PID-0001
6 | ALP-EPC-00QJA-IC-DSH-0001 | Nitrogen Supply - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-07-01 | 2027-07-22 | 2027-07-22 | 2027-07-29 | capacity i_and_c
6 | ALP-P01-00000-ME-MDB-0001 | Piping Bulk Materials - Manufacturing Record Book and Conformity Certificates | carbon steel, stainless | P01 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-20 | 2027-06-03 |  | 2027-06-03 | 2027-07-29 | PO MR-PI-001 | G-PRC-SHP MR-PI-001 | 2027-06-17 | G-PRC-SHP MR-PI-001 IFR
6 | ALP-EPC-00QJB-IC-DSH-0001 | Hydrogen and CO2 Supply - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-07-06 | 2027-07-27 | 2027-07-27 | 2027-08-03 | capacity i_and_c
6 | ALP-EPC-00UBA-PI-PPL-0001 | Electrical Building and Emergency Power - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR |  | 2027-05-12 | 2027-07-08 |  | 2027-07-22 | 2027-08-05 | capacity piping | G-CON-CWP CWP-03-HV-01 | 2027-10-11 | G-CON-CWP CWP-03-HV-01 IFC G-CON-IWP CWP-03-HV-01 IFC
6 | ALP-EPC-00QUA-IC-DSH-0001 | Sampling and SWAS - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-07-09 | 2027-07-30 | 2027-07-30 | 2027-08-06 | capacity i_and_c
6 | ALP-EPC-00UCA-PI-PPL-0001 | Control, Administration and Workshop Buildings - Piping General Arrangement |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR |  | 2027-05-12 | 2027-07-09 |  | 2027-07-23 | 2027-08-06 | capacity piping | G-CON-CWP CWP-11-HV-01 | 2027-11-08 | G-CON-CWP CWP-11-HV-01 IFC G-CON-IWP CWP-11-HV-01 IFC
6 | ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings |  | EPC | civil | CVL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-PLT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPA-CV-CAL-0002 is NONE, IFR needs it at IFR |  | 2027-05-10 | 2027-07-02 | 2027-07-30 | 2027-07-30 | 2027-08-06 | ALP-EPC-00UPA-CV-CAL-0002 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
6 | ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report |  | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-07-07 | 2027-08-04 | 2027-08-04 | 2027-08-11 | ALP-EPC-20LCB-PR-PID-0001
6 | ALP-E10-00BXA-ME-TRP-0001 | Cathodic Protection - Factory Acceptance Test Report | marine structures, buried piping and tanks | E10 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-27 | 2027-08-03 |  | 2027-08-17 | 2027-08-17 | PO MR-EL-010 | G-PRC-SHP MR-EL-010 | 2027-08-31 | G-PRC-SHP MR-EL-010 ACCEPTED
6 | ALP-EPC-00SGY-CM-OMM-0001 | Fire Detection and Alarm - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-07-20 |  | 2027-08-03 | 2027-08-17 | capacity commissioning | G-COM-SC-FF 00SGY | 2028-07-24 | G-COM-SC-FF 00SGY IFR G-OPS-HO-FF 00SGY IFC
6 | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-M3D-0001 is NONE, IFR needs it at IFR |  | 2027-05-10 | 2027-07-21 |  | 2027-08-04 | 2027-08-18 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
6 | ALP-P06-00000-ME-MDB-0001 | Piping Specialty Items - Manufacturing Record Book and Conformity Certificates | strainers, steam traps, expansion joints, sight glasses | P06 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0007 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-07-12 |  | 2027-07-12 | 2027-09-06 | PO MR-PI-006 | G-PRC-SHP MR-PI-006 | 2027-07-26 | G-PRC-SHP MR-PI-006 IFR
6 | ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-07-09 | 2027-08-06 | 2027-09-03 | 2027-09-03 | 2027-09-10 | capacity commissioning | G-OWN-TOC 00000 | 2028-08-21 | G-OWN-TOC 00000 ACCEPTED
6 | ALP-E08-00000-ME-MDB-0001 | Power and Control Cables - Manufacturing Record Book and Conformity Certificates |  | E08 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-05 | 2027-07-19 |  | 2027-07-19 | 2027-09-13 | PO MR-EL-008 | G-PRC-SHP MR-EL-008 | 2027-08-02 | G-PRC-SHP MR-EL-008 IFR
6 | ALP-EPC-00000-CM-CMP-0005 | Tests on LDO Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBY-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-07-20 | 2027-08-17 | 2027-09-14 | 2027-09-14 | 2027-09-21 | capacity commissioning | G-OWN-TOC 00000 | 2028-08-21 | G-OWN-TOC 00000 ACCEPTED
6 | ALP-EPC-00000-CM-CMP-0006 | Emission and Noise Test Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-STU-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CQA-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-07-22 | 2027-08-19 | 2027-09-16 | 2027-09-16 | 2027-09-23 | capacity commissioning | G-OWN-TOC 00000 | 2028-08-21 | G-OWN-TOC 00000 ACCEPTED
6 | ALP-EPC-00SGA-PI-PPL-0001 | Fire Water System - Underground Piping Drawings |  | EPC | piping | PPL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZC-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-08-26 |  | 2027-09-09 | 2027-09-23 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00SGA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
6 | ALP-P07-00000-ME-MDB-0001 | Safety and Relief Valves - Manufacturing Record Book and Conformity Certificates |  | P07 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0008 is NONE, IFR needs it at IFR |  | 2027-07-22 | 2027-08-05 |  | 2027-08-05 | 2027-09-30 | PO MR-PI-007 | G-PRC-SHP MR-PI-007 | 2027-08-19 | G-PRC-SHP MR-PI-007 IFR
6 | ALP-I10-00000-ME-MDB-0001 | Instrument Installation Materials - Manufacturing Record Book and Conformity Certificates | tubing, fittings, junction boxes, supports | I10 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-07-28 | 2027-08-11 |  | 2027-08-11 | 2027-10-06 | PO MR-IC-010 | G-PRC-SHP MR-IC-010 | 2027-08-25 | G-PRC-SHP MR-IC-010 IFR
6 | ALP-E10-00BXA-ME-MDB-0001 | Cathodic Protection - Manufacturing Record Book and Conformity Certificates | marine structures, buried piping and tanks | E10 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-03 | 2027-08-17 |  | 2027-08-17 | 2027-10-12 | PO MR-EL-010 | G-PRC-SHP MR-EL-010 | 2027-08-31 | G-PRC-SHP MR-EL-010 IFR
6 | ALP-P03-00000-ME-MDB-0001 | Valves - Manufacturing Record Book and Conformity Certificates | manual and check | P03 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0003 is NONE, IFR needs it at IFR |  | 2027-08-16 | 2027-08-30 |  | 2027-08-30 | 2027-10-25 | PO MR-PI-003 | G-PRC-SHP MR-PI-003 | 2027-09-13 | G-PRC-SHP MR-PI-003 IFR
6 | ALP-P05-00000-ME-MDB-0001 | Pipe Supports, Spring Hangers and Snubbers - Manufacturing Record Book and Conformity Certificates |  | P05 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0006 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-09-02 |  | 2027-09-02 | 2027-10-28 | PO MR-PI-005 | G-PRC-SHP MR-PI-005 | 2027-09-16 | G-PRC-SHP MR-PI-005 IFR
6 | ALP-EPC-00SGC-IC-DSH-0001 | Deluge, Spray and Foam Systems - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-10-06 | 2027-10-27 | 2027-10-27 | 2027-11-03 | capacity i_and_c
6 | ALP-EPC-10HAN-IC-DSH-0002 | HRSG Blowdown and Drains - Control Valve Sizing and Datasheets | EPC tanks and headers | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-06-29 | 2027-10-06 | 2027-10-27 | 2027-10-27 | 2027-11-03 | capacity i_and_c
6 | ALP-EPC-10HSB-IC-DSH-0002 | Ammonia Storage and Supply - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-10-08 | 2027-10-29 | 2027-10-29 | 2027-11-05 | capacity i_and_c
6 | ALP-EPC-00000-EL-CAL-0002 | Battery, UPS and DC System Sizing Calculation |  | EPC | electrical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR |  | 2027-09-27 | 2027-10-18 |  | 2027-11-01 | 2027-11-08 | capacity electrical
6 | ALP-EPC-10HAN-IC-DSH-0001 | HRSG Blowdown and Drains - Instrument Datasheets | EPC tanks and headers | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-07-05 | 2027-10-11 | 2027-11-01 | 2027-11-01 | 2027-11-08 | capacity i_and_c
6 | ALP-EPC-00000-EL-CAL-0003 | Emergency Diesel Generator and Transformer Sizing Calculation |  | EPC | electrical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR |  | 2027-09-28 | 2027-10-19 |  | 2027-11-02 | 2027-11-09 | capacity electrical
6 | ALP-EPC-10LAB-IC-DSH-0002 | Feedwater Piping - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-10-12 | 2027-11-02 | 2027-11-02 | 2027-11-09 | capacity i_and_c
6 | ALP-EPC-10LAC-IC-DSH-0002 | Boiler Feed Pumps - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-10-13 | 2027-11-03 | 2027-11-03 | 2027-11-10 | capacity i_and_c
6 | ALP-EPC-10LAE-IC-DSH-0002 | HP Attemperation Spray Water - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-10-05 | 2027-10-19 | 2027-11-09 | 2027-11-09 | 2027-11-16 | capacity i_and_c
6 | ALP-EPC-10HSB-IC-DSH-0001 | Ammonia Storage and Supply - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-10-22 | 2027-11-12 | 2027-11-12 | 2027-11-19 | capacity i_and_c
6 | ALP-EPC-10LAB-IC-DSH-0001 | Feedwater Piping - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-10-22 | 2027-11-12 | 2027-11-12 | 2027-11-19 | capacity i_and_c
6 | ALP-EPC-10LAE-IC-DSH-0001 | HP Attemperation Spray Water - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-10-22 | 2027-11-12 | 2027-11-12 | 2027-11-19 | capacity i_and_c
6 | ALP-EPC-10LAF-IC-DSH-0002 | Reheat Attemperation Spray Water - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-10-08 | 2027-10-22 | 2027-11-12 | 2027-11-12 | 2027-11-19 | capacity i_and_c
6 | ALP-E10-00BXA-ME-OMM-0001 | Cathodic Protection - Supplier Operation and Maintenance Manual | marine structures, buried piping and tanks | E10 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-25 | 2027-07-06 |  | 2027-07-20 | 2027-11-23 | PO MR-EL-010 | G-COM-SC-EL 00BXA | 2028-05-09 | G-COM-SC-EL 00BXA IFR G-OPS-HO-EL 00BXA IFC
6 | ALP-EPC-10LAC-IC-DSH-0001 | Boiler Feed Pumps - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-10-27 | 2027-11-17 | 2027-11-17 | 2027-11-24 | capacity i_and_c
6 | ALP-EPC-10LAF-IC-DSH-0001 | Reheat Attemperation Spray Water - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-10-08 | 2027-10-28 | 2027-11-18 | 2027-11-18 | 2027-11-25 | capacity i_and_c
6 | ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual |  | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-09-14 | 2027-10-29 |  | 2027-11-12 | 2027-11-26 | capacity commissioning | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFC
6 | ALP-EPC-10LBA-IC-DSH-0001 | Main Steam Piping - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-10-08 | 2027-11-05 | 2027-11-26 | 2027-11-26 | 2027-12-03 | capacity i_and_c
6 | ALP-EPC-10LBB-IC-DSH-0001 | Hot Reheat Piping - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-10-11 | 2027-11-08 | 2027-11-29 | 2027-11-29 | 2027-12-06 | capacity i_and_c
6 | ALP-EPC-20LCB-IC-DSH-0002 | Condensate Extraction Pumps - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-10-22 | 2027-11-08 | 2027-11-29 | 2027-11-29 | 2027-12-06 | capacity i_and_c
6 | ALP-EPC-10LBD-IC-DSH-0001 | LP Steam Piping - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-10-15 | 2027-11-09 | 2027-11-30 | 2027-11-30 | 2027-12-07 | capacity i_and_c
6 | ALP-EPC-20LCA-IC-DSH-0002 | Main Condensate Piping - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-10-22 | 2027-11-09 | 2027-11-30 | 2027-11-30 | 2027-12-07 | capacity i_and_c
6 | ALP-EPC-10LBC-IC-DSH-0001 | Cold Reheat Piping - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-10-15 | 2027-11-10 | 2027-12-01 | 2027-12-01 | 2027-12-08 | capacity i_and_c
6 | ALP-EPC-20MAN-IC-DSH-0002 | Turbine Bypass Stations and Piping - Control Valve Sizing and Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-PR-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-10-29 | 2027-11-15 | 2027-12-06 | 2027-12-06 | 2027-12-13 | capacity i_and_c
6 | ALP-EPC-20LCA-IC-DSH-0001 | Main Condensate Piping - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-10-20 | 2027-11-17 | 2027-12-08 | 2027-12-08 | 2027-12-15 | capacity i_and_c
6 | ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List |  | EPC | commissioning | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-10-28 | 2027-11-18 |  | 2027-12-02 | 2027-12-16 | capacity commissioning | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
6 | ALP-EPC-00000-CM-LST-0003 | Punch List at Taking-Over |  | EPC | commissioning | LST | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PRC-0001 is NONE, IFR needs it at IFR |  | 2027-11-11 | 2027-12-02 |  | 2027-12-02 | 2027-12-16 | ALP-EPC-00000-CM-PRC-0001 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
6 | ALP-EPC-20LCB-IC-DSH-0001 | Condensate Extraction Pumps - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-10-26 | 2027-11-23 | 2027-12-14 | 2027-12-14 | 2027-12-21 | capacity i_and_c
6 | ALP-EPC-20MAN-IC-DSH-0001 | Turbine Bypass Stations and Piping - Instrument Datasheets |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-10-29 | 2027-11-26 | 2027-12-17 | 2027-12-17 | 2027-12-24 | capacity i_and_c
6 | ALP-EPC-00ACA-CM-MDB-0001 | 380 kV GIS Switchyard - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00ACA | 2028-04-11 | G-COM-MC-EL 00ACA IFR G-COM-SC-EL 00ACA IFR G-OPS-HO-EL 00ACA IFC
6 | ALP-EPC-00BBA-CM-MDB-0001 | MV Switchgear 10.5 kV - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00BBA | 2028-04-11 | G-COM-MC-EL 00BBA IFR G-COM-SC-EL 00BBA IFR G-OPS-HO-EL 00BBA IFC
6 | ALP-EPC-00BFA-CM-MDB-0001 | LV Switchgear 0.4 kV - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00BFA | 2028-04-11 | G-COM-MC-EL 00BFA IFR G-COM-SC-EL 00BFA IFR G-OPS-HO-EL 00BFA IFC
6 | ALP-EPC-00BFT-CM-MDB-0001 | LV Transformers - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00BFT | 2028-04-11 | G-COM-MC-EL 00BFT IFR G-COM-SC-EL 00BFT IFR G-OPS-HO-EL 00BFT IFC
6 | ALP-EPC-00BLA-CM-MDB-0001 | Lighting and Small Power - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BLA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00BLA | 2028-04-11 | G-COM-MC-EL 00BLA IFR G-COM-SC-EL 00BLA IFR G-OPS-HO-EL 00BLA IFC
6 | ALP-EPC-00BMA-CM-MDB-0001 | Emergency LV Switchgear - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BMA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00BMA | 2028-04-11 | G-COM-MC-EL 00BMA IFR G-COM-SC-EL 00BMA IFR G-OPS-HO-EL 00BMA IFC
6 | ALP-EPC-00BRA-CM-MDB-0001 | UPS - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00BRA | 2028-04-11 | G-COM-MC-EL 00BRA IFR G-COM-SC-EL 00BRA IFR G-OPS-HO-EL 00BRA IFC
6 | ALP-EPC-00BTA-CM-MDB-0001 | Batteries and DC 220 V - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BTA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00BTA | 2028-04-11 | G-COM-MC-EL 00BTA IFR G-COM-SC-EL 00BTA IFR G-OPS-HO-EL 00BTA IFC
6 | ALP-EPC-00BXA-CM-MDB-0001 | Earthing and Lightning Protection - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BXA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00BXA | 2028-04-11 | G-COM-MC-EL 00BXA IFR G-COM-SC-EL 00BXA IFR G-OPS-HO-EL 00BXA IFC
6 | ALP-EPC-00XJA-CM-MDB-0001 | Emergency Diesel Generator - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 00XJA | 2028-04-11 | G-COM-MC-EL 00XJA IFR G-COM-SC-EL 00XJA IFR G-OPS-HO-EL 00XJA IFC
6 | ALP-EPC-10BBT-CM-MDB-0001 | GT Unit Auxiliary Transformer - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-04 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | as late as possible (need) | G-COM-MC-EL 10BBT | 2028-04-11 | G-COM-MC-EL 10BBT IFR G-COM-SC-EL 10BBT IFR G-OPS-HO-EL 10BBT IFC
6 | ALP-EPC-20BBT-CM-MDB-0001 | ST Unit Auxiliary Transformer - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20BBT-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-01-18 | 2028-02-01 |  | 2028-02-01 | 2028-02-08 | capacity commissioning | G-COM-MC-EL 20BBT | 2028-04-11 | G-COM-MC-EL 20BBT IFR G-COM-SC-EL 20BBT IFR G-OPS-HO-EL 20BBT IFC
6 | ALP-EPC-00000-PI-LST-0001 | Valve List |  | EPC | piping | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR |  | 2027-12-23 | 2028-01-13 |  | 2028-01-27 | 2028-02-10 | capacity piping | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
6 | ALP-EPC-00000-CM-OMM-0002 | Training Manuals and Courseware | classroom, simulator, on-the-job | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-PLN-0002 is NONE, IFR needs it at IFR |  | 2027-11-25 | 2028-01-20 |  | 2028-02-03 | 2028-02-17 | capacity commissioning
6 | ALP-EPC-00CJA-CM-MDB-0001 | Plant DCS - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00CJA | 2028-06-26 | G-COM-MC-FF 00CJA IFR G-COM-SC-FF 00CJA IFR G-OPS-HO-FF 00CJA IFC
6 | ALP-EPC-00CJG-CM-MDB-0001 | Safety Instrumented Systems - System Turnover Dossier | BOP | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00CJG | 2028-06-26 | G-COM-MC-FF 00CJG IFR G-COM-SC-FF 00CJG IFR G-OPS-HO-FF 00CJG IFC
6 | ALP-EPC-00CKA-CM-MDB-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00CKA | 2028-06-26 | G-COM-MC-FF 00CKA IFR G-COM-SC-FF 00CKA IFR G-OPS-HO-FF 00CKA IFC
6 | ALP-EPC-00CQA-CM-MDB-0001 | Continuous Emission Monitoring - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00CQA | 2028-06-26 | G-COM-MC-FF 00CQA IFR G-COM-SC-FF 00CQA IFR G-OPS-HO-FF 00CQA IFC
6 | ALP-EPC-00CYA-CM-MDB-0001 | Telecom, CCTV, Access Control, Security - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00CYA | 2028-06-26 | G-COM-MC-FF 00CYA IFR G-COM-SC-FF 00CYA IFR G-OPS-HO-FF 00CYA IFC
6 | ALP-EPC-00SGY-CM-MDB-0001 | Fire Detection and Alarm - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 00SGY | 2028-06-26 | G-COM-MC-FF 00SGY IFR G-COM-SC-FF 00SGY IFR G-OPS-HO-FF 00SGY IFC
6 | ALP-EPC-00SMA-CM-MDB-0001 | Cranes and Hoists - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 00SMA | 2028-06-26 | G-COM-MC-FF 00SMA IFR G-COM-SC-FF 00SMA IFR G-OPS-HO-FF 00SMA IFC
6 | ALP-EPC-10HNE-CM-MDB-0001 | Stack 65 m with CEMS Platform and Silencer - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 10HNE | 2028-06-26 | G-COM-MC-FF 10HNE IFR G-COM-SC-FF 10HNE IFR G-OPS-HO-FF 10HNE IFC
6 | ALP-EPC-00CQA-IC-TRP-0001 | CEMS Certification, QAL1 / QAL2 and AST Reports | EN 14181 | EPC | i_and_c | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2029-02-12 | 2029-02-19 |  | 2029-03-05 | 2029-03-12 | after COM-010
6 | ALP-EPC-00000-CM-TRP-0004 | Operational Demonstration and Reliability Run Report |  | EPC | commissioning | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-CMP-0004 is NONE, IFR needs it at IFR |  | 2029-03-28 | 2029-04-04 |  | 2029-04-18 | 2029-04-25 | after COM-040 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
7 | ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition |  | EPC | piping | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-SPC-0007 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-ME-DSH-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-PI-004 | 2026-12-21 | G-PRC-ENQ MR-PI-004 IFR G-PRC-PO MR-PI-004 IFC
7 | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition |  | EPC | i_and_c | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CQA-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-IC-002 | 2027-05-03 | G-PRC-ENQ MR-IC-002 IFR G-PRC-PO MR-IC-002 IFC
7 | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-DSH-0003 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-ME-DSH-0004 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-016 | 2026-11-16 | G-PRC-ENQ MR-ME-016 IFR G-PRC-PO MR-ME-016 IFC
7 | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-ME-DSH-0003 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-ME-DSH-0004 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-015 | 2026-11-16 | G-PRC-ENQ MR-ME-015 IFR G-PRC-PO MR-ME-015 IFC
7 | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-ME-DSH-0003 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-013 | 2027-03-29 | G-PRC-ENQ MR-ME-013 IFR G-PRC-PO MR-ME-013 IFC
7 | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-ME-DSH-0003 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-ME-DSH-0002 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-014 | 2027-03-22 | G-PRC-ENQ MR-ME-014 IFR G-PRC-PO MR-ME-014 IFC
7 | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | SWRO, demin, condensate polishing | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GCA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-ME-DSH-0003 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-012 | 2026-11-16 | G-PRC-ENQ MR-ME-012 IFR G-PRC-PO MR-ME-012 IFC
7 | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-ME-DSH-0003 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-004 | 2027-02-01 | G-PRC-ENQ MR-ME-004 IFR G-PRC-PO MR-ME-004 IFC
7 | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-003 | 2026-11-23 | G-PRC-ENQ MR-ME-003 IFR G-PRC-PO MR-ME-003 IFC
7 | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-ME-DSH-0003 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-006 | 2027-04-26 | G-PRC-ENQ MR-ME-006 IFR G-PRC-PO MR-ME-006 IFC
7 | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-DSH-0003 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-DSH-0004 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-ME-DSH-0005 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-005 | 2027-02-01 | G-PRC-ENQ MR-ME-005 IFR G-PRC-PO MR-ME-005 IFC
7 | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-ME-DSH-0003 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-ME-DSH-0004 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-007 | 2027-01-25 | G-PRC-ENQ MR-ME-007 IFR G-PRC-PO MR-ME-007 IFC
7 | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-ME-DSH-0003 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-008 | 2027-01-25 | G-PRC-ENQ MR-ME-008 IFR G-PRC-PO MR-ME-008 IFC
7 | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-ME-DSH-0003 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-ME-DSH-0004 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-009 | 2026-11-16 | G-PRC-ENQ MR-ME-009 IFR G-PRC-PO MR-ME-009 IFC
7 | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition |  | EPC | i_and_c | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-ME-DSH-0002 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-IC-003 | 2027-05-03 | G-PRC-ENQ MR-IC-003 IFR G-PRC-PO MR-IC-003 IFC
7 | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition |  | EPC | hvac | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-ME-DSH-0003 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-HV-001 | 2027-01-04 | G-PRC-ENQ MR-HV-001 IFR G-PRC-PO MR-HV-001 IFC
7 | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00SGC-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGC-ME-DSH-0002 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-020 | 2027-01-11 | G-PRC-ENQ MR-ME-020 IFR G-PRC-PO MR-ME-020 IFC
7 | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SMA-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-021 | 2026-11-30 | G-PRC-ENQ MR-ME-021 IFR G-PRC-PO MR-ME-021 IFC
7 | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-ME-DSH-0002 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-019 | 2027-03-15 | G-PRC-ENQ MR-ME-019 IFR G-PRC-PO MR-ME-019 IFC
7 | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-018 | 2027-01-25 | G-PRC-ENQ MR-ME-018 IFR G-PRC-PO MR-ME-018 IFC
7 | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-001 | 2026-11-16 | G-PRC-ENQ MR-ME-001 IFR G-PRC-PO MR-ME-001 IFC
7 | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-ME-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-ME-002 | 2027-02-01 | G-PRC-ENQ MR-ME-002 IFR G-PRC-PO MR-ME-002 IFC
7 | ALP-EPC-00000-EL-SLD-0002 | Construction Power Supply Single Line Diagram and RMU Design |  | EPC | electrical | SLD | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-16 |  | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
7 | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | API 650 | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-ME-DSH-0001 is NONE, IFR needs it at IFR |  | 2026-11-16 | 2026-11-23 |  | 2026-11-23 | 2026-11-26 | capacity mechanical | G-PRC-ENQ MR-ME-017 | 2027-05-17 | G-PRC-ENQ MR-ME-017 IFR G-PRC-PO MR-ME-017 IFC
7 | ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-EL-003 | 2026-12-07 | G-PRC-ENQ MR-EL-003 IFR G-PRC-PO MR-EL-003 IFC
7 | ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-EL-005 | 2027-01-18 | G-PRC-ENQ MR-EL-005 IFR G-PRC-PO MR-EL-005 IFC
7 | ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-EL-004 | 2027-03-22 | G-PRC-ENQ MR-EL-004 IFR G-PRC-PO MR-EL-004 IFC
7 | ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-EL-007 | 2027-03-22 | G-PRC-ENQ MR-EL-007 IFR G-PRC-PO MR-EL-007 IFC
7 | ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-EL-006 | 2026-12-07 | G-PRC-ENQ MR-EL-006 IFR G-PRC-PO MR-EL-006 IFC
7 | ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-EL-002 | 2027-01-25 | G-PRC-ENQ MR-EL-002 IFR G-PRC-PO MR-EL-002 IFC
7 | ALP-EPC-00000-EL-STU-0005 | Insulation Coordination Study | 380 kV | EPC | electrical | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-12-07 |  | 2026-12-21 | 2027-01-04
7 | ALP-EPC-00000-GE-SPC-0002 | Electrical and I&C Installation - Technical Specification | subcontract | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-04 | 2026-12-11 | 2027-01-08 | 2027-01-08 | 2027-01-15 | capacity general | G-PRC-ENQ MR-EL-012 | 2027-09-06 | G-PRC-ENQ MR-EL-012 IFR G-PRC-PO MR-EL-012 IFC
7 | ALP-EPC-00000-GE-RPT-0001 | Piling Works - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-03 | 2027-01-14 |  | 2027-01-14 | 2027-01-21 | capacity general | G-PRC-PO MR-CV-001 | 2027-03-22 | G-PRC-PO MR-CV-001 IFR
7 | ALP-EPC-00BBA-EL-SLD-0001 | MV Switchgear 10.5 kV - Single Line Diagram |  | EPC | electrical | SLD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-12-10 | 2027-01-01 | 2027-01-29 | 2027-01-29 | 2027-02-05 | capacity electrical | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
7 | ALP-EPC-00000-EL-STU-0001 | Load Flow, Short-Circuit and Motor Starting Study | IEC 60909 | EPC | electrical | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2027-01-11 |  | 2027-01-25 | 2027-02-08 | capacity electrical
7 | ALP-EPC-10HNE-GE-RPT-0001 | Stack 65 m with Silencer - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-12 | 2027-02-02 |  | 2027-02-02 | 2027-02-09 | capacity general | G-PRC-PO MR-SS-002 | 2027-03-22 | G-PRC-PO MR-SS-002 IFR
7 | ALP-C01-00000-GE-ITP-0001 | Piling Works - Subcontractor Inspection and Test Plans |  | C01 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-01-28 |  | 2027-02-11 | 2027-02-11 | PO MR-CV-001
7 | ALP-C01-00000-GE-MOS-0001 | Piling Works - Subcontractor Method Statements, Part 1 of 6 |  | C01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-01-28 |  | 2027-02-11 | 2027-02-11 | PO MR-CV-001
7 | ALP-C01-00000-GE-MOS-0002 | Piling Works - Subcontractor Method Statements, Part 2 of 6 |  | C01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-01-28 |  | 2027-02-11 | 2027-02-11 | PO MR-CV-001
7 | ALP-C01-00000-GE-MOS-0003 | Piling Works - Subcontractor Method Statements, Part 3 of 6 |  | C01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-01-28 |  | 2027-02-11 | 2027-02-11 | PO MR-CV-001
7 | ALP-C01-00000-GE-MOS-0004 | Piling Works - Subcontractor Method Statements, Part 4 of 6 |  | C01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-01-28 |  | 2027-02-11 | 2027-02-11 | PO MR-CV-001
7 | ALP-C01-00000-GE-MOS-0005 | Piling Works - Subcontractor Method Statements, Part 5 of 6 |  | C01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-01-28 |  | 2027-02-11 | 2027-02-11 | PO MR-CV-001
7 | ALP-C01-00000-GE-MOS-0006 | Piling Works - Subcontractor Method Statements, Part 6 of 6 |  | C01 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-01-28 |  | 2027-02-11 | 2027-02-11 | PO MR-CV-001
7 | ALP-EPC-10LBA-GE-RPT-0001 | Alloy Piping P91 / P22 - Technical Bid Evaluation | main steam, reheat | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-02-04 |  | 2027-02-04 | 2027-02-11 | bids MR-PI-002 | G-PRC-PO MR-PI-002 | 2027-02-22 | G-PRC-PO MR-PI-002 IFR
7 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram |  | EPC | electrical | SLD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-12-16 | 2027-01-08 | 2027-02-05 | 2027-02-05 | 2027-02-12 | capacity electrical | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
7 | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | IEC 61511 | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CJG-IC-DSH-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-02-22 |  | 2027-02-22 | 2027-02-25 | ALP-EPC-00CJG-IC-DSH-0001 | G-PRC-ENQ MR-IC-008 | 2027-04-12 | G-PRC-ENQ MR-IC-008 IFR G-PRC-PO MR-IC-008 IFC
7 | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition |  | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CKA-IC-DSH-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-02-22 |  | 2027-02-22 | 2027-02-25 | ALP-EPC-00CKA-IC-DSH-0001 | G-PRC-ENQ MR-IC-009 | 2027-04-12 | G-PRC-ENQ MR-IC-009 IFR G-PRC-PO MR-IC-009 IFC
7 | ALP-EPC-00UZA-EL-ELY-0001 | Site-Wide Infrastructure - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UZA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-01-28 |  | 2027-02-11 | 2027-02-25 | ALP-EPC-00000-EL-STU-0003 | G-CON-CWP CWP-12-EL-01 | 2027-05-17 | G-CON-CWP CWP-12-EL-01 IFC G-CON-IWP CWP-12-EL-01 IFC
7 | ALP-EPC-00UPA-EL-ELY-0002 | Marine Works - Electrical Layouts | equipment, trays, earthing, lighting; offshore | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR |  | 2026-12-29 | 2027-01-29 |  | 2027-02-12 | 2027-02-26 | ALP-EPC-00UPA-PI-LAY-0001 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
7 | ALP-EPC-00UCA-EL-ELY-0001 | Control, Administration and Workshop Buildings - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-02-01 |  | 2027-02-15 | 2027-03-01 | ALP-EPC-00000-EL-STU-0003 | G-CON-CWP CWP-11-EL-01 | 2027-11-08 | G-CON-CWP CWP-11-EL-01 IFC G-CON-IWP CWP-11-EL-01 IFC
7 | ALP-EPC-00UBA-EL-ELY-0001 | Electrical Building and Emergency Power - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-02-02 |  | 2027-02-16 | 2027-03-02 | ALP-EPC-00000-EL-STU-0003 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
7 | ALP-S02-10HNE-GE-ITP-0001 | Stack 65 m with Silencer - Subcontractor Inspection and Test Plans |  | S02 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 |  | 2027-03-16 | 2027-03-16 | PO MR-SS-002
7 | ALP-S02-10HNE-GE-MOS-0001 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 1 of 6 |  | S02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 |  | 2027-03-09 | 2027-03-16 | PO MR-SS-002
7 | ALP-S02-10HNE-GE-MOS-0002 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 2 of 6 |  | S02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 |  | 2027-03-09 | 2027-03-16 | PO MR-SS-002
7 | ALP-S02-10HNE-GE-MOS-0003 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 3 of 6 |  | S02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 |  | 2027-03-09 | 2027-03-16 | PO MR-SS-002
7 | ALP-S02-10HNE-GE-MOS-0004 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 4 of 6 |  | S02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 |  | 2027-03-09 | 2027-03-16 | PO MR-SS-002
7 | ALP-S02-10HNE-GE-MOS-0005 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 5 of 6 |  | S02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 |  | 2027-03-09 | 2027-03-16 | PO MR-SS-002
7 | ALP-S02-10HNE-GE-MOS-0006 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 6 of 6 |  | S02 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 |  | 2027-03-09 | 2027-03-16 | PO MR-SS-002
7 | ALP-EPC-00UAC-HV-GAD-0001 | GIS Building - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-02-19 |  | 2027-03-05 | 2027-03-19 | capacity hvac | G-CON-CWP CWP-04-CV-01 | 2027-04-05 | G-CON-CWP CWP-04-CV-01 IFC G-CON-IWP CWP-04-CV-01 IFC
7 | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition |  | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CYA-IC-DSH-0001 is NONE, IFR needs it at IFR |  | 2027-03-10 | 2027-03-17 |  | 2027-03-17 | 2027-03-22 | ALP-EPC-00CYA-IC-DSH-0001 | G-PRC-ENQ MR-IC-007 | 2027-05-24 | G-PRC-ENQ MR-IC-007 IFR G-PRC-PO MR-IC-007 IFC
7 | ALP-EPC-00UPC-IC-ELY-0002 | CW Pump House - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-22 |  | 2027-03-08 | 2027-03-22 | ALP-EPC-00000-HS-HAZ-0009 | G-CON-CWP CWP-05-IC-01 | 2028-02-28 | G-CON-CWP CWP-05-IC-01 IFC G-CON-IWP CWP-05-IC-01 IFC
7 | ALP-EPC-00UAC-IC-ELY-0001 | GIS Building - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-23 |  | 2027-03-09 | 2027-03-23 | ALP-EPC-00000-HS-HAZ-0009 | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
7 | ALP-EPC-20UMB-IC-ELY-0002 | Steam Turbine Hall - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-23 |  | 2027-03-09 | 2027-03-23 | ALP-EPC-00000-HS-HAZ-0009 | G-CON-CWP CWP-02-IC-01 | 2028-03-27 | G-CON-CWP CWP-02-IC-01 IFC G-CON-IWP CWP-02-IC-01 IFC
7 | ALP-EPC-00UBA-IC-ELY-0001 | Electrical Building - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-24 |  | 2027-03-10 | 2027-03-24 | ALP-EPC-00000-HS-HAZ-0009 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
7 | ALP-EPC-00UGA-IC-ELY-0002 | Water Treatment Building and Basins - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-25 |  | 2027-03-11 | 2027-03-25 | ALP-EPC-00UGA-CV-ARC-0001 | G-CON-CWP CWP-07-IC-01 | 2028-03-20 | G-CON-CWP CWP-07-IC-01 IFC G-CON-IWP CWP-07-IC-01 IFC
7 | ALP-EPC-00UQA-IC-ELY-0002 | Utility Building - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-25 |  | 2027-03-11 | 2027-03-25 | ALP-EPC-00UQA-CV-ARC-0001 | G-CON-CWP CWP-08-IC-01 | 2028-02-21 | G-CON-CWP CWP-08-IC-01 IFC G-CON-IWP CWP-08-IC-01 IFC
7 | ALP-EPC-00USA-IC-ELY-0001 | Workshop and Warehouse - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00USA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-25 |  | 2027-03-11 | 2027-03-25 | ALP-EPC-00USA-CV-ARC-0001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
7 | ALP-EPC-00UPC-HS-GAD-0001 | CW Pump House - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-19 | 2027-03-19 | 2027-03-19 | 2027-03-26 | ALP-EPC-00000-HS-HAZ-0009 | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
7 | ALP-S02-10HNE-CV-CAL-0001 | Stack 65 m with Silencer - Supplier Foundation Loads and Anchor Bolt Drawings |  | S02 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HNE-SS-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-11 | 2027-03-04 |  | 2027-03-18 | 2027-03-26 | PO MR-SS-002
7 | ALP-EPC-00UAC-HS-GAD-0001 | GIS Building - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-22 | 2027-03-22 | 2027-03-22 | 2027-03-29 | ALP-EPC-00000-HS-HAZ-0009 | G-CON-CWP CWP-04-CV-01 | 2027-04-05 | G-CON-CWP CWP-04-CV-01 IFC G-CON-IWP CWP-04-CV-01 IFC
7 | ALP-EPC-20UMB-HS-GAD-0001 | Steam Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-22 | 2027-03-22 | 2027-03-22 | 2027-03-29 | ALP-EPC-00000-HS-HAZ-0009 | G-CON-CWP CWP-02-CV-02 | 2027-04-19 | G-CON-CWP CWP-02-CV-02 IFC G-CON-IWP CWP-02-CV-02 IFC
7 | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-ME-DSH-0002 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-03-25 |  | 2027-03-25 | 2027-03-30 | ALP-EPC-00QJA-ME-DSH-0002 | G-PRC-ENQ MR-ME-010 | 2027-05-10 | G-PRC-ENQ MR-ME-010 IFR G-PRC-PO MR-ME-010 IFC
7 | ALP-EPC-00UBA-HS-GAD-0001 | Electrical Building - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-23 | 2027-03-23 | 2027-03-23 | 2027-03-30 | ALP-EPC-00000-HS-HAZ-0009 | G-CON-CWP CWP-03-CV-01 | 2027-03-29 | G-CON-CWP CWP-03-CV-01 IFC G-CON-IWP CWP-03-CV-01 IFC
7 | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition |  | EPC | mechanical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-ME-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-ME-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-ME-DSH-0003 is NONE, IFR needs it at IFR |  | 2027-03-19 | 2027-03-26 |  | 2027-03-26 | 2027-03-31 | ALP-EPC-00QCA-ME-DSH-0002 | G-PRC-ENQ MR-ME-011 | 2027-04-05 | G-PRC-ENQ MR-ME-011 IFR G-PRC-PO MR-ME-011 IFC
7 | ALP-EPC-00UEK-EL-ELY-0001 | Fuel Gas Station - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-03-03 |  | 2027-03-17 | 2027-03-31 | capacity electrical | G-CON-CWP CWP-09-EL-01 | 2027-12-27 | G-CON-CWP CWP-09-EL-01 IFC G-CON-IWP CWP-09-EL-01 IFC
7 | ALP-EPC-00UGA-HS-GAD-0001 | Water Treatment Building and Basins - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-24 | 2027-03-24 | 2027-03-24 | 2027-03-31 | ALP-EPC-00UGA-CV-ARC-0001 | G-CON-CWP CWP-07-CV-01 | 2027-04-05 | G-CON-CWP CWP-07-CV-01 IFC G-CON-IWP CWP-07-CV-01 IFC
7 | ALP-EPC-00USA-HS-GAD-0001 | Workshop and Warehouse - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00USA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-24 | 2027-03-24 | 2027-03-24 | 2027-03-31 | ALP-EPC-00USA-CV-ARC-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-10UMA-IC-ELY-0002 | Gas Turbine Hall - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-03-03 |  | 2027-03-17 | 2027-03-31 | ALP-EPC-10UMA-CV-ARC-0001 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
7 | ALP-S01-00UAC-SS-STL-0001 | GIS Building - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-SS-STL-0002 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-04-SS-01 | 2027-05-31 | G-CON-CWP CWP-04-SS-01 IFC G-CON-IWP CWP-04-SS-01 IFC
7 | ALP-S01-00UBA-SS-STL-0001 | Electrical Building - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-SS-STL-0002 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-03-SS-01 | 2027-05-24 | G-CON-CWP CWP-03-SS-01 IFC G-CON-IWP CWP-03-SS-01 IFC
7 | ALP-S01-00UBF-SS-STL-0001 | Transformer Bays - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBF-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-01-SS-01 | 2027-07-12 | G-CON-CWP CWP-01-SS-01 IFC G-CON-IWP CWP-01-SS-01 IFC
7 | ALP-S01-00UCA-SS-STL-0001 | Control Building - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-SS-STL-0002 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
7 | ALP-S01-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-10-CV-01 | 2027-06-03 | G-CON-CWP CWP-10-CV-01 IFC G-CON-IWP CWP-10-CV-01 IFC
7 | ALP-S01-00UEK-SS-STL-0001 | Gas Station Structures - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-09-CV-01 | 2027-08-04 | G-CON-CWP CWP-09-CV-01 IFC G-CON-IWP CWP-09-CV-01 IFC
7 | ALP-S01-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-SS-STL-0002 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-07-SS-01 | 2027-06-14 | G-CON-CWP CWP-07-SS-01 IFC G-CON-IWP CWP-07-SS-01 IFC
7 | ALP-S01-00UPC-SS-STL-0001 | CW Pump House - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
7 | ALP-S01-00UQA-SS-STL-0001 | Utility Building - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-08-SS-01 | 2027-06-29 | G-CON-CWP CWP-08-SS-01 IFC G-CON-IWP CWP-08-SS-01 IFC
7 | ALP-S01-00USA-SS-STL-0001 | Workshop and Warehouse - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00USA-SS-STL-0002 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
7 | ALP-S01-00UYA-SS-STL-0001 | Administration Building - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UYA-SS-STL-0002 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
7 | ALP-S01-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Fabrication and Erection Drawings, Part 1 of 2 |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZD-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
7 | ALP-S01-00UZD-SS-STL-0002 | Pipe Racks and Pipe Sleepers - Steel Fabrication and Erection Drawings, Part 2 of 2 |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZD-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
7 | ALP-S01-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
7 | ALP-S01-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-01-SS-01 | 2027-07-12 | G-CON-CWP CWP-01-SS-01 IFC G-CON-IWP CWP-01-SS-01 IFC
7 | ALP-S01-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Fabrication and Erection Drawings |  | S01 | structural | STL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-SS-STL-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-10 |  | 2027-03-10 | 2027-03-31 | PO MR-SS-001 | G-CON-CWP CWP-02-SS-01 | 2027-07-12 | G-CON-CWP CWP-02-SS-01 IFC G-CON-IWP CWP-02-SS-01 IFC
7 | ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-CV-FND-0002 is NONE, IFR needs it at IFR |  | 2027-01-19 | 2027-02-25 | 2027-03-25 | 2027-03-25 | 2027-04-01 | ALP-EPC-00UPC-CV-FND-0002 | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
7 | ALP-EPC-00UQA-HS-GAD-0001 | Utility Building - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-25 | 2027-03-25 | 2027-03-25 | 2027-04-01 | ALP-EPC-00UQA-CV-ARC-0001 | G-CON-CWP CWP-08-CV-01 | 2027-05-04 | G-CON-CWP CWP-08-CV-01 IFC G-CON-IWP CWP-08-CV-01 IFC
7 | ALP-EPC-00EKA-IC-HMI-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-03-12 |  | 2027-03-26 | 2027-04-02 | ALP-EPC-00EKA-IC-CNR-0001
7 | ALP-EPC-00USA-HV-GAD-0001 | Workshop and Warehouse - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00USA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-03-05 |  | 2027-03-19 | 2027-04-02 | ALP-EPC-00USA-CV-ARC-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-00EGC-IC-HMI-0001 | LDO Forwarding and Treatment - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-15 |  | 2027-03-29 | 2027-04-05 | ALP-EPC-00EGC-IC-CNR-0001
7 | ALP-EPC-00UCA-IC-ELY-0002 | Control Building - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-09 |  | 2027-03-23 | 2027-04-06 | ALP-EPC-00UCA-CV-ARC-0001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
7 | ALP-EPC-00USA-CV-RBR-0001 | Workshop and Warehouse - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00USA-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-02-17 | 2027-03-16 |  | 2027-03-30 | 2027-04-06 | ALP-EPC-00USA-CV-FND-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-00UYA-CV-RBR-0001 | Administration Building - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UYA-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-02-17 | 2027-03-16 |  | 2027-03-30 | 2027-04-06 | ALP-EPC-00UYA-CV-FND-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-00UYA-IC-ELY-0001 | Administration Building - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UYA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-09 |  | 2027-03-23 | 2027-04-06 | ALP-EPC-00UYA-CV-ARC-0001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
7 | ALP-EPC-10UMA-EL-ELY-0001 | Power Block - GT and HRSG - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2026-12-28 | 2027-03-09 |  | 2027-03-23 | 2027-04-06 | capacity electrical | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
7 | ALP-EPC-10UMA-HS-GAD-0001 | Gas Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-03-02 | 2027-03-30 | 2027-03-30 | 2027-04-06 | ALP-EPC-10UMA-CV-ARC-0001 | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
7 | ALP-EPC-00UCA-CV-RBR-0001 | Control Building - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-02-17 | 2027-03-17 |  | 2027-03-31 | 2027-04-07 | ALP-EPC-00UCA-CV-FND-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-00UAC-CV-RBR-0001 | GIS Building - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-18 |  | 2027-04-01 | 2027-04-08 | ALP-EPC-00UAC-CV-FND-0001 | G-CON-CWP CWP-04-CV-01 | 2027-04-05 | G-CON-CWP CWP-04-CV-01 IFC G-CON-IWP CWP-04-CV-01 IFC
7 | ALP-EPC-00UBA-HV-GAD-0002 | Electrical Building - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-21 | 2027-03-11 |  | 2027-03-25 | 2027-04-08 | ALP-EPC-00UBA-CV-ARC-0001 | G-CON-CWP CWP-03-CV-01 | 2027-03-29 | G-CON-CWP CWP-03-CV-01 IFC G-CON-IWP CWP-03-CV-01 IFC
7 | ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UHA-CV-FND-0002 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-03-04 | 2027-04-01 | 2027-04-01 | 2027-04-08 | ALP-EPC-10UHA-CV-FND-0002 | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
7 | ALP-P02-10LBA-ME-DSH-0001 | Alloy Piping P91 / P22 - Supplier Catalogues and Material Datasheets | main steam, reheat | P02 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 |  | 2027-03-25 | 2027-04-08 | PO MR-PI-002
7 | ALP-P02-10LBA-ME-ITP-0001 | Alloy Piping P91 / P22 - Supplier Inspection and Test Plan | main steam, reheat | P02 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 |  | 2027-04-01 | 2027-04-08 | PO MR-PI-002
7 | ALP-EPC-00UCA-HS-GAD-0001 | Control Building - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-05 | 2027-04-02 | 2027-04-02 | 2027-04-09 | ALP-EPC-00UCA-CV-ARC-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-00UYA-HS-GAD-0001 | Administration Building - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UYA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-05 | 2027-04-02 | 2027-04-02 | 2027-04-09 | ALP-EPC-00UYA-CV-ARC-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-00UBA-CV-RBR-0001 | Electrical Building - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-22 |  | 2027-04-05 | 2027-04-12 | ALP-EPC-00UBA-CV-FND-0001 | G-CON-CWP CWP-03-CV-01 | 2027-03-29 | G-CON-CWP CWP-03-CV-01 IFC G-CON-IWP CWP-03-CV-01 IFC
7 | ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBF-CV-FND-0002 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-09 | 2027-04-06 | 2027-04-06 | 2027-04-13 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
7 | ALP-EPC-00SGY-IC-DSH-0001 | Fire Detection and Alarm: Control System - Datasheet |  | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGY-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-03-17 | 2027-04-07 | 2027-04-07 | 2027-04-14 | ALP-EPC-00SGY-GE-SPC-0001
7 | ALP-EPC-00UCA-EL-ELY-0003 | Control Building - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-02-17 | 2027-03-17 |  | 2027-03-31 | 2027-04-14 | ALP-EPC-00UCA-CV-FND-0001 | G-CON-CWP CWP-11-EL-01 | 2027-11-08 | G-CON-CWP CWP-11-EL-01 IFC G-CON-IWP CWP-11-EL-01 IFC
7 | ALP-EPC-00USA-EL-ELY-0001 | Workshop and Warehouse - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00USA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-02-17 | 2027-03-17 |  | 2027-03-31 | 2027-04-14 | ALP-EPC-00USA-CV-FND-0001 | G-CON-CWP CWP-11-EL-01 | 2027-11-08 | G-CON-CWP CWP-11-EL-01 IFC G-CON-IWP CWP-11-EL-01 IFC
7 | ALP-EPC-00UYA-EL-ELY-0001 | Administration Building - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UYA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-02-17 | 2027-03-17 |  | 2027-03-31 | 2027-04-14 | ALP-EPC-00UYA-CV-FND-0001 | G-CON-CWP CWP-11-EL-01 | 2027-11-08 | G-CON-CWP CWP-11-EL-01 IFC G-CON-IWP CWP-11-EL-01 IFC
7 | ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UHN-CV-FND-0002 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-10 | 2027-04-07 | 2027-04-07 | 2027-04-14 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
7 | ALP-EPC-00UAC-SS-STL-0001 | GIS Building - Structural Drawings | concrete / steel | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UAC-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UAC-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-11 | 2027-04-08 | 2027-04-08 | 2027-04-15 | ALP-EPC-00UAC-CV-CAL-0001 | G-CON-CWP CWP-04-SS-01 | 2027-05-31 | G-CON-CWP CWP-04-SS-01 IFC G-CON-IWP CWP-04-SS-01 IFC
7 | ALP-EPC-00UQA-EL-ELY-0001 | BOP Utilities - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-01-29 | 2027-03-18 |  | 2027-04-01 | 2027-04-15 | capacity electrical | G-CON-CWP CWP-08-EL-01 | 2028-01-10 | G-CON-CWP CWP-08-EL-01 IFC G-CON-IWP CWP-08-EL-01 IFC
7 | ALP-EPC-00SGY-GE-ITP-0001 | Fire Detection and Alarm System - Inspection and Test Plan |  | EPC | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-19 | 2027-04-09 | 2027-04-09 | 2027-04-16 | capacity general | G-PRC-PO MR-IC-006 | 2027-07-19 | G-PRC-PO MR-IC-006 IFR
7 | ALP-EPC-00UBA-EL-ELY-0003 | Electrical Building - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-19 |  | 2027-04-02 | 2027-04-16 | ALP-EPC-00UBA-CV-FND-0001 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
7 | ALP-EPC-00UPC-HV-GAD-0001 | CW Pump House - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-05 | 2027-03-19 |  | 2027-04-02 | 2027-04-16 | capacity hvac | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
7 | ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-03-12 | 2027-04-09 | 2027-04-09 | 2027-04-16 | ALP-EPC-10UMA-CV-FND-0001 | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
7 | ALP-EPC-00UZA-EL-ELY-0003 | Roads and Paving - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZA-CV-CVL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-03-22 |  | 2027-04-05 | 2027-04-19 | ALP-EPC-00UZA-CV-CVL-0002 | G-CON-CWP CWP-12-EL-01 | 2027-05-17 | G-CON-CWP CWP-12-EL-01 IFC G-CON-IWP CWP-12-EL-01 IFC
7 | ALP-EPC-00EKA-CM-CMP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-03-16 | 2027-04-13 | 2027-04-13 | 2027-04-20 | ALP-EPC-00EKA-IC-CNR-0001 | G-COM-SC-FF 00EKA | 2028-07-24 | G-COM-SC-FF 00EKA ACCEPTED
7 | ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-IEC-20MAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-03-16 | 2027-04-13 | 2027-04-13 | 2027-04-20 | ALP-EPC-20UMB-CV-FND-0001 | G-CON-CWP CWP-02-CV-02 | 2027-04-19 | G-CON-CWP CWP-02-CV-02 IFC G-CON-IWP CWP-02-CV-02 IFC
7 | ALP-EPC-00PGA-IC-HMI-0001 | Closed Cooling Water - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-03-31 |  | 2027-04-14 | 2027-04-21 | ALP-EPC-00PGA-IC-CNR-0001
7 | ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-02-17 | 2027-03-17 | 2027-04-14 | 2027-04-14 | 2027-04-21 | ALP-EPC-00SGA-IC-CNR-0001 | G-COM-SC-FF 00SGA | 2028-07-24 | G-COM-SC-FF 00SGA ACCEPTED
7 | ALP-EPC-00SGC-CM-CMP-0001 | Deluge, Spray and Foam Systems - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-02-17 | 2027-03-17 | 2027-04-14 | 2027-04-14 | 2027-04-21 | ALP-EPC-00SGC-IC-CNR-0001 | G-COM-SC-FF 00SGC | 2028-07-24 | G-COM-SC-FF 00SGC ACCEPTED
7 | ALP-EPC-00EGC-CM-CMP-0001 | LDO Forwarding and Treatment - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-18 | 2027-04-15 | 2027-04-15 | 2027-04-22 | ALP-EPC-00EGC-IC-CNR-0001 | G-COM-SC-FF 00EGC | 2028-07-24 | G-COM-SC-FF 00EGC ACCEPTED
7 | ALP-EPC-00UCA-HV-GAD-0002 | Control Building - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-29 |  | 2027-04-12 | 2027-04-26 | ALP-EPC-00UCA-CV-ARC-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-00UYA-HV-GAD-0001 | Administration Building - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UYA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-29 |  | 2027-04-12 | 2027-04-26 | ALP-EPC-00UYA-CV-ARC-0001 | G-CON-CWP CWP-11-CV-01 | 2027-03-29 | G-CON-CWP CWP-11-CV-01 IFC G-CON-IWP CWP-11-CV-01 IFC
7 | ALP-EPC-00UGA-CV-RBR-0001 | Water Treatment Building and Basins - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-04-06 |  | 2027-04-20 | 2027-04-27 | ALP-EPC-00UGA-CV-FND-0001 | G-CON-CWP CWP-07-CV-01 | 2027-04-05 | G-CON-CWP CWP-07-CV-01 IFC G-CON-IWP CWP-07-CV-01 IFC
7 | ALP-EPC-00SAA-CM-CMP-0001 | HVAC - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-03-24 | 2027-04-21 | 2027-04-21 | 2027-04-28 | ALP-EPC-00SAA-IC-CNR-0001 | G-COM-SC-FF 00SAA | 2028-07-24 | G-COM-SC-FF 00SAA ACCEPTED
7 | ALP-EPC-00UAC-EL-ELY-0001 | 380 kV GIS Switchyard - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UAC-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-04-01 |  | 2027-04-15 | 2027-04-29 | capacity electrical | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
7 | ALP-EPC-00GBA-IC-HMI-0001 | Seawater Reverse Osmosis - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-03-23 | 2027-04-14 |  | 2027-04-28 | 2027-05-05 | ALP-EPC-00GBA-IC-CNR-0001
7 | ALP-EPC-00UGA-HV-GAD-0001 | Water Treatment Building and Basins - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-02-19 | 2027-04-08 |  | 2027-04-22 | 2027-05-06 | capacity hvac | G-CON-CWP CWP-07-CV-01 | 2027-04-05 | G-CON-CWP CWP-07-CV-01 IFC G-CON-IWP CWP-07-CV-01 IFC
7 | ALP-EPC-00GMA-IC-HMI-0001 | Process Drains and Waste Water Collection - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-16 |  | 2027-04-30 | 2027-05-07 | ALP-EPC-00GMA-IC-CNR-0001
7 | ALP-EPC-00GNA-IC-HMI-0001 | Waste Water Treatment - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-19 |  | 2027-05-03 | 2027-05-10 | ALP-EPC-00GNA-IC-CNR-0001
7 | ALP-EPC-00PGA-CM-CMP-0001 | Closed Cooling Water - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-04-05 | 2027-05-03 | 2027-05-03 | 2027-05-10 | ALP-EPC-00PGA-IC-CNR-0001 | G-COM-SC-FF 00PGA | 2028-07-24 | G-COM-SC-FF 00PGA ACCEPTED
7 | ALP-EPC-00PAA-IC-HMI-0001 | CW Intake, Screens and Outfall - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-20 |  | 2027-05-04 | 2027-05-11 | capacity i_and_c
7 | ALP-EPC-00UBA-SS-STL-0001 | Electrical Building - Structural Drawings | concrete / steel | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-04-08 | 2027-05-06 | 2027-05-06 | 2027-05-13 | capacity structural | G-CON-CWP CWP-03-SS-01 | 2027-05-24 | G-CON-CWP CWP-03-SS-01 IFC G-CON-IWP CWP-03-SS-01 IFC
7 | ALP-EPC-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Structural Drawings | concrete / steel | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-04-08 | 2027-05-06 | 2027-05-06 | 2027-05-13 | capacity structural | G-CON-CWP CWP-07-SS-01 | 2027-06-14 | G-CON-CWP CWP-07-SS-01 IFC G-CON-IWP CWP-07-SS-01 IFC
7 | ALP-EPC-00PBA-IC-HMI-0001 | Electro-Chlorination - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-26 |  | 2027-05-10 | 2027-05-17 | capacity i_and_c
7 | ALP-EPC-00EKA-IC-LOG-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-04-13 | 2027-05-11 | 2027-05-11 | 2027-05-18 | ALP-EPC-00EKA-IC-CNR-0001
7 | ALP-EPC-10UMA-HV-GAD-0002 | Gas Turbine Hall - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-21 |  | 2027-05-05 | 2027-05-19 | capacity hvac | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
7 | ALP-EPC-00EGC-IC-LOG-0001 | LDO Forwarding and Treatment - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-04-15 | 2027-05-13 | 2027-05-13 | 2027-05-20 | ALP-EPC-00EGC-IC-CNR-0001
7 | ALP-EPC-20UMB-HV-GAD-0001 | Steam Turbine Hall - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-19 | 2027-04-22 |  | 2027-05-06 | 2027-05-20 | capacity hvac | G-CON-CWP CWP-02-CV-02 | 2027-04-19 | G-CON-CWP CWP-02-CV-02 IFC G-CON-IWP CWP-02-CV-02 IFC
7 | ALP-EPC-00QCA-IC-HMI-0001 | Chemical Dosing - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-05-03 |  | 2027-05-17 | 2027-05-24 | capacity i_and_c
7 | ALP-EPC-00GBA-CM-CMP-0001 | Seawater Reverse Osmosis - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-23 | 2027-04-20 | 2027-05-18 | 2027-05-18 | 2027-05-25 | ALP-EPC-00GBA-IC-CNR-0001 | G-COM-SC-FF 00GBA | 2028-07-24 | G-COM-SC-FF 00GBA ACCEPTED
7 | ALP-EPC-00GMA-CM-CMP-0001 | Process Drains and Waste Water Collection - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-22 | 2027-05-20 | 2027-05-20 | 2027-05-27 | ALP-EPC-00GMA-IC-CNR-0001 | G-COM-SC-FF 00GMA | 2028-07-24 | G-COM-SC-FF 00GMA ACCEPTED
7 | ALP-EPC-00UQA-CV-RBR-0001 | Utility Building - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-05-06 |  | 2027-05-20 | 2027-05-27 | capacity civil | G-CON-CWP CWP-08-CV-01 | 2027-05-04 | G-CON-CWP CWP-08-CV-01 IFC G-CON-IWP CWP-08-CV-01 IFC
7 | ALP-EPC-00EGA-IC-HMI-0001 | LDO Unloading - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-05-07 |  | 2027-05-21 | 2027-05-28 | ALP-EPC-00EGA-IC-CNR-0001
7 | ALP-EPC-00GNA-CM-CMP-0001 | Waste Water Treatment - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-23 | 2027-05-21 | 2027-05-21 | 2027-05-28 | ALP-EPC-00GNA-IC-CNR-0001 | G-COM-SC-FF 00GNA | 2028-07-24 | G-COM-SC-FF 00GNA ACCEPTED
7 | ALP-EPC-00PAA-CM-CMP-0001 | CW Intake, Screens and Outfall - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-23 | 2027-05-21 | 2027-05-21 | 2027-05-28 | ALP-EPC-00PAA-IC-CNR-0001 | G-COM-SC-FF 00PAA | 2028-07-24 | G-COM-SC-FF 00PAA ACCEPTED
7 | ALP-EPC-00PBA-CM-CMP-0001 | Electro-Chlorination - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-23 | 2027-05-21 | 2027-05-21 | 2027-05-28 | ALP-EPC-00PBA-IC-CNR-0001 | G-COM-SC-FF 00PBA | 2028-07-24 | G-COM-SC-FF 00PBA ACCEPTED
7 | ALP-EPC-00QCA-CM-CMP-0001 | Chemical Dosing - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-23 | 2027-05-21 | 2027-05-21 | 2027-05-28 | ALP-EPC-00QCA-IC-CNR-0001 | G-COM-SC-FF 00QCA | 2028-07-24 | G-COM-SC-FF 00QCA ACCEPTED
7 | ALP-EPC-00QEA-CM-CMP-0001 | Compressed Air - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-03-29 | 2027-04-26 | 2027-05-24 | 2027-05-24 | 2027-05-31 | ALP-EPC-00QEA-IC-CNR-0001 | G-COM-SC-FF 00QEA | 2028-07-24 | G-COM-SC-FF 00QEA ACCEPTED
7 | ALP-EPC-00UQA-HV-GAD-0001 | Utility Building - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-03-29 | 2027-05-05 |  | 2027-05-19 | 2027-06-02 | capacity hvac | G-CON-CWP CWP-08-CV-01 | 2027-05-04 | G-CON-CWP CWP-08-CV-01 IFC G-CON-IWP CWP-08-CV-01 IFC
7 | ALP-EPC-00EGB-IC-HMI-0001 | LDO Storage - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-19 |  | 2027-06-02 | 2027-06-09 | ALP-EPC-00EGB-IC-CNR-0001
7 | ALP-EPC-00UZD-EL-ELY-0001 | Pipe Racks and Pipe Sleepers - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZD-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-13 |  | 2027-05-27 | 2027-06-10 | ALP-EPC-00UZD-CV-FND-0001 | G-CON-CWP CWP-12-EL-01 | 2027-05-17 | G-CON-CWP CWP-12-EL-01 IFC G-CON-IWP CWP-12-EL-01 IFC
7 | ALP-EPC-00EKC-IC-HMI-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-05-24 |  | 2027-06-07 | 2027-06-14 | ALP-EPC-00EKC-IC-CNR-0001
7 | ALP-EPC-00GCA-IC-HMI-0001 | Demineralisation - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GCA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-05-24 |  | 2027-06-07 | 2027-06-14 | ALP-EPC-00GCA-IC-CNR-0001
7 | ALP-EPC-00UEG-CV-RBR-0001 | LDO Tank Farm Structures - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-04-22 | 2027-05-24 |  | 2027-06-07 | 2027-06-14 | ALP-EPC-00UEG-CV-FND-0001 | G-CON-CWP CWP-10-CV-01 | 2027-06-03 | G-CON-CWP CWP-10-CV-01 IFC G-CON-IWP CWP-10-CV-01 IFC
7 | ALP-EPC-00GHA-IC-HMI-0001 | Demineralised Water Storage and Distribution - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-25 |  | 2027-06-08 | 2027-06-15 | ALP-EPC-00GHA-IC-CNR-0001
7 | ALP-EPC-00LBG-IC-HMI-0001 | Auxiliary Steam - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LBG-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-25 |  | 2027-06-08 | 2027-06-15 | ALP-EPC-00LBG-IC-CNR-0001
7 | ALP-EPC-00LDA-IC-HMI-0001 | Condensate Polishing - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-25 |  | 2027-06-08 | 2027-06-15 | ALP-EPC-00LDA-IC-CNR-0001
7 | ALP-EPC-00USA-SS-STL-0001 | Workshop and Warehouse - Structural Drawings | concrete / steel | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00USA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00USA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-03-31 | 2027-05-11 | 2027-06-08 | 2027-06-08 | 2027-06-15 | capacity structural | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
7 | ALP-EPC-00PAB-IC-HMI-0001 | CW Piping - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-26 |  | 2027-06-09 | 2027-06-16 | capacity i_and_c
7 | ALP-EPC-00UCA-SS-STL-0001 | Control Building - Structural Drawings | concrete / steel | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-03-31 | 2027-05-12 | 2027-06-09 | 2027-06-09 | 2027-06-16 | capacity structural | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
7 | ALP-EPC-00EGA-CM-CMP-0001 | LDO Unloading - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-05-13 | 2027-06-10 | 2027-06-10 | 2027-06-17 | ALP-EPC-00EGA-IC-CNR-0001 | G-COM-SC-FF 00EGA | 2028-07-24 | G-COM-SC-FF 00EGA ACCEPTED
7 | ALP-EPC-00PAC-IC-HMI-0001 | CW Pumps - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-27 |  | 2027-06-10 | 2027-06-17 | capacity i_and_c
7 | ALP-EPC-00QHA-CM-CMP-0001 | Auxiliary Boiler - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-05-13 | 2027-06-10 | 2027-06-10 | 2027-06-17 | ALP-EPC-00QHA-IC-CNR-0001 | G-COM-SC-FF 00QHA | 2028-07-24 | G-COM-SC-FF 00QHA ACCEPTED
7 | ALP-EPC-00UZD-CV-RBR-0001 | Pipe Racks and Pipe Sleepers - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZD-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-27 |  | 2027-06-10 | 2027-06-17 | capacity civil | G-CON-CWP CWP-12-CV-02 | 2027-03-22 | G-CON-CWP CWP-12-CV-02 IFC G-CON-IWP CWP-12-CV-02 IFC
7 | ALP-EPC-00UYA-SS-STL-0001 | Administration Building - Structural Drawings | concrete / steel | EPC | structural | STL | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UYA-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UYA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-02 | 2027-05-17 | 2027-06-14 | 2027-06-14 | 2027-06-21 | capacity structural | G-CON-CWP CWP-11-SS-01 | 2027-05-24 | G-CON-CWP CWP-11-SS-01 IFC G-CON-IWP CWP-11-SS-01 IFC
7 | ALP-EPC-00PAH-IC-HMI-0001 | Condenser Tube Cleaning - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-05-04 | 2027-06-01 |  | 2027-06-15 | 2027-06-22 | capacity i_and_c
7 | ALP-EPC-00PGA-IC-LOG-0001 | Closed Cooling Water - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-08 | 2027-05-18 | 2027-06-15 | 2027-06-15 | 2027-06-22 | capacity i_and_c
7 | ALP-EPC-00GMA-IC-LOG-0001 | Process Drains and Waste Water Collection - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-05-20 | 2027-06-17 | 2027-06-17 | 2027-06-24 | ALP-EPC-00GMA-IC-CNR-0001
7 | ALP-EPC-00QEA-IC-HMI-0001 | Compressed Air - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-04-02 | 2027-06-03 |  | 2027-06-17 | 2027-06-24 | capacity i_and_c
7 | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report |  | EPC | piping | M3D | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-05-14 | 2027-06-04 |  | 2027-06-18 | 2027-06-25 | ALP-EPC-00UPC-PI-PPL-0001 | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
7 | ALP-EPC-00EGB-CM-CMP-0001 | LDO Storage - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-25 | 2027-06-22 | 2027-06-22 | 2027-06-29 | ALP-EPC-00EGB-IC-CNR-0001 | G-COM-SC-FF 00EGB | 2028-07-24 | G-COM-SC-FF 00EGB ACCEPTED
7 | ALP-EPC-00PAA-IC-LOG-0001 | CW Intake, Screens and Outfall - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-05-27 | 2027-06-24 | 2027-06-24 | 2027-07-01 | capacity i_and_c
7 | ALP-EPC-00EKC-CM-CMP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-05-28 | 2027-06-25 | 2027-06-25 | 2027-07-02 | ALP-EPC-00EKC-IC-CNR-0001 | G-COM-SC-FF 00EKC | 2028-07-24 | G-COM-SC-FF 00EKC ACCEPTED
7 | ALP-EPC-00GCA-CM-CMP-0001 | Demineralisation - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GCA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-05-28 | 2027-06-25 | 2027-06-25 | 2027-07-02 | ALP-EPC-00GCA-IC-CNR-0001 | G-COM-SC-FF 00GCA | 2028-07-24 | G-COM-SC-FF 00GCA ACCEPTED
7 | ALP-EPC-00GHA-CM-CMP-0001 | Demineralised Water Storage and Distribution - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-31 | 2027-06-28 | 2027-06-28 | 2027-07-05 | ALP-EPC-00GHA-IC-CNR-0001 | G-COM-SC-FF 00GHA | 2028-07-24 | G-COM-SC-FF 00GHA ACCEPTED
7 | ALP-EPC-00LDA-CM-CMP-0001 | Condensate Polishing - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-31 | 2027-06-28 | 2027-06-28 | 2027-07-05 | ALP-EPC-00LDA-IC-CNR-0001 | G-COM-SC-FF 00LDA | 2028-07-24 | G-COM-SC-FF 00LDA ACCEPTED
7 | ALP-EPC-00PAB-CM-CMP-0001 | CW Piping - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-31 | 2027-06-28 | 2027-06-28 | 2027-07-05 | ALP-EPC-00PAB-IC-CNR-0001 | G-COM-SC-FF 00PAB | 2028-07-24 | G-COM-SC-FF 00PAB ACCEPTED
7 | ALP-EPC-00PAB-PI-STR-0001 | CW Piping - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-14 | 2027-06-14 |  | 2027-06-28 | 2027-07-05 | ALP-EPC-00UPC-PI-PPL-0001
7 | ALP-EPC-00PAC-CM-CMP-0001 | CW Pumps - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-31 | 2027-06-28 | 2027-06-28 | 2027-07-05 | ALP-EPC-00PAC-IC-CNR-0001 | G-COM-SC-FF 00PAC | 2028-07-24 | G-COM-SC-FF 00PAC ACCEPTED
7 | ALP-EPC-00PAH-CM-CMP-0001 | Condenser Tube Cleaning - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-04 | 2027-06-01 | 2027-06-29 | 2027-06-29 | 2027-07-06 | ALP-EPC-00PAH-IC-CNR-0001 | G-COM-SC-FF 00PAH | 2028-07-24 | G-COM-SC-FF 00PAH ACCEPTED
7 | ALP-EPC-00000-GE-RPT-0009 | Painting and Insulation - Technical Bid Evaluation | subcontract | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-30 |  | 2027-06-30 | 2027-07-07 | bids MR-ME-022 | G-PRC-PO MR-ME-022 | 2028-01-10 | G-PRC-PO MR-ME-022 IFR
7 | ALP-EPC-00QHA-IC-HMI-0001 | Auxiliary Boiler - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-05-28 | 2027-06-23 |  | 2027-07-07 | 2027-07-14 | capacity i_and_c
7 | ALP-EPC-00EGA-IC-LOG-0001 | LDO Unloading - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-06-10 | 2027-07-08 | 2027-07-08 | 2027-07-15 | ALP-EPC-00EGA-IC-CNR-0001
7 | ALP-EPC-00SAA-IC-HMI-0001 | HVAC - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-06-24 |  | 2027-07-08 | 2027-07-15 | capacity i_and_c
7 | ALP-EPC-00UEK-CV-RBR-0001 | Gas Station Structures - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-25 |  | 2027-07-09 | 2027-07-16 | ALP-EPC-00UEK-CV-FND-0001 | G-CON-CWP CWP-09-CV-01 | 2027-08-04 | G-CON-CWP CWP-09-CV-01 IFC G-CON-IWP CWP-09-CV-01 IFC
7 | ALP-EPC-00EKC-IC-LOG-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-06-14 | 2027-07-12 | 2027-07-12 | 2027-07-19 | ALP-EPC-00EKC-IC-CNR-0001
7 | ALP-EPC-00GKA-IC-HMI-0001 | Potable Water - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-28 |  | 2027-07-12 | 2027-07-19 | ALP-EPC-00GKA-IC-CNR-0001
7 | ALP-EPC-00GUA-IC-HMI-0001 | Sanitary Waste Water Treatment - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-28 |  | 2027-07-12 | 2027-07-19 | ALP-EPC-00GUA-IC-CNR-0001
7 | ALP-EPC-00UEK-IC-ELY-0002 | Gas Station Structures - Fire Detection and Alarm Layouts |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-21 |  | 2027-07-05 | 2027-07-19 | ALP-EPC-00UEK-CV-ARC-0001 | G-CON-CWP CWP-09-IC-01 | 2028-01-24 | G-CON-CWP CWP-09-IC-01 IFC G-CON-IWP CWP-09-IC-01 IFC
7 | ALP-EPC-00LBG-IC-LOG-0001 | Auxiliary Steam - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-06-15 | 2027-07-13 | 2027-07-13 | 2027-07-20 | ALP-EPC-00LBG-IC-CNR-0001
7 | ALP-EPC-00QJA-IC-HMI-0001 | Nitrogen Supply - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-29 |  | 2027-07-13 | 2027-07-20 | capacity i_and_c
7 | ALP-EPC-00UEK-HV-GAD-0001 | Gas Station Structures - Building Services | plumbing, HVAC ducting, fire fighting | EPC | hvac | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HV-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-22 |  | 2027-07-06 | 2027-07-20 | ALP-EPC-00UEK-CV-ARC-0001 | G-CON-CWP CWP-09-CV-01 | 2027-08-04 | G-CON-CWP CWP-09-CV-01 IFC G-CON-IWP CWP-09-CV-01 IFC
7 | ALP-EPC-00QJA-CM-CMP-0001 | Nitrogen Supply - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-19 | 2027-06-16 | 2027-07-14 | 2027-07-14 | 2027-07-21 | ALP-EPC-00QJA-IC-CNR-0001 | G-COM-SC-FF 00QJA | 2028-07-24 | G-COM-SC-FF 00QJA ACCEPTED
7 | ALP-EPC-00QJB-IC-HMI-0001 | Hydrogen and CO2 Supply - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-06-30 |  | 2027-07-14 | 2027-07-21 | capacity i_and_c
7 | ALP-EPC-00UAC-IC-HUP-0001 | 380 kV GIS Switchyard - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-14 | 2027-07-21 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
7 | ALP-EPC-00UZA-IC-HUP-0001 | Site-Wide Infrastructure - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-14 | 2027-07-21 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
7 | ALP-EPC-00UZF-GE-SPC-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Specification | subcontract | EPC | general | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-ME-STU-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-PLN-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZF-CV-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-19 | 2027-06-16 | 2027-07-14 | 2027-07-14 | 2027-07-21 | ALP-EPC-00UZF-CV-RPT-0001 | G-PRC-ENQ MR-ME-024 | 2027-09-20 | G-PRC-ENQ MR-ME-024 IFR G-PRC-PO MR-ME-024 IFC
7 | ALP-EPC-00EGB-IC-LOG-0001 | LDO Storage - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-06-17 | 2027-07-15 | 2027-07-15 | 2027-07-22 | ALP-EPC-00EGB-IC-CNR-0001
7 | ALP-EPC-00QJB-CM-CMP-0001 | Hydrogen and CO2 Supply - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-21 | 2027-06-18 | 2027-07-16 | 2027-07-16 | 2027-07-23 | ALP-EPC-00QJB-IC-CNR-0001 | G-COM-SC-FF 00QJB | 2028-07-24 | G-COM-SC-FF 00QJB ACCEPTED
7 | ALP-EPC-00UBA-IC-HUP-0001 | Electrical Building and Emergency Power - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-16 |  | 2027-07-16 | 2027-07-23 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
7 | ALP-EPC-00UCA-IC-HUP-0001 | Control, Administration and Workshop Buildings - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-16 |  | 2027-07-16 | 2027-07-23 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
7 | ALP-EPC-00UEG-IC-HUP-0001 | LDO Tank Farm and Unloading - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-16 |  | 2027-07-16 | 2027-07-23 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-10-IC-01 | 2028-02-21 | G-CON-CWP CWP-10-IC-01 IFC G-CON-IWP CWP-10-IC-01 IFC
7 | ALP-EPC-00UEK-IC-HUP-0001 | Fuel Gas Station - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-16 |  | 2027-07-16 | 2027-07-23 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-09-IC-01 | 2028-01-24 | G-CON-CWP CWP-09-IC-01 IFC G-CON-IWP CWP-09-IC-01 IFC
7 | ALP-EPC-00UPC-IC-HUP-0001 | CW Pump House and Onshore CW - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-16 |  | 2027-07-16 | 2027-07-23 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-05-IC-01 | 2028-02-28 | G-CON-CWP CWP-05-IC-01 IFC G-CON-IWP CWP-05-IC-01 IFC
7 | ALP-EPC-20UMB-IC-HUP-0001 | Power Block - ST and Condenser - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-16 |  | 2027-07-16 | 2027-07-23 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-02-IC-01 | 2028-03-27 | G-CON-CWP CWP-02-IC-01 IFC G-CON-IWP CWP-02-IC-01 IFC
7 | ALP-EPC-00UEK-HS-GAD-0001 | Gas Station Structures - Fire Fighting, Escape Route and Safety Signage Layouts |  | EPC | hse | GAD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-CV-ARC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-21 | 2027-07-19 | 2027-07-19 | 2027-07-26 | ALP-EPC-00UEK-CV-ARC-0001 | G-CON-CWP CWP-09-CV-01 | 2027-08-04 | G-CON-CWP CWP-09-CV-01 IFC G-CON-IWP CWP-09-CV-01 IFC
7 | ALP-EPC-00UGA-IC-HUP-0001 | Water Treatment and Effluents - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-20 |  | 2027-07-20 | 2027-07-27 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-07-IC-01 | 2028-03-20 | G-CON-CWP CWP-07-IC-01 IFC G-CON-IWP CWP-07-IC-01 IFC
7 | ALP-M22-00000-GE-ITP-0001 | Painting and Insulation - Subcontractor Inspection and Test Plans | subcontract | M22 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-28 | 2027-07-28 | PO MR-ME-022
7 | ALP-M22-00000-GE-MOS-0001 | Painting and Insulation - Subcontractor Method Statements, Part 1 of 6 | subcontract | M22 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-28 | 2027-07-28 | PO MR-ME-022
7 | ALP-M22-00000-GE-MOS-0002 | Painting and Insulation - Subcontractor Method Statements, Part 2 of 6 | subcontract | M22 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-28 | 2027-07-28 | PO MR-ME-022
7 | ALP-M22-00000-GE-MOS-0003 | Painting and Insulation - Subcontractor Method Statements, Part 3 of 6 | subcontract | M22 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-28 | 2027-07-28 | PO MR-ME-022
7 | ALP-M22-00000-GE-MOS-0004 | Painting and Insulation - Subcontractor Method Statements, Part 4 of 6 | subcontract | M22 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-28 | 2027-07-28 | PO MR-ME-022
7 | ALP-M22-00000-GE-MOS-0005 | Painting and Insulation - Subcontractor Method Statements, Part 5 of 6 | subcontract | M22 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-28 | 2027-07-28 | PO MR-ME-022
7 | ALP-M22-00000-GE-MOS-0006 | Painting and Insulation - Subcontractor Method Statements, Part 6 of 6 | subcontract | M22 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-14 |  | 2027-07-28 | 2027-07-28 | PO MR-ME-022
7 | ALP-EPC-00GHA-IC-LOG-0001 | Demineralised Water Storage and Distribution - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-06-24 | 2027-07-22 | 2027-07-22 | 2027-07-29 | ALP-EPC-00GHA-IC-CNR-0001
7 | ALP-EPC-00PAB-IC-LOG-0001 | CW Piping - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-06-25 | 2027-07-23 | 2027-07-23 | 2027-07-30 | capacity i_and_c
7 | ALP-EPC-00QUA-CM-CMP-0001 | Sampling and SWAS - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-05-28 | 2027-06-25 | 2027-07-23 | 2027-07-23 | 2027-07-30 | ALP-EPC-00QUA-IC-CNR-0001 | G-COM-SC-FF 00QUA | 2028-07-24 | G-COM-SC-FF 00QUA ACCEPTED
7 | ALP-EPC-00QUA-IC-HMI-0001 | Sampling and SWAS - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-06-14 | 2027-07-09 |  | 2027-07-23 | 2027-07-30 | capacity i_and_c
7 | ALP-EPC-00EKA-PI-STR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-14 | 2027-07-13 |  | 2027-07-27 | 2027-08-03 | capacity piping
7 | ALP-EPC-00PAC-IC-LOG-0001 | CW Pumps - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-07-01 | 2027-07-29 | 2027-07-29 | 2027-08-05 | capacity i_and_c
7 | ALP-EPC-00QCA-IC-LOG-0001 | Chemical Dosing - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-03-29 | 2027-07-01 | 2027-07-29 | 2027-07-29 | 2027-08-05 | capacity i_and_c
7 | ALP-EPC-00UPA-CV-MOS-0001 | Marine Works Construction Method Statement | intake, outfall, dredging | EPC | civil | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPA-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2027-07-02 | 2027-07-16 |  | 2027-07-30 | 2027-08-06 | ALP-EPC-00UPA-CV-CVL-0001
7 | ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings |  | EPC | civil | FND | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-CV-FND-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UPA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CV-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-26 | 2027-07-02 | 2027-07-30 | 2027-07-30 | 2027-08-06 | ALP-EPC-00UZF-CV-FND-0002 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
7 | ALP-EPC-00GKA-CM-CMP-0001 | Potable Water - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-07-05 | 2027-08-02 | 2027-08-02 | 2027-08-09 | ALP-EPC-00GKA-IC-CNR-0001 | G-COM-SC-FF 00GKA | 2028-07-24 | G-COM-SC-FF 00GKA ACCEPTED
7 | ALP-EPC-00GUA-CM-CMP-0001 | Sanitary Waste Water Treatment - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-07-05 | 2027-08-02 | 2027-08-02 | 2027-08-09 | ALP-EPC-00GUA-IC-CNR-0001 | G-COM-SC-FF 00GUA | 2028-07-24 | G-COM-SC-FF 00GUA ACCEPTED
7 | ALP-EPC-00PAH-IC-LOG-0001 | Condenser Tube Cleaning - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-05-04 | 2027-07-05 | 2027-08-02 | 2027-08-02 | 2027-08-09 | capacity i_and_c
7 | ALP-EPC-00UEG-EL-ELY-0001 | LDO Tank Farm and Unloading - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-07-12 |  | 2027-07-26 | 2027-08-09 | capacity electrical | G-CON-CWP CWP-10-EL-01 | 2028-01-24 | G-CON-CWP CWP-10-EL-01 IFC G-CON-IWP CWP-10-EL-01 IFC
7 | ALP-EPC-10HSB-CM-CMP-0001 | Ammonia Storage and Supply - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-07-05 | 2027-08-02 | 2027-08-02 | 2027-08-09 | ALP-EPC-10HSB-IC-CNR-0001 | G-COM-SC-FF 10HSB | 2028-07-24 | G-COM-SC-FF 10HSB ACCEPTED
7 | ALP-EPC-00UEK-EL-ELY-0003 | Gas Station Structures - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-06-14 | 2027-07-13 |  | 2027-07-27 | 2027-08-10 | capacity electrical | G-CON-CWP CWP-09-EL-01 | 2027-12-27 | G-CON-CWP CWP-09-EL-01 IFC G-CON-IWP CWP-09-EL-01 IFC
7 | ALP-EPC-00UPC-EL-ELY-0001 | CW Pump House and Onshore CW - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-15 | 2027-07-16 |  | 2027-07-30 | 2027-08-13 | capacity electrical | G-CON-CWP CWP-05-EL-01 | 2028-01-31 | G-CON-CWP CWP-05-EL-01 IFC G-CON-IWP CWP-05-EL-01 IFC
7 | ALP-EPC-00EGC-PI-STR-0001 | LDO Forwarding and Treatment - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-07-26 |  | 2027-08-09 | 2027-08-16 | capacity piping
7 | ALP-EPC-00UQA-IC-HUP-0001 | BOP Utilities - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-09 |  | 2027-08-09 | 2027-08-16 | capacity i_and_c | G-CON-CWP CWP-08-IC-01 | 2028-02-21 | G-CON-CWP CWP-08-IC-01 IFC G-CON-IWP CWP-08-IC-01 IFC
7 | ALP-EPC-00EKC-PI-STR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-07-27 |  | 2027-08-10 | 2027-08-17 | capacity piping
7 | ALP-EPC-10UMA-IC-HUP-0001 | Power Block - GT and HRSG - Instrument Hook-Up Drawings |  | EPC | i_and_c | HUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-10 |  | 2027-08-10 | 2027-08-17 | capacity i_and_c | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
7 | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | DCS | EPC | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBY-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-21 |  | 2027-08-04 | 2027-08-18 | ALP-EPC-00000-IC-LST-0001
7 | ALP-EPC-00GKA-IC-LOG-0001 | Potable Water - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-07-16 | 2027-08-13 | 2027-08-13 | 2027-08-20 | ALP-EPC-00GKA-IC-CNR-0001
7 | ALP-EPC-00QJB-IC-LOG-0001 | Hydrogen and CO2 Supply - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-07-19 | 2027-08-16 | 2027-08-16 | 2027-08-23 | capacity i_and_c
7 | ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | IEC 60079-10-1 | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0004 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-14 | 2027-07-20 | 2027-08-17 | 2027-08-17 | 2027-08-24 | capacity hse
7 | ALP-EPC-00UPA-CV-RBR-0001 | CW Intake and Outfall Marine Structures - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPA-CV-CVL-0001 is NONE, IFR needs it at IFR |  | 2027-07-02 | 2027-08-03 |  | 2027-08-17 | 2027-08-24 | ALP-EPC-00UPA-CV-CVL-0001 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
7 | ALP-EPC-10LBA-PI-STR-0001 | Main Steam Piping - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-08-03 |  | 2027-08-17 | 2027-08-24 | capacity piping
7 | ALP-EPC-00UAC-IC-ELY-0002 | 380 kV GIS Switchyard - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-28 |  | 2027-08-11 | 2027-08-25 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
7 | ALP-EPC-00UZA-IC-ELY-0001 | Site-Wide Infrastructure - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-28 |  | 2027-08-11 | 2027-08-25 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
7 | ALP-EPC-10LBB-PI-STR-0001 | Hot Reheat Piping - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR |  | 2027-06-29 | 2027-08-05 |  | 2027-08-19 | 2027-08-26 | capacity piping
7 | ALP-EPC-00UAC-EL-ELY-0003 | GIS Building - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-05-21 | 2027-08-02 |  | 2027-08-16 | 2027-08-30 | capacity electrical | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
7 | ALP-EPC-00UCA-IC-ELY-0001 | Control, Administration and Workshop Buildings - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-02 |  | 2027-08-16 | 2027-08-30 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
7 | ALP-EPC-00UEG-IC-ELY-0001 | LDO Tank Farm and Unloading - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-02 |  | 2027-08-16 | 2027-08-30 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-10-IC-01 | 2028-02-21 | G-CON-CWP CWP-10-IC-01 IFC G-CON-IWP CWP-10-IC-01 IFC
7 | ALP-EPC-00UEK-IC-ELY-0001 | Fuel Gas Station - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-02 |  | 2027-08-16 | 2027-08-30 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-09-IC-01 | 2028-01-24 | G-CON-CWP CWP-09-IC-01 IFC G-CON-IWP CWP-09-IC-01 IFC
7 | ALP-EPC-00UPC-IC-ELY-0001 | CW Pump House and Onshore CW - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-02 |  | 2027-08-16 | 2027-08-30 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-05-IC-01 | 2028-02-28 | G-CON-CWP CWP-05-IC-01 IFC G-CON-IWP CWP-05-IC-01 IFC
7 | ALP-EPC-20UMB-IC-ELY-0001 | Power Block - ST and Condenser - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-02 |  | 2027-08-16 | 2027-08-30 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-02-IC-01 | 2028-03-27 | G-CON-CWP CWP-02-IC-01 IFC G-CON-IWP CWP-02-IC-01 IFC
7 | ALP-EPC-00UBA-IC-ELY-0002 | Electrical Building and Emergency Power - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-PI-LAY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-03 |  | 2027-08-17 | 2027-08-31 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
7 | ALP-EPC-00UGA-IC-ELY-0001 | Water Treatment and Effluents - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-04 |  | 2027-08-18 | 2027-09-01 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-07-IC-01 | 2028-03-20 | G-CON-CWP CWP-07-IC-01 IFC G-CON-IWP CWP-07-IC-01 IFC
7 | ALP-EPC-00000-HS-RPT-0004 | HAZOP Close-Out Report |  | EPC | hse | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0003 is NONE, IFR needs it at IFR |  | 2027-07-20 | 2027-08-12 |  | 2027-08-26 | 2027-09-02 | capacity hse
7 | ALP-EPC-10HAN-PI-STR-0001 | HRSG Blowdown and Drains - Pipe Stress Analysis | EPC tanks and headers | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-08-13 |  | 2027-08-27 | 2027-09-03 | capacity piping
7 | ALP-EPC-10LBC-PI-STR-0001 | Cold Reheat Piping - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-08-13 |  | 2027-08-27 | 2027-09-03 | capacity piping
7 | ALP-EPC-00UPA-EL-ELY-0001 | CW Intake and Outfall Marine Structures - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPA-CV-CVL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-07-02 | 2027-08-09 |  | 2027-08-23 | 2027-09-06 | ALP-EPC-00UPA-CV-CVL-0001 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
7 | ALP-EPC-10LBD-PI-STR-0001 | LP Steam Piping - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-08-17 |  | 2027-08-31 | 2027-09-07 | capacity piping
7 | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | IEC 61511 | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0004 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0005 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0006 is NONE, IFR needs it at IFR |  | 2027-07-07 | 2027-08-04 | 2027-09-01 | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-HS-HAZ-0003
7 | ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-08-18 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00UQA-PI-PPL-0003
7 | ALP-EPC-10UMA-IC-ELY-0001 | Power Block - GT and HRSG - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-11 |  | 2027-08-25 | 2027-09-08 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
7 | ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-08-19 |  | 2027-09-02 | 2027-09-09 | ALP-EPC-00UQA-PI-PPL-0003
7 | ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-08-19 |  | 2027-09-02 | 2027-09-09 | ALP-EPC-00UQA-PI-PPL-0003
7 | ALP-EPC-00SAA-PI-ISO-0001 | HVAC - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-09-02 |  | 2027-09-02 | 2027-09-09 | ALP-EPC-00UBA-PI-PPL-0001 | G-CON-CWP CWP-03-HV-01 | 2027-10-11 | G-COM-MC-FF 00SAA IFC G-CON-CWP CWP-03-HV-01 IFC G-CON-IWP CWP-03-HV-01 IFC G-OPS-AB 00000 AB
7 | ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-08-19 |  | 2027-09-02 | 2027-09-09 | ALP-EPC-00UQA-PI-PPL-0003
7 | ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-08-20 |  | 2027-09-03 | 2027-09-10 | ALP-EPC-00UQA-PI-PPL-0003
7 | ALP-EPC-00UQA-IC-ELY-0001 | BOP Utilities - Instrument Location and I&C Cable Routing |  | EPC | i_and_c | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-08-16 |  | 2027-08-30 | 2027-09-13 | ALP-EPC-00000-IC-LST-0001 | G-CON-CWP CWP-08-IC-01 | 2028-02-21 | G-CON-CWP CWP-08-IC-01 IFC G-CON-IWP CWP-08-IC-01 IFC
7 | ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-08-23 |  | 2027-09-06 | 2027-09-13 | ALP-EPC-00UQA-PI-PPL-0003
7 | ALP-EPC-00UGA-EL-ELY-0001 | Water Treatment and Effluents - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-07-16 | 2027-08-20 |  | 2027-09-03 | 2027-09-17 | capacity electrical | G-CON-CWP CWP-07-EL-01 | 2028-02-21 | G-CON-CWP CWP-07-EL-01 IFC G-CON-IWP CWP-07-EL-01 IFC
7 | ALP-EPC-00000-HS-HAZ-0010 | Major Accident Assessment and QRA | Seveso lower tier | EPC | hse | HAZ | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0004 is NONE, IFR needs it at IFR |  | 2027-07-19 | 2027-08-17 | 2027-09-14 | 2027-09-14 | 2027-09-21 | capacity hse
7 | ALP-EPC-00000-GE-RPT-0010 | Mechanical and Piping Erection - Technical Bid Evaluation | subcontract | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0005 is NONE, IFR needs it at IFR |  | 2027-08-25 | 2027-09-15 |  | 2027-09-15 | 2027-09-22 | bids MR-ME-023 | G-PRC-PO MR-ME-023 | 2027-11-15 | G-PRC-PO MR-ME-023 IFR
7 | ALP-EPC-00UQA-EL-ELY-0003 | Utility Building - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-07-16 | 2027-08-26 |  | 2027-09-09 | 2027-09-23 | capacity electrical | G-CON-CWP CWP-08-EL-01 | 2028-01-10 | G-CON-CWP CWP-08-EL-01 IFC G-CON-IWP CWP-08-EL-01 IFC
7 | ALP-EPC-00UEG-EL-ELY-0003 | LDO Tank Farm Structures - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-07-19 | 2027-08-30 |  | 2027-09-13 | 2027-09-27 | capacity electrical | G-CON-CWP CWP-10-EL-01 | 2028-01-24 | G-CON-CWP CWP-10-EL-01 IFC G-CON-IWP CWP-10-EL-01 IFC
7 | ALP-EPC-20UMB-EL-ELY-0001 | Power Block - ST and Condenser - Electrical Layouts | equipment, trays, earthing, lighting | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-LAY-0001 is NONE, IFR needs it at IFR |  | 2027-07-01 | 2027-08-30 |  | 2027-09-13 | 2027-09-27 | capacity electrical | G-CON-CWP CWP-02-EL-01 | 2028-02-28 | G-CON-CWP CWP-02-EL-01 IFC G-CON-IWP CWP-02-EL-01 IFC
7 | ALP-EPC-00LBG-CM-CMP-0001 | Auxiliary Steam - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LBG-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-07-19 | 2027-08-24 | 2027-09-21 | 2027-09-21 | 2027-09-28 | capacity commissioning | G-COM-SC-WS 00LBG | 2028-09-25 | G-COM-SC-WS 00LBG ACCEPTED
7 | ALP-EPC-10HAN-CM-CMP-0001 | HRSG Blowdown and Drains - System Commissioning Procedure | EPC tanks and headers | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-04 | 2027-09-01 | 2027-09-29 | 2027-09-29 | 2027-10-06 | capacity commissioning | G-COM-SC-WS 10HAN | 2028-09-25 | G-COM-SC-WS 10HAN ACCEPTED
7 | ALP-EPC-10LAB-CM-CMP-0001 | Feedwater Piping - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-04 | 2027-09-01 | 2027-09-29 | 2027-09-29 | 2027-10-06 | capacity commissioning | G-COM-SC-WS 10LAB | 2028-09-25 | G-COM-SC-WS 10LAB ACCEPTED
7 | ALP-EPC-00QJA-IC-LOG-0001 | Nitrogen Supply - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-09-02 | 2027-09-30 | 2027-09-30 | 2027-10-07 | capacity i_and_c
7 | ALP-EPC-10LAC-CM-CMP-0001 | Boiler Feed Pumps - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-06 | 2027-09-03 | 2027-10-01 | 2027-10-01 | 2027-10-08 | capacity commissioning | G-COM-SC-WS 10LAC | 2028-09-25 | G-COM-SC-WS 10LAC ACCEPTED
7 | ALP-EPC-10LAE-CM-CMP-0001 | HP Attemperation Spray Water - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-06 | 2027-09-03 | 2027-10-01 | 2027-10-01 | 2027-10-08 | capacity commissioning | G-COM-SC-WS 10LAE | 2028-09-25 | G-COM-SC-WS 10LAE ACCEPTED
7 | ALP-EPC-10LAF-CM-CMP-0001 | Reheat Attemperation Spray Water - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAF-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-06 | 2027-09-03 | 2027-10-01 | 2027-10-01 | 2027-10-08 | capacity commissioning | G-COM-SC-WS 10LAF | 2028-09-25 | G-COM-SC-WS 10LAF ACCEPTED
7 | ALP-EPC-00UGA-EL-ELY-0003 | Water Treatment Building and Basins - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-08-12 | 2027-09-13 |  | 2027-09-27 | 2027-10-11 | capacity electrical | G-CON-CWP CWP-07-EL-01 | 2028-02-21 | G-CON-CWP CWP-07-EL-01 IFC G-CON-IWP CWP-07-EL-01 IFC
7 | ALP-M23-00000-GE-ITP-0001 | Mechanical and Piping Erection - Subcontractor Inspection and Test Plans | subcontract | M23 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0005 is NONE, IFR needs it at IFR |  | 2027-09-15 | 2027-09-29 |  | 2027-10-13 | 2027-10-13 | PO MR-ME-023
7 | ALP-M23-00000-GE-MOS-0001 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 1 of 6 | subcontract | M23 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0005 is NONE, IFR needs it at IFR |  | 2027-09-15 | 2027-09-29 |  | 2027-10-13 | 2027-10-13 | PO MR-ME-023
7 | ALP-M23-00000-GE-MOS-0002 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 2 of 6 | subcontract | M23 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0005 is NONE, IFR needs it at IFR |  | 2027-09-15 | 2027-09-29 |  | 2027-10-13 | 2027-10-13 | PO MR-ME-023
7 | ALP-M23-00000-GE-MOS-0003 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 3 of 6 | subcontract | M23 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0005 is NONE, IFR needs it at IFR |  | 2027-09-15 | 2027-09-29 |  | 2027-10-13 | 2027-10-13 | PO MR-ME-023
7 | ALP-M23-00000-GE-MOS-0004 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 4 of 6 | subcontract | M23 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0005 is NONE, IFR needs it at IFR |  | 2027-09-15 | 2027-09-29 |  | 2027-10-13 | 2027-10-13 | PO MR-ME-023
7 | ALP-M23-00000-GE-MOS-0005 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 5 of 6 | subcontract | M23 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0005 is NONE, IFR needs it at IFR |  | 2027-09-15 | 2027-09-29 |  | 2027-10-13 | 2027-10-13 | PO MR-ME-023
7 | ALP-M23-00000-GE-MOS-0006 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 6 of 6 | subcontract | M23 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0005 is NONE, IFR needs it at IFR |  | 2027-09-15 | 2027-09-29 |  | 2027-10-13 | 2027-10-13 | PO MR-ME-023
7 | ALP-EPC-00SGA-IC-HMI-0001 | Fire Water System - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-02-23 | 2027-09-23 |  | 2027-10-07 | 2027-10-14 | capacity i_and_c
7 | ALP-EPC-10LBA-CM-CMP-0001 | Main Steam Piping - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-16 | 2027-09-13 | 2027-10-11 | 2027-10-11 | 2027-10-18 | capacity commissioning | G-COM-SC-WS 10LBA | 2028-09-25 | G-COM-SC-WS 10LBA ACCEPTED
7 | ALP-EPC-10LBB-CM-CMP-0001 | Hot Reheat Piping - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-17 | 2027-09-14 | 2027-10-12 | 2027-10-12 | 2027-10-19 | capacity commissioning | G-COM-SC-WS 10LBB | 2028-09-25 | G-COM-SC-WS 10LBB ACCEPTED
7 | ALP-EPC-10LBC-CM-CMP-0001 | Cold Reheat Piping - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-17 | 2027-09-14 | 2027-10-12 | 2027-10-12 | 2027-10-19 | capacity commissioning | G-COM-SC-WS 10LBC | 2028-09-25 | G-COM-SC-WS 10LBC ACCEPTED
7 | ALP-EPC-10LBD-CM-CMP-0001 | LP Steam Piping - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBD-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-09-16 | 2027-10-14 | 2027-10-14 | 2027-10-21 | capacity commissioning | G-COM-SC-WS 10LBD | 2028-09-25 | G-COM-SC-WS 10LBD ACCEPTED
7 | ALP-EPC-20LCA-CM-CMP-0001 | Main Condensate Piping - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-09-16 | 2027-10-14 | 2027-10-14 | 2027-10-21 | capacity commissioning | G-COM-SC-WS 20LCA | 2028-09-25 | G-COM-SC-WS 20LCA ACCEPTED
7 | ALP-EPC-20LCB-CM-CMP-0001 | Condensate Extraction Pumps - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-08-24 | 2027-09-21 | 2027-10-19 | 2027-10-19 | 2027-10-26 | capacity commissioning | G-COM-SC-WS 20LCB | 2028-09-25 | G-COM-SC-WS 20LCB ACCEPTED
7 | ALP-EPC-00000-EL-STU-0006 | Grid Code Compliance and Reactive Capability Study |  | EPC | electrical | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-09-29 |  | 2027-10-13 | 2027-10-27 | capacity electrical
7 | ALP-EPC-00000-EL-SPC-0003 | Revenue Metering and TSO SCADA Interface Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2027-08-27 | 2027-09-24 | 2027-10-22 | 2027-10-22 | 2027-10-29 | capacity electrical
7 | ALP-EPC-00SAA-IC-LOG-0001 | HVAC - Logic Diagrams, Part 1 of 2 |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-09-24 | 2027-10-22 | 2027-10-22 | 2027-10-29 | capacity i_and_c
7 | ALP-EPC-00QUA-IC-LOG-0001 | Sampling and SWAS - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-06-14 | 2027-09-27 | 2027-10-25 | 2027-10-25 | 2027-11-01 | capacity i_and_c
7 | ALP-EPC-20MAN-CM-CMP-0001 | Turbine Bypass Stations and Piping - System Commissioning Procedure |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20MAN-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-CM-PLN-0001 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-29 | 2027-10-27 | 2027-10-27 | 2027-11-03 | capacity commissioning | G-COM-SC-WS 20MAN | 2028-09-25 | G-COM-SC-WS 20MAN ACCEPTED
7 | ALP-EPC-00SGC-IC-HMI-0001 | Deluge, Spray and Foam Systems - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGC-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-09-20 | 2027-10-15 |  | 2027-10-29 | 2027-11-05 | capacity i_and_c
7 | ALP-EPC-10HAN-IC-HMI-0001 | HRSG Blowdown and Drains - Operator Displays | HMI graphics; EPC tanks and headers | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-10-15 |  | 2027-10-29 | 2027-11-05 | capacity i_and_c
7 | ALP-EPC-10HSB-IC-HMI-0001 | Ammonia Storage and Supply - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-10-18 |  | 2027-11-01 | 2027-11-08 | capacity i_and_c
7 | ALP-EPC-10LAB-IC-HMI-0001 | Feedwater Piping - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-10-18 |  | 2027-11-01 | 2027-11-08 | capacity i_and_c
7 | ALP-EPC-10LAC-IC-HMI-0001 | Boiler Feed Pumps - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-10-21 |  | 2027-11-04 | 2027-11-11 | capacity i_and_c
7 | ALP-EPC-00SAA-IC-LOG-0002 | HVAC - Logic Diagrams, Part 2 of 2 |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SAA-HV-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-10-08 | 2027-11-05 | 2027-11-05 | 2027-11-12 | capacity i_and_c
7 | ALP-EPC-10LAE-IC-HMI-0001 | HP Attemperation Spray Water - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-09-08 | 2027-10-22 |  | 2027-11-05 | 2027-11-12 | capacity i_and_c
7 | ALP-EPC-10LAE-PI-STR-0001 | HP Attemperation Spray Water - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-20 | 2027-10-29 |  | 2027-11-12 | 2027-11-19 | capacity piping
7 | ALP-EPC-10LAF-IC-HMI-0001 | Reheat Attemperation Spray Water - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAF-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-10-08 | 2027-10-29 |  | 2027-11-12 | 2027-11-19 | capacity i_and_c
7 | ALP-EPC-10LBA-IC-HMI-0001 | Main Steam Piping - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-10-08 | 2027-10-29 |  | 2027-11-12 | 2027-11-19 | capacity i_and_c
7 | ALP-EPC-10LBB-IC-HMI-0001 | Hot Reheat Piping - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBB-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-10-12 | 2027-11-02 |  | 2027-11-16 | 2027-11-23 | capacity i_and_c
7 | ALP-EPC-10LBC-IC-HMI-0001 | Cold Reheat Piping - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBC-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-10-13 | 2027-11-03 |  | 2027-11-17 | 2027-11-24 | capacity i_and_c
7 | ALP-EPC-10LBD-IC-HMI-0001 | LP Steam Piping - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBD-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-10-18 | 2027-11-08 |  | 2027-11-22 | 2027-11-29 | capacity i_and_c
7 | ALP-EPC-10LAF-PI-STR-0001 | Reheat Attemperation Spray Water - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-07-20 | 2027-11-09 |  | 2027-11-23 | 2027-11-30 | capacity piping
7 | ALP-EPC-00ACA-EL-SLD-0001 | 380 kV GIS Switchyard - Single Line Diagram |  | EPC | electrical | SLD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2027-10-07 | 2027-10-29 | 2027-11-26 | 2027-11-26 | 2027-12-03 | capacity electrical | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
7 | ALP-EPC-20LCA-IC-HMI-0001 | Main Condensate Piping - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCA-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-10-21 | 2027-11-12 |  | 2027-11-26 | 2027-12-03 | capacity i_and_c
7 | ALP-EPC-00BLA-EL-SLD-0001 | Lighting and Small Power - Single Line Diagram |  | EPC | electrical | SLD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2027-10-07 | 2027-11-01 | 2027-11-29 | 2027-11-29 | 2027-12-06 | capacity electrical | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
7 | ALP-EPC-00SGA-IC-LOG-0001 | Fire Water System - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-11-02 | 2027-11-30 | 2027-11-30 | 2027-12-07 | capacity i_and_c
7 | ALP-EPC-20LCB-IC-HMI-0001 | Condensate Extraction Pumps - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-10-26 | 2027-11-16 |  | 2027-11-30 | 2027-12-07 | capacity i_and_c
7 | ALP-EPC-10HAN-IC-LOG-0001 | HRSG Blowdown and Drains - Logic Diagrams | EPC tanks and headers | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-11-08 | 2027-12-06 | 2027-12-06 | 2027-12-13 | capacity i_and_c
7 | ALP-EPC-00BMA-EL-SLD-0001 | Emergency LV Switchgear - Single Line Diagram |  | EPC | electrical | SLD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2027-10-18 | 2027-11-09 | 2027-12-07 | 2027-12-07 | 2027-12-14 | capacity electrical | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
7 | ALP-EPC-10LAE-IC-LOG-0001 | HP Attemperation Spray Water - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-10-06 | 2027-11-09 | 2027-12-07 | 2027-12-07 | 2027-12-14 | capacity i_and_c
7 | ALP-EPC-20MAN-IC-HMI-0001 | Turbine Bypass Stations and Piping - Operator Displays | HMI graphics | EPC | i_and_c | HMI | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20MAN-IC-CNR-0001 is NONE, IFR needs it at IFR |  | 2027-11-01 | 2027-11-23 |  | 2027-12-07 | 2027-12-14 | capacity i_and_c
7 | ALP-EPC-00BRA-EL-SLD-0001 | UPS - Single Line Diagram |  | EPC | electrical | SLD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2027-10-19 | 2027-11-10 | 2027-12-08 | 2027-12-08 | 2027-12-15 | capacity electrical | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
7 | ALP-EPC-10LAF-IC-LOG-0001 | Reheat Attemperation Spray Water - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAF-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-10-08 | 2027-11-10 | 2027-12-08 | 2027-12-08 | 2027-12-15 | capacity i_and_c
7 | ALP-EPC-10LAB-IC-LOG-0001 | Feedwater Piping - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-09-27 | 2027-11-11 | 2027-12-09 | 2027-12-09 | 2027-12-16 | capacity i_and_c
7 | ALP-EPC-10LBA-IC-LOG-0001 | Main Steam Piping - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-10-08 | 2027-11-16 | 2027-12-14 | 2027-12-14 | 2027-12-21 | capacity i_and_c
7 | ALP-EPC-00SGC-IC-LOG-0001 | Deluge, Spray and Foam Systems - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-09-22 | 2027-11-17 | 2027-12-15 | 2027-12-15 | 2027-12-22 | capacity i_and_c
7 | ALP-EPC-10LBB-IC-LOG-0001 | Hot Reheat Piping - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-10-13 | 2027-11-18 | 2027-12-16 | 2027-12-16 | 2027-12-23 | capacity i_and_c
7 | ALP-EPC-10HSB-IC-LOG-0001 | Ammonia Storage and Supply - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-11-19 | 2027-12-17 | 2027-12-17 | 2027-12-24 | capacity i_and_c
7 | ALP-EPC-10LBC-IC-LOG-0001 | Cold Reheat Piping - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-10-15 | 2027-11-19 | 2027-12-17 | 2027-12-17 | 2027-12-24 | capacity i_and_c
7 | ALP-EPC-10LBD-IC-LOG-0001 | LP Steam Piping - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBD-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-10-18 | 2027-11-22 | 2027-12-20 | 2027-12-20 | 2027-12-27 | capacity i_and_c
7 | ALP-EPC-10LAC-IC-LOG-0001 | Boiler Feed Pumps - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-11-25 | 2027-12-23 | 2027-12-23 | 2027-12-30 | capacity i_and_c
7 | ALP-P02-10LBA-ME-MDB-0001 | Alloy Piping P91 / P22 - Manufacturing Record Book and Conformity Certificates | main steam, reheat | P02 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-10-21 | 2027-11-04 |  | 2027-11-04 | 2027-12-30 | PO MR-PI-002 | G-PRC-SHP MR-PI-002 | 2027-11-18 | G-PRC-SHP MR-PI-002 IFR
7 | ALP-EPC-20LCA-IC-LOG-0001 | Main Condensate Piping - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-10-22 | 2027-12-09 | 2028-01-06 | 2028-01-06 | 2028-01-13 | capacity i_and_c
7 | ALP-EPC-20MAN-IC-LOG-0001 | Turbine Bypass Stations and Piping - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-20MAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-11-01 | 2027-12-14 | 2028-01-11 | 2028-01-11 | 2028-01-18 | capacity i_and_c
7 | ALP-EPC-20MAN-PI-STR-0001 | Turbine Bypass Stations and Piping - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-IEC-00000-PI-LST-0001 is NONE, IFR needs it at IFR |  | 2027-11-26 | 2027-12-31 |  | 2028-01-14 | 2028-01-21 | capacity piping
7 | ALP-EPC-20LCB-PI-STR-0001 | Condensate Extraction Pumps - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-12-08 | 2028-01-05 |  | 2028-01-19 | 2028-01-26 | capacity piping
7 | ALP-EPC-20LCA-PI-STR-0001 | Main Condensate Piping - Pipe Stress Analysis |  | EPC | piping | STR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-PI-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-12-07 | 2028-01-06 |  | 2028-01-20 | 2028-01-27 | capacity piping
7 | ALP-EPC-20LCB-IC-LOG-0001 | Condensate Extraction Pumps - Logic Diagrams |  | EPC | i_and_c | LOG | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-10-27 | 2027-12-23 | 2028-01-20 | 2028-01-20 | 2028-01-27 | capacity i_and_c
7 | ALP-EPC-00000-CM-TRP-0001 | Steam Blowing and Chemical Cleaning Report |  | EPC | commissioning | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-09-18 | 2028-09-25 |  | 2028-10-09 | 2028-10-16 | after KD-020 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
7 | ALP-EPC-00000-CM-TRP-0005 | Tests on LDO Report |  | EPC | commissioning | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-CMP-0005 is NONE, IFR needs it at IFR |  | 2029-02-26 | 2029-03-05 |  | 2029-03-19 | 2029-03-26 | after COM-030 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
7 | ALP-EPC-00000-CM-TRP-0006 | Emission Test and Noise Survey Reports |  | EPC | commissioning | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-CMP-0006 is NONE, IFR needs it at IFR |  | 2029-03-26 | 2029-04-03 |  | 2029-04-17 | 2029-04-24 | capacity commissioning | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
8 | ALP-EPC-00000-GE-SPC-0001 | Construction Power Supply - Technical Specification | RMU, temporary distribution | EPC | general | SPC | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-16 |  | G-PRC-ENQ MR-EL-011 | 2026-11-09 | G-PRC-ENQ MR-EL-011 IFR G-PRC-PO MR-EL-011 IFC
8 | ALP-EPC-00BBA-EL-DSH-0001 | MV Switchgear 10.5 kV - Datasheet | 2 items | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-00BFA-EL-DSH-0001 | LV Switchgear 0.4 kV - Datasheet | 8 items | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-00BFT-EL-DSH-0001 | LV Transformers - Datasheet | 6 items | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-00BMA-EL-DSH-0001 | Emergency LV Switchgear - Datasheet | 2 items | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet |  | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BFA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-00BTA-EL-DSH-0001 | Batteries and DC 220 V: Battery - Datasheet |  | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-00XJA-EL-DSH-0001 | Emergency Diesel Generator - Datasheet |  | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-10BBT-EL-DSH-0001 | GT Unit Auxiliary Transformer - Datasheet |  | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-20BBT-EL-DSH-0001 | ST Unit Auxiliary Transformer - Datasheet |  | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
8 | ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification |  | EPC | electrical | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0005 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-EL-001 | 2026-12-15 | G-PRC-ENQ MR-EL-001 IFR G-PRC-PO MR-EL-001 IFC
8 | ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification |  | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CJA-IC-BLK-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-30 | 2026-11-30 | 2026-12-07 |  | G-PRC-ENQ MR-IC-001 | 2026-11-30 | G-PRC-ENQ MR-IC-001 IFR G-PRC-PO MR-IC-001 IFC
8 | ALP-EPC-00BBA-EL-ITP-0001 | MV Switchgear 10.5 kV - Inspection and Test Plan |  | EPC | electrical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-EL-003 | 2027-02-15 | G-PRC-PO MR-EL-003 IFR
8 | ALP-EPC-00BRA-EL-DSH-0002 | UPS: Switchgear - Datasheet |  | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BFA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BRA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14
8 | ALP-EPC-00XJA-EL-ITP-0001 | Emergency Diesel Generator - Inspection and Test Plan |  | EPC | electrical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-EL-006 | 2027-02-15 | G-PRC-PO MR-EL-006 IFR
8 | ALP-EPC-00BFA-EL-ITP-0001 | LV Switchboards and MCCs - Inspection and Test Plan |  | EPC | electrical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-03 | 2026-11-23 | 2026-12-14 | 2026-12-14 | 2026-12-21 | capacity electrical | G-PRC-PO MR-EL-005 | 2027-03-29 | G-PRC-PO MR-EL-005 IFR
8 | ALP-EPC-10BBT-EL-ITP-0001 | Unit Auxiliary Transformers - Inspection and Test Plan |  | EPC | electrical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-05 | 2026-12-02 | 2026-12-23 | 2026-12-23 | 2026-12-30 | capacity electrical | G-PRC-PO MR-EL-002 | 2027-04-05 | G-PRC-PO MR-EL-002 IFR
8 | ALP-EPC-00BFT-EL-ITP-0001 | LV Transformers - Inspection and Test Plan |  | EPC | electrical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-26 | 2026-12-10 | 2026-12-31 | 2026-12-31 | 2027-01-07 | capacity electrical | G-PRC-PO MR-EL-004 | 2027-05-10 | G-PRC-PO MR-EL-004 IFR
8 | ALP-EPC-00BRA-EL-ITP-0001 | UPS, Batteries and DC Systems - Inspection and Test Plan |  | EPC | electrical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-12-02 | 2026-12-16 | 2027-01-06 | 2027-01-06 | 2027-01-13 | capacity electrical | G-PRC-PO MR-EL-007 | 2027-05-10 | G-PRC-PO MR-EL-007 IFR
8 | ALP-EPC-00EGA-GE-RPT-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2027-01-07 |  | 2027-01-07 | 2027-01-14 | bids MR-ME-016 | G-PRC-PO MR-ME-016 | 2027-01-25 | G-PRC-PO MR-ME-016 IFR
8 | ALP-EPC-00EKA-GE-RPT-0001 | Gas Receiving and Metering Station - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2027-01-07 |  | 2027-01-07 | 2027-01-14 | bids MR-ME-015 | G-PRC-PO MR-ME-015 | 2027-01-25 | G-PRC-PO MR-ME-015 IFR
8 | ALP-EPC-00PAC-GE-RPT-0001 | CW Pumps - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2027-01-07 |  | 2027-01-07 | 2027-01-14 | bids MR-ME-003 | G-PRC-PO MR-ME-003 | 2027-02-01 | G-PRC-PO MR-ME-003 IFR
8 | ALP-EPC-00QHA-GE-RPT-0001 | Auxiliary Boiler - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2027-01-07 |  | 2027-01-07 | 2027-01-14 | bids MR-ME-009 | G-PRC-PO MR-ME-009 | 2027-01-25 | G-PRC-PO MR-ME-009 IFR
8 | ALP-EPC-00SMA-GE-RPT-0001 | EOT Cranes - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2027-01-07 |  | 2027-01-07 | 2027-01-14 | bids MR-ME-021 | G-PRC-PO MR-ME-021 | 2027-02-08 | G-PRC-PO MR-ME-021 IFR
8 | ALP-EPC-10LAC-GE-RPT-0001 | Boiler Feed Pumps - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2027-01-07 |  | 2027-01-07 | 2027-01-14 | bids MR-ME-001 | G-PRC-PO MR-ME-001 | 2027-01-25 | G-PRC-PO MR-ME-001 IFR
8 | ALP-EPC-00PAB-GE-RPT-0001 | GRP CW Pipes and Fittings - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0004 is NONE, IFR needs it at IFR |  | 2026-12-10 | 2027-01-13 |  | 2027-01-13 | 2027-01-20 | capacity general | G-PRC-PO MR-PI-004 | 2027-02-22 | G-PRC-PO MR-PI-004 IFR
8 | ALP-EPC-00GBA-GE-RPT-0001 | Water Treatment Package - Technical Bid Evaluation | SWRO, demin, condensate polishing | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-24 | 2027-01-14 |  | 2027-01-14 | 2027-01-21 | bids MR-ME-012 | G-PRC-PO MR-ME-012 | 2027-02-08 | G-PRC-PO MR-ME-012 IFR
8 | ALP-EPC-00GHA-GE-RPT-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-03 | 2027-01-22 |  | 2027-01-22 | 2027-01-29 | capacity general | G-PRC-PO MR-ME-013 | 2027-05-17 | G-PRC-PO MR-ME-013 IFR
8 | ALP-EPC-00GNA-GE-RPT-0001 | Waste Water and Sanitary Treatment Packages - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-01-28 |  | 2027-01-28 | 2027-02-04 | capacity general | G-PRC-PO MR-ME-014 | 2027-05-31 | G-PRC-PO MR-ME-014 IFR
8 | ALP-EPC-00SAA-GE-RPT-0001 | HVAC Plant and Equipment - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-01-28 |  | 2027-01-28 | 2027-02-04 | capacity general | G-PRC-PO MR-HV-001 | 2027-03-15 | G-PRC-PO MR-HV-001 IFR
8 | ALP-EPC-00SGA-GE-RPT-0001 | Fire Pumps and Fire Protection Systems - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-07 | 2027-01-28 |  | 2027-01-28 | 2027-02-04 | capacity general | G-PRC-PO MR-ME-020 | 2027-03-22 | G-PRC-PO MR-ME-020 IFR
8 | ALP-EPC-00PAA-GE-RPT-0001 | Travelling Band Screens and Trash Rakes - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-12 |  | 2027-02-12 | 2027-02-19 | capacity general | G-PRC-PO MR-ME-004 | 2027-04-12 | G-PRC-PO MR-ME-004 IFR
8 | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation |  | EPC | electrical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-STU-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-02-01 |  | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-EL-STU-0001
8 | ALP-EPC-00PBA-GE-RPT-0001 | Electro-Chlorination Package - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-15 |  | 2027-02-15 | 2027-02-22 | capacity general | G-PRC-PO MR-ME-005 | 2027-04-12 | G-PRC-PO MR-ME-005 IFR
8 | ALP-EPC-00XJA-ME-DSH-0001 | Emergency Diesel Generator: Tank - Datasheet |  | EPC | mechanical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-ME-DBR-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-01-25 | 2027-02-15 | 2027-02-15 | 2027-02-22 | ALP-EPC-00000-ME-DBR-0001
8 | ALP-EPC-10HAN-GE-RPT-0001 | HRSG Blowdown and Drain Tanks - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-03 | 2027-02-15 |  | 2027-02-15 | 2027-02-22 | capacity general | G-PRC-PO MR-ME-019 | 2027-05-03 | G-PRC-PO MR-ME-019 IFR
8 | ALP-P04-00PAB-ME-DSH-0001 | GRP CW Pipes and Fittings - Supplier Catalogues and Material Datasheets |  | P04 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-01-20 | 2027-02-03 |  | 2027-02-17 | 2027-02-24 | PO MR-PI-004
8 | ALP-P04-00PAB-ME-ITP-0001 | GRP CW Pipes and Fittings - Supplier Inspection and Test Plan |  | P04 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-01-20 | 2027-02-03 |  | 2027-02-24 | 2027-02-24 | PO MR-PI-004
8 | ALP-EPC-00PGA-GE-RPT-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-18 |  | 2027-02-18 | 2027-02-25 | capacity general | G-PRC-PO MR-ME-007 | 2027-04-05 | G-PRC-PO MR-ME-007 IFR
8 | ALP-EPC-00QEA-GE-RPT-0001 | Air Compressors and Dryers - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-18 |  | 2027-02-18 | 2027-02-25 | capacity general | G-PRC-PO MR-ME-008 | 2027-04-05 | G-PRC-PO MR-ME-008 IFR
8 | ALP-EPC-10HSB-GE-RPT-0001 | Aqueous Ammonia Storage and Forwarding - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-22 |  | 2027-02-22 | 2027-03-01 | capacity general | G-PRC-PO MR-ME-018 | 2027-04-05 | G-PRC-PO MR-ME-018 IFR
8 | ALP-EPC-20LCB-GE-RPT-0001 | Condensate Extraction Pumps - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-22 |  | 2027-02-22 | 2027-03-01 | capacity general | G-PRC-PO MR-ME-002 | 2027-04-12 | G-PRC-PO MR-ME-002 IFR
8 | ALP-M13-00GHA-ME-ITP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Inspection and Test Plan |  | M13 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-10 |  | 2027-03-01 | 2027-03-01 | PO MR-ME-013 | G-PRC-FAB MR-ME-013 | 2027-07-28 | G-PRC-FAB MR-ME-013 ACCEPTED
8 | ALP-M16-00EGA-ME-ITP-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Inspection and Test Plan |  | M16 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-09 |  | 2027-03-02 | 2027-03-05 | PO MR-ME-016 | G-PRC-FAB MR-ME-016 | 2027-05-05 | G-PRC-FAB MR-ME-016 ACCEPTED
8 | ALP-M21-00SMA-ME-ITP-0001 | EOT Cranes - Supplier Inspection and Test Plan |  | M21 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-09 |  | 2027-03-02 | 2027-03-05 | PO MR-ME-021 | G-PRC-FAB MR-ME-021 | 2027-05-19 | G-PRC-FAB MR-ME-021 ACCEPTED
8 | ALP-M13-00GHA-CV-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Foundation Loads and Anchor Bolt Drawings |  | M13 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-29 | 2027-02-19 |  | 2027-03-05 | 2027-03-09 | PO MR-ME-013 | G-PRC-FAB MR-ME-013 | 2027-07-28 | G-PRC-FAB MR-ME-013 ACCEPTED
8 | ALP-M13-00GHA-ME-DSH-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Certified Datasheets and Performance Curves |  | M13 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-27 | 2027-02-10 |  | 2027-02-24 | 2027-03-09 | PO MR-ME-013 | G-PRC-FAB MR-ME-013 | 2027-07-28 | G-PRC-FAB MR-ME-013 ACCEPTED
8 | ALP-H01-00SAA-ME-ITP-0001 | HVAC Plant and Equipment - Supplier Inspection and Test Plan |  | H01 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-18 |  | 2027-03-11 | 2027-03-11 | PO MR-HV-001 | G-PRC-FAB MR-HV-001 | 2027-06-07 | G-PRC-FAB MR-HV-001 ACCEPTED
8 | ALP-M01-10LAC-ME-ITP-0001 | Boiler Feed Pumps - Supplier Inspection and Test Plan |  | M01 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-03-04 | 2027-03-11 | PO MR-ME-001 | G-PRC-FAB MR-ME-001 | 2027-05-17 | G-PRC-FAB MR-ME-001 ACCEPTED
8 | ALP-M03-00PAC-ME-ITP-0001 | CW Pumps - Supplier Inspection and Test Plan |  | M03 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-03-04 | 2027-03-11 | PO MR-ME-003 | G-PRC-FAB MR-ME-003 | 2027-06-03 | G-PRC-FAB MR-ME-003 ACCEPTED
8 | ALP-M09-00QHA-ME-ITP-0001 | Auxiliary Boiler - Supplier Inspection and Test Plan |  | M09 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-03-04 | 2027-03-11 | PO MR-ME-009 | G-PRC-FAB MR-ME-009 | 2027-05-17 | G-PRC-FAB MR-ME-009 ACCEPTED
8 | ALP-M14-00GNA-ME-ITP-0001 | Waste Water and Sanitary Treatment Packages - Supplier Inspection and Test Plan |  | M14 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-18 |  | 2027-03-11 | 2027-03-11 | PO MR-ME-014 | G-PRC-FAB MR-ME-014 | 2027-08-23 | G-PRC-FAB MR-ME-014 ACCEPTED
8 | ALP-M15-00EKA-ME-ITP-0001 | Gas Receiving and Metering Station - Supplier Inspection and Test Plan |  | M15 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-03-04 | 2027-03-11 | PO MR-ME-015 | G-PRC-FAB MR-ME-015 | 2027-05-17 | G-PRC-FAB MR-ME-015 ACCEPTED
8 | ALP-EPC-00000-EL-STU-0002 | Protection Coordination Study and Relay Settings |  | EPC | electrical | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-STU-0001 is NONE, IFR needs it at IFR |  | 2027-01-11 | 2027-02-15 |  | 2027-03-01 | 2027-03-15 | ALP-EPC-00000-EL-STU-0001
8 | ALP-M20-00SGA-ME-ITP-0001 | Fire Pumps and Fire Protection Systems - Supplier Inspection and Test Plan |  | M20 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-05 | 2027-02-19 |  | 2027-03-12 | 2027-03-15 | PO MR-ME-020 | G-PRC-FAB MR-ME-020 | 2027-06-18 | G-PRC-FAB MR-ME-020 ACCEPTED
8 | ALP-M13-00GHA-ME-GAD-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier GA Drawings |  | M13 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-22 | 2027-02-19 |  | 2027-03-05 | 2027-03-18 | PO MR-ME-013 | G-PRC-FAB MR-ME-013 | 2027-07-28 | G-COM-MC-FF 00GHA IFC G-CON-CWP CWP-07-ME-01 IFC G-CON-IWP CWP-07-ME-01 IFC G-PRC-FAB MR-ME-013 ACCEPTED
8 | ALP-M16-00EGA-CV-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Foundation Loads and Anchor Bolt Drawings |  | M16 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-22 |  | 2027-03-08 | 2027-03-18 | PO MR-ME-016 | G-PRC-FAB MR-ME-016 | 2027-05-05 | G-PRC-FAB MR-ME-016 ACCEPTED
8 | ALP-M16-00EGA-ME-DSH-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Certified Datasheets and Performance Curves |  | M16 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-09 |  | 2027-02-23 | 2027-03-18 | PO MR-ME-016 | G-PRC-FAB MR-ME-016 | 2027-05-05 | G-PRC-FAB MR-ME-016 ACCEPTED
8 | ALP-M21-00SMA-CV-CAL-0001 | EOT Cranes - Supplier Foundation Loads and Anchor Bolt Drawings |  | M21 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-22 |  | 2027-03-08 | 2027-03-18 | PO MR-ME-021 | G-PRC-FAB MR-ME-021 | 2027-05-19 | G-PRC-FAB MR-ME-021 ACCEPTED
8 | ALP-M21-00SMA-ME-DSH-0001 | EOT Cranes - Supplier Certified Datasheets and Performance Curves |  | M21 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-09 |  | 2027-02-23 | 2027-03-18 | PO MR-ME-021 | G-PRC-FAB MR-ME-021 | 2027-05-19 | G-PRC-FAB MR-ME-021 ACCEPTED
8 | ALP-H01-00SAA-ME-DSH-0001 | HVAC Plant and Equipment - Supplier Certified Datasheets and Performance Curves |  | H01 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-18 |  | 2027-03-04 | 2027-03-23 | PO MR-HV-001 | G-PRC-FAB MR-HV-001 | 2027-06-07 | G-PRC-FAB MR-HV-001 ACCEPTED
8 | ALP-M14-00GNA-CV-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Foundation Loads and Anchor Bolt Drawings |  | M14 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-01 |  | 2027-03-15 | 2027-03-23 | PO MR-ME-014 | G-PRC-FAB MR-ME-014 | 2027-08-23 | G-PRC-FAB MR-ME-014 ACCEPTED
8 | ALP-M14-00GNA-ME-DSH-0001 | Waste Water and Sanitary Treatment Packages - Supplier Certified Datasheets and Performance Curves |  | M14 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-18 |  | 2027-03-04 | 2027-03-23 | PO MR-ME-014 | G-PRC-FAB MR-ME-014 | 2027-08-23 | G-PRC-FAB MR-ME-014 ACCEPTED
8 | ALP-M19-10HAN-ME-ITP-0001 | HRSG Blowdown and Drain Tanks - Supplier Inspection and Test Plan |  | M19 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-04 |  | 2027-03-23 | 2027-03-23 | PO MR-ME-019 | G-PRC-FAB MR-ME-019 | 2027-07-14 | G-PRC-FAB MR-ME-019 ACCEPTED
8 | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | subcontract | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0002 is NONE, IFR needs it at IFR |  | 2026-12-11 | 2027-03-19 |  | 2027-03-19 | 2027-03-24 | capacity general | G-PRC-ENQ MR-EL-012 | 2027-09-06 | G-PRC-ENQ MR-EL-012 IFR G-PRC-PO MR-EL-012 IFC
8 | ALP-EPC-00PAH-GE-RPT-0001 | Condenser Tube Cleaning System - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-03-17 |  | 2027-03-17 | 2027-03-24 | capacity general | G-PRC-PO MR-ME-006 | 2027-07-05 | G-PRC-PO MR-ME-006 IFR
8 | ALP-M01-10LAC-CV-CAL-0001 | Boiler Feed Pumps - Supplier Foundation Loads and Anchor Bolt Drawings |  | M01 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-25 |  | 2027-03-11 | 2027-03-25 | PO MR-ME-001 | G-PRC-FAB MR-ME-001 | 2027-05-17 | G-PRC-FAB MR-ME-001 ACCEPTED
8 | ALP-M01-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Supplier Certified Datasheets and Performance Curves |  | M01 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-02-25 | 2027-03-25 | PO MR-ME-001 | G-PRC-FAB MR-ME-001 | 2027-05-17 | G-PRC-FAB MR-ME-001 ACCEPTED
8 | ALP-M03-00PAC-CV-CAL-0001 | CW Pumps - Supplier Foundation Loads and Anchor Bolt Drawings |  | M03 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-25 |  | 2027-03-11 | 2027-03-25 | PO MR-ME-003 | G-PRC-FAB MR-ME-003 | 2027-06-03 | G-PRC-FAB MR-ME-003 ACCEPTED
8 | ALP-M03-00PAC-ME-DSH-0001 | CW Pumps - Supplier Certified Datasheets and Performance Curves |  | M03 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-02-25 | 2027-03-25 | PO MR-ME-003 | G-PRC-FAB MR-ME-003 | 2027-06-03 | G-PRC-FAB MR-ME-003 ACCEPTED
8 | ALP-M09-00QHA-CV-CAL-0001 | Auxiliary Boiler - Supplier Foundation Loads and Anchor Bolt Drawings |  | M09 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-25 |  | 2027-03-11 | 2027-03-25 | PO MR-ME-009 | G-PRC-FAB MR-ME-009 | 2027-05-17 | G-PRC-FAB MR-ME-009 ACCEPTED
8 | ALP-M09-00QHA-ME-DSH-0001 | Auxiliary Boiler - Supplier Certified Datasheets and Performance Curves |  | M09 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-02-25 | 2027-03-25 | PO MR-ME-009 | G-PRC-FAB MR-ME-009 | 2027-05-17 | G-PRC-FAB MR-ME-009 ACCEPTED
8 | ALP-M12-00GBA-ME-ITP-0001 | Water Treatment Package - Supplier Inspection and Test Plan | SWRO, demin, condensate polishing | M12 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-11 | 2027-02-25 |  | 2027-03-18 | 2027-03-25 | PO MR-ME-012 | G-PRC-FAB MR-ME-012 | 2027-06-10 | G-PRC-FAB MR-ME-012 ACCEPTED
8 | ALP-M15-00EKA-CV-CAL-0001 | Gas Receiving and Metering Station - Supplier Foundation Loads and Anchor Bolt Drawings |  | M15 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-25 |  | 2027-03-11 | 2027-03-25 | PO MR-ME-015 | G-PRC-FAB MR-ME-015 | 2027-05-17 | G-PRC-FAB MR-ME-015 ACCEPTED
8 | ALP-M15-00EKA-ME-DSH-0001 | Gas Receiving and Metering Station - Supplier Certified Datasheets and Performance Curves |  | M15 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-11 |  | 2027-02-25 | 2027-03-25 | PO MR-ME-015 | G-PRC-FAB MR-ME-015 | 2027-05-17 | G-PRC-FAB MR-ME-015 ACCEPTED
8 | ALP-M20-00SGA-CV-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Foundation Loads and Anchor Bolt Drawings |  | M20 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-10 | 2027-03-03 |  | 2027-03-17 | 2027-03-25 | PO MR-ME-020 | G-PRC-FAB MR-ME-020 | 2027-06-18 | G-PRC-FAB MR-ME-020 ACCEPTED
8 | ALP-M20-00SGA-ME-DSH-0001 | Fire Pumps and Fire Protection Systems - Supplier Certified Datasheets and Performance Curves |  | M20 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-05 | 2027-02-19 |  | 2027-03-05 | 2027-03-25 | PO MR-ME-020 | G-PRC-FAB MR-ME-020 | 2027-06-18 | G-PRC-FAB MR-ME-020 ACCEPTED
8 | ALP-EPC-00CQA-GE-RPT-0001 | Continuous Emission Monitoring System - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-03-19 |  | 2027-03-19 | 2027-03-26 | capacity general | G-PRC-PO MR-IC-002 | 2027-07-12 | G-PRC-PO MR-IC-002 IFR
8 | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition |  | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00SGY-IC-DSH-0001 is NONE, IFR needs it at IFR |  | 2027-03-17 | 2027-03-24 |  | 2027-03-24 | 2027-03-29 | ALP-EPC-00SGY-IC-DSH-0001 | G-PRC-ENQ MR-IC-006 | 2027-05-24 | G-PRC-ENQ MR-IC-006 IFR G-PRC-PO MR-IC-006 IFC
8 | ALP-M13-00GHA-IC-IOL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier I/O List, Control Philosophy and Interface Signals |  | M13 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-01 |  | 2027-03-15 | 2027-03-29 | PO MR-ME-013
8 | ALP-M13-00GHA-ME-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Design Calculations |  | M13 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-01 |  | 2027-03-15 | 2027-03-29 | PO MR-ME-013 | G-PRC-FAB MR-ME-013 | 2027-07-28 | G-PRC-FAB MR-ME-013 ACCEPTED
8 | ALP-M13-00GHA-PR-PID-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier P&IDs |  | M13 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-03-01 |  | 2027-03-29 | 2027-03-29 | PO MR-ME-013 | G-PRC-FAB MR-ME-013 | 2027-07-28 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-013 ACCEPTED
8 | ALP-EPC-00QUA-GE-RPT-0001 | Steam/Water Analysis System - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-03-23 |  | 2027-03-23 | 2027-03-30 | capacity general | G-PRC-PO MR-IC-003 | 2027-07-12 | G-PRC-PO MR-IC-003 IFR
8 | ALP-M16-00EGA-ME-GAD-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier GA Drawings |  | M16 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-22 |  | 2027-03-08 | 2027-03-31 | PO MR-ME-016 | G-PRC-FAB MR-ME-016 | 2027-05-05 | G-COM-MC-FF 00EGA IFC G-CON-CWP CWP-10-ME-01 IFC G-CON-IWP CWP-10-ME-01 IFC G-PRC-FAB MR-ME-016 ACCEPTED
8 | ALP-M19-10HAN-CV-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Foundation Loads and Anchor Bolt Drawings |  | M19 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-15 |  | 2027-03-29 | 2027-03-31 | PO MR-ME-019 | G-PRC-FAB MR-ME-019 | 2027-07-14 | G-PRC-FAB MR-ME-019 ACCEPTED
8 | ALP-M19-10HAN-ME-DSH-0001 | HRSG Blowdown and Drain Tanks - Supplier Certified Datasheets and Performance Curves |  | M19 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-04 |  | 2027-03-18 | 2027-03-31 | PO MR-ME-019 | G-PRC-FAB MR-ME-019 | 2027-07-14 | G-PRC-FAB MR-ME-019 ACCEPTED
8 | ALP-M21-00SMA-ME-GAD-0001 | EOT Cranes - Supplier GA Drawings |  | M21 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-22 |  | 2027-03-08 | 2027-03-31 | PO MR-ME-021 | G-PRC-FAB MR-ME-021 | 2027-05-19 | G-COM-MC-FF 00SMA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC G-PRC-FAB MR-ME-021 ACCEPTED
8 | ALP-EPC-00EGB-GE-RPT-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Bid Evaluation | API 650 | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-25 |  | 2027-03-25 | 2027-04-01 | capacity general | G-PRC-PO MR-ME-017 | 2027-07-26 | G-PRC-PO MR-ME-017 IFR
8 | ALP-H01-00SAA-ME-GAD-0001 | HVAC Plant and Equipment - Supplier GA Drawings |  | H01 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-03-01 |  | 2027-03-15 | 2027-04-01 | PO MR-HV-001 | G-PRC-FAB MR-HV-001 | 2027-06-07 | G-COM-MC-FF 00SAA IFC G-CON-CWP CWP-03-HV-01 IFC G-CON-IWP CWP-03-HV-01 IFC G-PRC-FAB MR-HV-001 ACCEPTED
8 | ALP-M07-00PGA-ME-ITP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Inspection and Test Plan |  | M07 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 |  | 2027-04-01 | 2027-04-01 | PO MR-ME-007 | G-PRC-FAB MR-ME-007 | 2027-06-28 | G-PRC-FAB MR-ME-007 ACCEPTED
8 | ALP-M08-00QEA-ME-ITP-0001 | Air Compressors and Dryers - Supplier Inspection and Test Plan |  | M08 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 |  | 2027-04-01 | 2027-04-01 | PO MR-ME-008 | G-PRC-FAB MR-ME-008 | 2027-06-28 | G-PRC-FAB MR-ME-008 ACCEPTED
8 | ALP-M14-00GNA-ME-GAD-0001 | Waste Water and Sanitary Treatment Packages - Supplier GA Drawings |  | M14 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-03-01 |  | 2027-03-15 | 2027-04-01 | PO MR-ME-014 | G-PRC-FAB MR-ME-014 | 2027-08-23 | G-COM-MC-FF 00GNA IFC G-CON-CWP CWP-07-ME-01 IFC G-CON-IWP CWP-07-ME-01 IFC G-PRC-FAB MR-ME-014 ACCEPTED
8 | ALP-M04-00PAA-ME-ITP-0001 | Travelling Band Screens and Trash Rakes - Supplier Inspection and Test Plan |  | M04 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-03-10 |  | 2027-03-31 | 2027-04-05 | PO MR-ME-004 | G-PRC-FAB MR-ME-004 | 2027-07-21 | G-PRC-FAB MR-ME-004 ACCEPTED
8 | ALP-M18-10HSB-ME-ITP-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Inspection and Test Plan |  | M18 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-03-15 |  | 2027-04-05 | 2027-04-05 | PO MR-ME-018 | G-PRC-FAB MR-ME-018 | 2027-06-28 | G-PRC-FAB MR-ME-018 ACCEPTED
8 | ALP-M05-00PBA-ME-ITP-0001 | Electro-Chlorination Package - Supplier Inspection and Test Plan |  | M05 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 |  | 2027-04-01 | 2027-04-06 | PO MR-ME-005 | G-PRC-FAB MR-ME-005 | 2027-07-21 | G-PRC-FAB MR-ME-005 ACCEPTED
8 | ALP-M20-00SGA-ME-GAD-0001 | Fire Pumps and Fire Protection Systems - Supplier GA Drawings |  | M20 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-03 | 2027-03-03 |  | 2027-03-17 | 2027-04-06 | PO MR-ME-020 | G-PRC-FAB MR-ME-020 | 2027-06-18 | G-COM-MC-FF 00SGA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-PRC-FAB MR-ME-020 ACCEPTED
8 | ALP-M01-10LAC-ME-GAD-0001 | Boiler Feed Pumps - Supplier GA Drawings |  | M01 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-25 |  | 2027-03-11 | 2027-04-08 | PO MR-ME-001 | G-PRC-FAB MR-ME-001 | 2027-05-17 | G-COM-MC-WS 10LAC IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-PRC-FAB MR-ME-001 ACCEPTED
8 | ALP-M03-00PAC-ME-GAD-0001 | CW Pumps - Supplier GA Drawings |  | M03 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-25 |  | 2027-03-11 | 2027-04-08 | PO MR-ME-003 | G-PRC-FAB MR-ME-003 | 2027-06-03 | G-COM-MC-FF 00PAC IFC G-CON-CWP CWP-05-ME-01 IFC G-CON-IWP CWP-05-ME-01 IFC G-PRC-FAB MR-ME-003 ACCEPTED
8 | ALP-M09-00QHA-ME-GAD-0001 | Auxiliary Boiler - Supplier GA Drawings |  | M09 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-25 |  | 2027-03-11 | 2027-04-08 | PO MR-ME-009 | G-PRC-FAB MR-ME-009 | 2027-05-17 | G-COM-MC-FF 00QHA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-PRC-FAB MR-ME-009 ACCEPTED
8 | ALP-M12-00GBA-CV-CAL-0001 | Water Treatment Package - Supplier Foundation Loads and Anchor Bolt Drawings | SWRO, demin, condensate polishing | M12 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-08 | PO MR-ME-012 | G-PRC-FAB MR-ME-012 | 2027-06-10 | G-PRC-FAB MR-ME-012 ACCEPTED
8 | ALP-M12-00GBA-ME-DSH-0001 | Water Treatment Package - Supplier Certified Datasheets and Performance Curves | SWRO, demin, condensate polishing | M12 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-11 | 2027-02-25 |  | 2027-03-11 | 2027-04-08 | PO MR-ME-012 | G-PRC-FAB MR-ME-012 | 2027-06-10 | G-PRC-FAB MR-ME-012 ACCEPTED
8 | ALP-M15-00EKA-ME-GAD-0001 | Gas Receiving and Metering Station - Supplier GA Drawings |  | M15 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-25 |  | 2027-03-11 | 2027-04-08 | PO MR-ME-015 | G-PRC-FAB MR-ME-015 | 2027-05-17 | G-COM-MC-FF 00EKA IFC G-CON-CWP CWP-09-ME-01 IFC G-CON-IWP CWP-09-ME-01 IFC G-PRC-FAB MR-ME-015 ACCEPTED
8 | ALP-M19-10HAN-ME-GAD-0001 | HRSG Blowdown and Drain Tanks - Supplier GA Drawings |  | M19 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-03-15 |  | 2027-03-29 | 2027-04-09 | PO MR-ME-019 | G-PRC-FAB MR-ME-019 | 2027-07-14 | G-COM-MC-WS 10HAN IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC G-PRC-FAB MR-ME-019 ACCEPTED
8 | ALP-H01-00SAA-IC-IOL-0001 | HVAC Plant and Equipment - Supplier I/O List, Control Philosophy and Interface Signals |  | H01 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-12 | PO MR-HV-001
8 | ALP-H01-00SAA-ME-CAL-0001 | HVAC Plant and Equipment - Supplier Design Calculations |  | H01 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-12 | PO MR-HV-001 | G-PRC-FAB MR-HV-001 | 2027-06-07 | G-PRC-FAB MR-HV-001 ACCEPTED
8 | ALP-H01-00SAA-PR-PID-0001 | HVAC Plant and Equipment - Supplier P&IDs |  | H01 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-03-11 |  | 2027-04-12 | 2027-04-12 | PO MR-HV-001 | G-PRC-FAB MR-HV-001 | 2027-06-07 | G-OPS-AB 00000 AB G-PRC-FAB MR-HV-001 ACCEPTED
8 | ALP-M14-00GNA-IC-IOL-0001 | Waste Water and Sanitary Treatment Packages - Supplier I/O List, Control Philosophy and Interface Signals |  | M14 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-12 | PO MR-ME-014
8 | ALP-M14-00GNA-ME-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Design Calculations |  | M14 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-12 | PO MR-ME-014 | G-PRC-FAB MR-ME-014 | 2027-08-23 | G-PRC-FAB MR-ME-014 ACCEPTED
8 | ALP-M14-00GNA-PR-PID-0001 | Waste Water and Sanitary Treatment Packages - Supplier P&IDs |  | M14 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-03-11 |  | 2027-04-12 | 2027-04-12 | PO MR-ME-014 | G-PRC-FAB MR-ME-014 | 2027-08-23 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-014 ACCEPTED
8 | ALP-EPC-00UZA-EL-ELY-0002 | Site-Wide Infrastructure - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZA-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-02-15 | 2027-03-16 |  | 2027-03-30 | 2027-04-13 | ALP-EPC-00UZA-PI-PPL-0001 | G-CON-CWP CWP-12-EL-01 | 2027-05-17 | G-CON-CWP CWP-12-EL-01 IFC G-CON-IWP CWP-12-EL-01 IFC
8 | ALP-M02-20LCB-ME-ITP-0001 | Condensate Extraction Pumps - Supplier Inspection and Test Plan |  | M02 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-18 |  | 2027-04-08 | 2027-04-13 | PO MR-ME-002 | G-PRC-FAB MR-ME-002 | 2027-07-21 | G-PRC-FAB MR-ME-002 ACCEPTED
8 | ALP-M07-00PGA-CV-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Foundation Loads and Anchor Bolt Drawings |  | M07 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-03-22 |  | 2027-04-05 | 2027-04-13 | PO MR-ME-007 | G-PRC-FAB MR-ME-007 | 2027-06-28 | G-PRC-FAB MR-ME-007 ACCEPTED
8 | ALP-M07-00PGA-ME-DSH-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Certified Datasheets and Performance Curves |  | M07 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 |  | 2027-03-25 | 2027-04-13 | PO MR-ME-007 | G-PRC-FAB MR-ME-007 | 2027-06-28 | G-PRC-FAB MR-ME-007 ACCEPTED
8 | ALP-M08-00QEA-CV-CAL-0001 | Air Compressors and Dryers - Supplier Foundation Loads and Anchor Bolt Drawings |  | M08 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-03-22 |  | 2027-04-05 | 2027-04-13 | PO MR-ME-008 | G-PRC-FAB MR-ME-008 | 2027-06-28 | G-PRC-FAB MR-ME-008 ACCEPTED
8 | ALP-M08-00QEA-ME-DSH-0001 | Air Compressors and Dryers - Supplier Certified Datasheets and Performance Curves |  | M08 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 |  | 2027-03-25 | 2027-04-13 | PO MR-ME-008 | G-PRC-FAB MR-ME-008 | 2027-06-28 | G-PRC-FAB MR-ME-008 ACCEPTED
8 | ALP-M16-00EGA-IC-IOL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier I/O List, Control Philosophy and Interface Signals |  | M16 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-05 |  | 2027-03-19 | 2027-04-13 | PO MR-ME-016
8 | ALP-M16-00EGA-ME-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Design Calculations |  | M16 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-05 |  | 2027-03-19 | 2027-04-13 | PO MR-ME-016 | G-PRC-FAB MR-ME-016 | 2027-05-05 | G-PRC-FAB MR-ME-016 ACCEPTED
8 | ALP-M16-00EGA-PR-PID-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier P&IDs |  | M16 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-29 | 2027-03-05 |  | 2027-04-09 | 2027-04-13 | PO MR-ME-016 | G-PRC-FAB MR-ME-016 | 2027-05-05 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-016 ACCEPTED
8 | ALP-M21-00SMA-IC-IOL-0001 | EOT Cranes - Supplier I/O List, Control Philosophy and Interface Signals |  | M21 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-05 |  | 2027-03-19 | 2027-04-13 | PO MR-ME-021
8 | ALP-M21-00SMA-ME-CAL-0001 | EOT Cranes - Supplier Design Calculations |  | M21 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-05 |  | 2027-03-19 | 2027-04-13 | PO MR-ME-021 | G-PRC-FAB MR-ME-021 | 2027-05-19 | G-PRC-FAB MR-ME-021 ACCEPTED
8 | ALP-M13-00GHA-EL-WIR-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Electrical Schematics and Wiring Diagrams |  | M13 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-02-16 | 2027-03-09 |  | 2027-03-23 | 2027-04-15 | PO MR-ME-013 | G-CON-CWP CWP-07-ME-01 | 2027-12-27 | G-COM-MC-FF 00GHA IFC G-CON-CWP CWP-07-ME-01 IFC G-CON-IWP CWP-07-ME-01 IFC
8 | ALP-M13-00GHA-IC-DSH-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Instrument List and Datasheets |  | M13 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-23 | 2027-03-09 |  | 2027-03-23 | 2027-04-15 | PO MR-ME-013
8 | ALP-M18-10HSB-CV-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Foundation Loads and Anchor Bolt Drawings |  | M18 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-03-24 |  | 2027-04-07 | 2027-04-15 | PO MR-ME-018 | G-PRC-FAB MR-ME-018 | 2027-06-28 | G-PRC-FAB MR-ME-018 ACCEPTED
8 | ALP-M18-10HSB-ME-DSH-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Certified Datasheets and Performance Curves |  | M18 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-03-15 |  | 2027-03-29 | 2027-04-15 | PO MR-ME-018 | G-PRC-FAB MR-ME-018 | 2027-06-28 | G-PRC-FAB MR-ME-018 ACCEPTED
8 | ALP-M04-00PAA-CV-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Foundation Loads and Anchor Bolt Drawings |  | M04 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-03-23 |  | 2027-04-06 | 2027-04-16 | PO MR-ME-004 | G-PRC-FAB MR-ME-004 | 2027-07-21 | G-PRC-FAB MR-ME-004 ACCEPTED
8 | ALP-M04-00PAA-ME-DSH-0001 | Travelling Band Screens and Trash Rakes - Supplier Certified Datasheets and Performance Curves |  | M04 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-03-10 |  | 2027-03-24 | 2027-04-16 | PO MR-ME-004 | G-PRC-FAB MR-ME-004 | 2027-07-21 | G-PRC-FAB MR-ME-004 ACCEPTED
8 | ALP-M20-00SGA-IC-IOL-0001 | Fire Pumps and Fire Protection Systems - Supplier I/O List, Control Philosophy and Interface Signals |  | M20 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-15 |  | 2027-03-29 | 2027-04-16 | PO MR-ME-020
8 | ALP-M20-00SGA-ME-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Design Calculations |  | M20 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-15 |  | 2027-03-29 | 2027-04-16 | PO MR-ME-020 | G-PRC-FAB MR-ME-020 | 2027-06-18 | G-PRC-FAB MR-ME-020 ACCEPTED
8 | ALP-M20-00SGA-PR-PID-0001 | Fire Pumps and Fire Protection Systems - Supplier P&IDs |  | M20 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-15 |  | 2027-04-16 | 2027-04-16 | PO MR-ME-020 | G-PRC-FAB MR-ME-020 | 2027-06-18 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-020 ACCEPTED
8 | ALP-M05-00PBA-CV-CAL-0001 | Electro-Chlorination Package - Supplier Foundation Loads and Anchor Bolt Drawings |  | M05 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-03-24 |  | 2027-04-07 | 2027-04-19 | PO MR-ME-005 | G-PRC-FAB MR-ME-005 | 2027-07-21 | G-PRC-FAB MR-ME-005 ACCEPTED
8 | ALP-M05-00PBA-ME-DSH-0001 | Electro-Chlorination Package - Supplier Certified Datasheets and Performance Curves |  | M05 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-11 |  | 2027-03-25 | 2027-04-19 | PO MR-ME-005 | G-PRC-FAB MR-ME-005 | 2027-07-21 | G-PRC-FAB MR-ME-005 ACCEPTED
8 | ALP-M19-10HAN-IC-IOL-0001 | HRSG Blowdown and Drain Tanks - Supplier I/O List, Control Philosophy and Interface Signals |  | M19 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-03-23 |  | 2027-04-06 | 2027-04-20 | PO MR-ME-019
8 | ALP-M19-10HAN-ME-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Design Calculations |  | M19 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-03-23 |  | 2027-04-06 | 2027-04-20 | PO MR-ME-019 | G-PRC-FAB MR-ME-019 | 2027-07-14 | G-PRC-FAB MR-ME-019 ACCEPTED
8 | ALP-M19-10HAN-PR-PID-0001 | HRSG Blowdown and Drain Tanks - Supplier P&IDs |  | M19 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-03-23 |  | 2027-04-20 | 2027-04-20 | PO MR-ME-019 | G-PRC-FAB MR-ME-019 | 2027-07-14 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-019 ACCEPTED
8 | ALP-M01-10LAC-IC-IOL-0001 | Boiler Feed Pumps - Supplier I/O List, Control Philosophy and Interface Signals |  | M01 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-001
8 | ALP-M01-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Supplier Design Calculations |  | M01 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-001 | G-PRC-FAB MR-ME-001 | 2027-05-17 | G-PRC-FAB MR-ME-001 ACCEPTED
8 | ALP-M01-10LAC-PR-PID-0001 | Boiler Feed Pumps - Supplier P&IDs |  | M01 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-03-11 |  | 2027-04-15 | 2027-04-22 | PO MR-ME-001 | G-PRC-FAB MR-ME-001 | 2027-05-17 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-001 ACCEPTED
8 | ALP-M03-00PAC-IC-IOL-0001 | CW Pumps - Supplier I/O List, Control Philosophy and Interface Signals |  | M03 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-003
8 | ALP-M03-00PAC-ME-CAL-0001 | CW Pumps - Supplier Design Calculations |  | M03 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-003 | G-PRC-FAB MR-ME-003 | 2027-06-03 | G-PRC-FAB MR-ME-003 ACCEPTED
8 | ALP-M03-00PAC-PR-PID-0001 | CW Pumps - Supplier P&IDs |  | M03 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-03-11 |  | 2027-04-15 | 2027-04-22 | PO MR-ME-003 | G-PRC-FAB MR-ME-003 | 2027-06-03 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-003 ACCEPTED
8 | ALP-M07-00PGA-ME-GAD-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier GA Drawings |  | M07 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-22 |  | 2027-04-05 | 2027-04-22 | PO MR-ME-007 | G-PRC-FAB MR-ME-007 | 2027-06-28 | G-COM-MC-FF 00PGA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-PRC-FAB MR-ME-007 ACCEPTED
8 | ALP-M08-00QEA-ME-GAD-0001 | Air Compressors and Dryers - Supplier GA Drawings |  | M08 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-22 |  | 2027-04-05 | 2027-04-22 | PO MR-ME-008 | G-PRC-FAB MR-ME-008 | 2027-06-28 | G-COM-MC-FF 00QEA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-PRC-FAB MR-ME-008 ACCEPTED
8 | ALP-M09-00QHA-IC-IOL-0001 | Auxiliary Boiler - Supplier I/O List, Control Philosophy and Interface Signals |  | M09 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-009
8 | ALP-M09-00QHA-ME-CAL-0001 | Auxiliary Boiler - Supplier Design Calculations |  | M09 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-009 | G-PRC-FAB MR-ME-009 | 2027-05-17 | G-PRC-FAB MR-ME-009 ACCEPTED
8 | ALP-M09-00QHA-PR-PID-0001 | Auxiliary Boiler - Supplier P&IDs |  | M09 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-03-11 |  | 2027-04-15 | 2027-04-22 | PO MR-ME-009 | G-PRC-FAB MR-ME-009 | 2027-05-17 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-009 ACCEPTED
8 | ALP-M12-00GBA-ME-GAD-0001 | Water Treatment Package - Supplier GA Drawings | SWRO, demin, condensate polishing | M12 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-11 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-012 | G-PRC-FAB MR-ME-012 | 2027-06-10 | G-COM-MC-FF 00GBA IFC G-CON-CWP CWP-07-ME-01 IFC G-CON-IWP CWP-07-ME-01 IFC G-PRC-FAB MR-ME-012 ACCEPTED
8 | ALP-M15-00EKA-IC-IOL-0001 | Gas Receiving and Metering Station - Supplier I/O List, Control Philosophy and Interface Signals |  | M15 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-015
8 | ALP-M15-00EKA-ME-CAL-0001 | Gas Receiving and Metering Station - Supplier Design Calculations |  | M15 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-11 |  | 2027-03-25 | 2027-04-22 | PO MR-ME-015 | G-PRC-FAB MR-ME-015 | 2027-05-17 | G-PRC-FAB MR-ME-015 ACCEPTED
8 | ALP-M15-00EKA-PR-PID-0001 | Gas Receiving and Metering Station - Supplier P&IDs |  | M15 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-03-11 |  | 2027-04-15 | 2027-04-22 | PO MR-ME-015 | G-PRC-FAB MR-ME-015 | 2027-05-17 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-015 ACCEPTED
8 | ALP-M17-00EGB-GE-ITP-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Inspection and Test Plans | API 650 | M17 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 |  | 2027-04-22 | 2027-04-22 | PO MR-ME-017
8 | ALP-M17-00EGB-GE-MOS-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 1 of 6 | API 650 | M17 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 |  | 2027-04-22 | 2027-04-22 | PO MR-ME-017
8 | ALP-M17-00EGB-GE-MOS-0002 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 2 of 6 | API 650 | M17 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 |  | 2027-04-22 | 2027-04-22 | PO MR-ME-017
8 | ALP-M17-00EGB-GE-MOS-0003 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 3 of 6 | API 650 | M17 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 |  | 2027-04-22 | 2027-04-22 | PO MR-ME-017
8 | ALP-M17-00EGB-GE-MOS-0004 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 4 of 6 | API 650 | M17 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 |  | 2027-04-22 | 2027-04-22 | PO MR-ME-017
8 | ALP-M17-00EGB-GE-MOS-0005 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 5 of 6 | API 650 | M17 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 |  | 2027-04-22 | 2027-04-22 | PO MR-ME-017
8 | ALP-M17-00EGB-GE-MOS-0006 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 6 of 6 | API 650 | M17 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 |  | 2027-04-22 | 2027-04-22 | PO MR-ME-017
8 | ALP-M13-00GHA-ME-LST-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Spare Parts and Special Tools Lists |  | M13 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-18 |  | 2027-04-01 | 2027-04-23 | PO MR-ME-013
8 | ALP-M02-20LCB-CV-CAL-0001 | Condensate Extraction Pumps - Supplier Foundation Loads and Anchor Bolt Drawings |  | M02 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-10 | 2027-03-31 |  | 2027-04-14 | 2027-04-26 | PO MR-ME-002 | G-PRC-FAB MR-ME-002 | 2027-07-21 | G-PRC-FAB MR-ME-002 ACCEPTED
8 | ALP-M02-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Supplier Certified Datasheets and Performance Curves |  | M02 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-18 |  | 2027-04-01 | 2027-04-26 | PO MR-ME-002 | G-PRC-FAB MR-ME-002 | 2027-07-21 | G-PRC-FAB MR-ME-002 ACCEPTED
8 | ALP-M18-10HSB-ME-GAD-0001 | Aqueous Ammonia Storage and Forwarding - Supplier GA Drawings |  | M18 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-03-24 |  | 2027-04-07 | 2027-04-26 | PO MR-ME-018 | G-PRC-FAB MR-ME-018 | 2027-06-28 | G-COM-MC-FF 10HSB IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-PRC-FAB MR-ME-018 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0001 | LV Schematic and Wiring Diagrams, Part 1 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-03-08 | 2027-04-20 |  | 2027-04-20 | 2027-04-27 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-M06-00PAH-ME-ITP-0001 | Condenser Tube Cleaning System - Supplier Inspection and Test Plan |  | M06 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-24 | 2027-04-07 |  | 2027-04-28 | 2027-04-28 | PO MR-ME-006 | G-PRC-FAB MR-ME-006 | 2027-09-27 | G-PRC-FAB MR-ME-006 ACCEPTED
8 | ALP-M04-00PAA-ME-GAD-0001 | Travelling Band Screens and Trash Rakes - Supplier GA Drawings |  | M04 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-23 | 2027-03-23 |  | 2027-04-06 | 2027-04-29 | PO MR-ME-004 | G-PRC-FAB MR-ME-004 | 2027-07-21 | G-COM-MC-FF 00PAA IFC G-CON-CWP CWP-05-ME-01 IFC G-CON-IWP CWP-05-ME-01 IFC G-PRC-FAB MR-ME-004 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0002 | LV Schematic and Wiring Diagrams, Part 10 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-03-09 | 2027-04-23 |  | 2027-04-23 | 2027-04-30 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-I02-00CQA-ME-ITP-0001 | Continuous Emission Monitoring System - Supplier Inspection and Test Plan |  | I02 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-09 |  | 2027-04-30 | 2027-04-30 | PO MR-IC-002 | G-PRC-FAB MR-IC-002 | 2027-10-04 | G-PRC-FAB MR-IC-002 ACCEPTED
8 | ALP-M05-00PBA-ME-GAD-0001 | Electro-Chlorination Package - Supplier GA Drawings |  | M05 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-24 | 2027-03-24 |  | 2027-04-07 | 2027-04-30 | PO MR-ME-005 | G-PRC-FAB MR-ME-005 | 2027-07-21 | G-COM-MC-FF 00PBA IFC G-CON-CWP CWP-05-ME-01 IFC G-CON-IWP CWP-05-ME-01 IFC G-PRC-FAB MR-ME-005 ACCEPTED
8 | ALP-M07-00PGA-IC-IOL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier I/O List, Control Philosophy and Interface Signals |  | M07 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-01 |  | 2027-04-15 | 2027-05-03 | PO MR-ME-007
8 | ALP-M07-00PGA-ME-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Design Calculations |  | M07 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-01 |  | 2027-04-15 | 2027-05-03 | PO MR-ME-007 | G-PRC-FAB MR-ME-007 | 2027-06-28 | G-PRC-FAB MR-ME-007 ACCEPTED
8 | ALP-M07-00PGA-PR-PID-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier P&IDs |  | M07 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-04-01 |  | 2027-05-03 | 2027-05-03 | PO MR-ME-007 | G-PRC-FAB MR-ME-007 | 2027-06-28 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-007 ACCEPTED
8 | ALP-M08-00QEA-IC-IOL-0001 | Air Compressors and Dryers - Supplier I/O List, Control Philosophy and Interface Signals |  | M08 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-01 |  | 2027-04-15 | 2027-05-03 | PO MR-ME-008
8 | ALP-M08-00QEA-ME-CAL-0001 | Air Compressors and Dryers - Supplier Design Calculations |  | M08 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-01 |  | 2027-04-15 | 2027-05-03 | PO MR-ME-008 | G-PRC-FAB MR-ME-008 | 2027-06-28 | G-PRC-FAB MR-ME-008 ACCEPTED
8 | ALP-M08-00QEA-PR-PID-0001 | Air Compressors and Dryers - Supplier P&IDs |  | M08 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-04-01 |  | 2027-05-03 | 2027-05-03 | PO MR-ME-008 | G-PRC-FAB MR-ME-008 | 2027-06-28 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-008 ACCEPTED
8 | ALP-H01-00SAA-EL-WIR-0001 | HVAC Plant and Equipment - Supplier Electrical Schematics and Wiring Diagrams, Part 1 of 2 |  | H01 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-02 | 2027-03-23 |  | 2027-04-06 | 2027-05-04 | PO MR-HV-001 | G-CON-CWP CWP-03-HV-01 | 2027-10-11 | G-COM-MC-FF 00SAA IFC G-CON-CWP CWP-03-HV-01 IFC G-CON-IWP CWP-03-HV-01 IFC
8 | ALP-H01-00SAA-EL-WIR-0002 | HVAC Plant and Equipment - Supplier Electrical Schematics and Wiring Diagrams, Part 2 of 2 |  | H01 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-02 | 2027-03-23 |  | 2027-04-06 | 2027-05-04 | PO MR-HV-001 | G-CON-CWP CWP-03-HV-01 | 2027-10-11 | G-COM-MC-FF 00SAA IFC G-CON-CWP CWP-03-HV-01 IFC G-CON-IWP CWP-03-HV-01 IFC
8 | ALP-H01-00SAA-IC-DSH-0001 | HVAC Plant and Equipment - Supplier Instrument List and Datasheets |  | H01 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-09 | 2027-03-23 |  | 2027-04-06 | 2027-05-04 | PO MR-HV-001
8 | ALP-I03-00QUA-ME-ITP-0001 | Steam/Water Analysis System - Supplier Inspection and Test Plan |  | I03 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-30 | 2027-04-13 |  | 2027-05-04 | 2027-05-04 | PO MR-IC-003 | G-PRC-FAB MR-IC-003 | 2027-10-04 | G-PRC-FAB MR-IC-003 ACCEPTED
8 | ALP-M14-00GNA-EL-WIR-0001 | Waste Water and Sanitary Treatment Packages - Supplier Electrical Schematics and Wiring Diagrams |  | M14 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-02 | 2027-03-23 |  | 2027-04-06 | 2027-05-04 | PO MR-ME-014 | G-CON-CWP CWP-07-ME-01 | 2027-12-27 | G-COM-MC-FF 00GNA IFC G-CON-CWP CWP-07-ME-01 IFC G-CON-IWP CWP-07-ME-01 IFC
8 | ALP-M14-00GNA-IC-DSH-0001 | Waste Water and Sanitary Treatment Packages - Supplier Instrument List and Datasheets |  | M14 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-09 | 2027-03-23 |  | 2027-04-06 | 2027-05-04 | PO MR-ME-014
8 | ALP-M18-10HSB-IC-IOL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier I/O List, Control Philosophy and Interface Signals |  | M18 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-04-05 |  | 2027-04-19 | 2027-05-05 | PO MR-ME-018
8 | ALP-M18-10HSB-ME-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Design Calculations |  | M18 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-04-05 |  | 2027-04-19 | 2027-05-05 | PO MR-ME-018 | G-PRC-FAB MR-ME-018 | 2027-06-28 | G-PRC-FAB MR-ME-018 ACCEPTED
8 | ALP-M18-10HSB-PR-PID-0001 | Aqueous Ammonia Storage and Forwarding - Supplier P&IDs |  | M18 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-04-05 |  | 2027-05-05 | 2027-05-05 | PO MR-ME-018 | G-PRC-FAB MR-ME-018 | 2027-06-28 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-018 ACCEPTED
8 | ALP-EPC-00CJG-GE-RPT-0001 | BOP Safety Instrumented System - Technical Bid Evaluation | IEC 61511 | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-08 | 2027-04-29 |  | 2027-04-29 | 2027-05-06 | bids MR-IC-008 | G-PRC-PO MR-IC-008 | 2027-06-07 | G-PRC-PO MR-IC-008 IFR
8 | ALP-M12-00GBA-IC-IOL-0001 | Water Treatment Package - Supplier I/O List, Control Philosophy and Interface Signals | SWRO, demin, condensate polishing | M12 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-25 |  | 2027-04-08 | 2027-05-06 | PO MR-ME-012
8 | ALP-M12-00GBA-ME-CAL-0001 | Water Treatment Package - Supplier Design Calculations | SWRO, demin, condensate polishing | M12 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-25 |  | 2027-04-08 | 2027-05-06 | PO MR-ME-012 | G-PRC-FAB MR-ME-012 | 2027-06-10 | G-PRC-FAB MR-ME-012 ACCEPTED
8 | ALP-M12-00GBA-PR-PID-0001 | Water Treatment Package - Supplier P&IDs | SWRO, demin, condensate polishing | M12 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-25 |  | 2027-04-29 | 2027-05-06 | PO MR-ME-012 | G-PRC-FAB MR-ME-012 | 2027-06-10 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-012 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0003 | LV Schematic and Wiring Diagrams, Part 11 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-03-18 | 2027-04-30 |  | 2027-04-30 | 2027-05-07 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-M02-20LCB-ME-GAD-0001 | Condensate Extraction Pumps - Supplier GA Drawings |  | M02 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-03 | 2027-03-31 |  | 2027-04-14 | 2027-05-07 | PO MR-ME-002 | G-PRC-FAB MR-ME-002 | 2027-07-21 | G-COM-MC-WS 20LCB IFC G-CON-CWP CWP-02-ME-01 IFC G-CON-IWP CWP-02-ME-01 IFC G-PRC-FAB MR-ME-002 ACCEPTED
8 | ALP-M16-00EGA-EL-WIR-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Electrical Schematics and Wiring Diagrams |  | M16 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-02-25 | 2027-03-18 |  | 2027-04-01 | 2027-05-07 | PO MR-ME-016 | G-CON-CWP CWP-10-ME-01 | 2027-10-04 | G-COM-MC-FF 00EGA IFC G-CON-CWP CWP-10-ME-01 IFC G-CON-IWP CWP-10-ME-01 IFC
8 | ALP-M16-00EGA-IC-DSH-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Instrument List and Datasheets |  | M16 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-18 |  | 2027-04-01 | 2027-05-07 | PO MR-ME-016
8 | ALP-M19-10HAN-EL-WIR-0001 | HRSG Blowdown and Drain Tanks - Supplier Electrical Schematics and Wiring Diagrams |  | M19 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-10 | 2027-03-31 |  | 2027-04-14 | 2027-05-07 | PO MR-ME-019 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-COM-MC-WS 10HAN IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC
8 | ALP-M19-10HAN-IC-DSH-0001 | HRSG Blowdown and Drain Tanks - Supplier Instrument List and Datasheets |  | M19 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-17 | 2027-03-31 |  | 2027-04-14 | 2027-05-07 | PO MR-ME-019
8 | ALP-M21-00SMA-EL-WIR-0001 | EOT Cranes - Supplier Electrical Schematics and Wiring Diagrams |  | M21 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-02-25 | 2027-03-18 |  | 2027-04-01 | 2027-05-07 | PO MR-ME-021 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-COM-MC-FF 00SMA IFC G-CON-CWP CWP-01-ME-01 IFC G-CON-IWP CWP-01-ME-01 IFC
8 | ALP-EPC-00UPC-CV-RBR-0001 | CW Pump House - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-04-19 |  | 2027-05-03 | 2027-05-10 | capacity civil | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
8 | ALP-M06-00PAH-ME-DSH-0001 | Condenser Tube Cleaning System - Supplier Certified Datasheets and Performance Curves |  | M06 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-24 | 2027-04-07 |  | 2027-04-21 | 2027-05-10 | PO MR-ME-006 | G-PRC-FAB MR-ME-006 | 2027-09-27 | G-PRC-FAB MR-ME-006 ACCEPTED
8 | ALP-M20-00SGA-EL-WIR-0001 | Fire Pumps and Fire Protection Systems - Supplier Electrical Schematics and Wiring Diagrams |  | M20 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-04 | 2027-03-25 |  | 2027-04-08 | 2027-05-10 | PO MR-ME-020 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-COM-MC-FF 00SGA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC
8 | ALP-M20-00SGA-IC-DSH-0001 | Fire Pumps and Fire Protection Systems - Supplier Instrument List and Datasheets |  | M20 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-05-10 | PO MR-ME-020
8 | ALP-I02-00CQA-ME-DSH-0001 | Continuous Emission Monitoring System - Supplier Certified Datasheets and Performance Curves |  | I02 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-26 | 2027-04-09 |  | 2027-04-23 | 2027-05-12 | PO MR-IC-002 | G-PRC-FAB MR-IC-002 | 2027-10-04 | G-PRC-FAB MR-IC-002 ACCEPTED
8 | ALP-M04-00PAA-IC-IOL-0001 | Travelling Band Screens and Trash Rakes - Supplier I/O List, Control Philosophy and Interface Signals |  | M04 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-04-05 |  | 2027-04-19 | 2027-05-12 | PO MR-ME-004
8 | ALP-M04-00PAA-ME-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Design Calculations |  | M04 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-04-05 |  | 2027-04-19 | 2027-05-12 | PO MR-ME-004 | G-PRC-FAB MR-ME-004 | 2027-07-21 | G-PRC-FAB MR-ME-004 ACCEPTED
8 | ALP-M04-00PAA-PR-PID-0001 | Travelling Band Screens and Trash Rakes - Supplier P&IDs |  | M04 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-01 | 2027-04-05 |  | 2027-05-10 | 2027-05-12 | PO MR-ME-004 | G-PRC-FAB MR-ME-004 | 2027-07-21 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-004 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0004 | LV Schematic and Wiring Diagrams, Part 12 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-03-22 | 2027-05-06 |  | 2027-05-06 | 2027-05-13 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-H01-00SAA-ME-LST-0001 | HVAC Plant and Equipment - Spare Parts and Special Tools Lists |  | H01 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-01 |  | 2027-04-15 | 2027-05-13 | PO MR-HV-001
8 | ALP-M05-00PBA-IC-IOL-0001 | Electro-Chlorination Package - Supplier I/O List, Control Philosophy and Interface Signals |  | M05 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-16 | 2027-04-06 |  | 2027-04-20 | 2027-05-13 | PO MR-ME-005
8 | ALP-M05-00PBA-ME-CAL-0001 | Electro-Chlorination Package - Supplier Design Calculations |  | M05 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-16 | 2027-04-06 |  | 2027-04-20 | 2027-05-13 | PO MR-ME-005 | G-PRC-FAB MR-ME-005 | 2027-07-21 | G-PRC-FAB MR-ME-005 ACCEPTED
8 | ALP-M05-00PBA-PR-PID-0001 | Electro-Chlorination Package - Supplier P&IDs |  | M05 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-04-06 |  | 2027-05-11 | 2027-05-13 | PO MR-ME-005 | G-PRC-FAB MR-ME-005 | 2027-07-21 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-005 ACCEPTED
8 | ALP-M14-00GNA-ME-LST-0001 | Waste Water and Sanitary Treatment Packages - Spare Parts and Special Tools Lists |  | M14 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-01 |  | 2027-04-15 | 2027-05-13 | PO MR-ME-014
8 | ALP-I03-00QUA-ME-DSH-0001 | Steam/Water Analysis System - Supplier Certified Datasheets and Performance Curves |  | I03 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-30 | 2027-04-13 |  | 2027-04-27 | 2027-05-14 | PO MR-IC-003 | G-PRC-FAB MR-IC-003 | 2027-10-04 | G-PRC-FAB MR-IC-003 ACCEPTED
8 | ALP-M13-00GHA-ME-TST-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Factory Acceptance Test Procedure |  | M13 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-12 | 2027-04-02 |  | 2027-04-30 | 2027-05-14 | PO MR-ME-013 | G-PRC-FAT MR-ME-013 | 2027-06-25 | G-PRC-FAT MR-ME-013 ACCEPTED
8 | ALP-M19-10HAN-ME-LST-0001 | HRSG Blowdown and Drain Tanks - Spare Parts and Special Tools Lists |  | M19 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-19 | 2027-04-09 |  | 2027-04-23 | 2027-05-17 | PO MR-ME-019
8 | ALP-EPC-10UHA-CV-RBR-0001 | HRSG Foundations and Structures - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UHA-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-27 |  | 2027-05-11 | 2027-05-18 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
8 | ALP-EPC-10UMA-CV-RBR-0001 | Gas Turbine Hall - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-CV-FND-0002 is NONE, IFR needs it at IFR |  | 2027-03-12 | 2027-04-27 |  | 2027-05-11 | 2027-05-18 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
8 | ALP-EPC-00QCA-GE-RPT-0001 | Chemical Dosing Skid - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-21 | 2027-05-12 |  | 2027-05-12 | 2027-05-19 | bids MR-ME-011 | G-PRC-PO MR-ME-011 | 2027-05-17 | G-PRC-PO MR-ME-011 IFR
8 | ALP-EPC-20UMB-CV-RBR-0001 | Steam Turbine Hall - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-CV-FND-0002 is NONE, IFR needs it at IFR |  | 2027-03-16 | 2027-04-28 |  | 2027-05-12 | 2027-05-19 | capacity civil | G-CON-CWP CWP-02-CV-02 | 2027-04-19 | G-CON-CWP CWP-02-CV-02 IFC G-CON-IWP CWP-02-CV-02 IFC
8 | ALP-M06-00PAH-ME-GAD-0001 | Condenser Tube Cleaning System - Supplier GA Drawings |  | M06 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-19 | 2027-04-16 |  | 2027-04-30 | 2027-05-19 | PO MR-ME-006 | G-PRC-FAB MR-ME-006 | 2027-09-27 | G-COM-MC-FF 00PAH IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC G-PRC-FAB MR-ME-006 ACCEPTED
8 | ALP-EPC-00CKA-GE-RPT-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-22 | 2027-05-13 |  | 2027-05-13 | 2027-05-20 | bids MR-IC-009 | G-PRC-PO MR-IC-009 | 2027-06-21 | G-PRC-PO MR-IC-009 IFR
8 | ALP-EPC-10UHN-CV-RBR-0001 | Stack Foundation - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UHN-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-04-06 | 2027-04-29 |  | 2027-05-13 | 2027-05-20 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
8 | ALP-M01-10LAC-EL-WIR-0001 | Boiler Feed Pumps - Supplier Electrical Schematics and Wiring Diagrams |  | M01 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-04 | 2027-03-25 |  | 2027-04-08 | 2027-05-20 | PO MR-ME-001 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-COM-MC-WS 10LAC IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC
8 | ALP-M01-10LAC-IC-DSH-0001 | Boiler Feed Pumps - Supplier Instrument List and Datasheets |  | M01 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-05-20 | PO MR-ME-001
8 | ALP-M02-20LCB-IC-IOL-0001 | Condensate Extraction Pumps - Supplier I/O List, Control Philosophy and Interface Signals |  | M02 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-23 | 2027-04-13 |  | 2027-04-27 | 2027-05-20 | PO MR-ME-002
8 | ALP-M02-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Supplier Design Calculations |  | M02 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-23 | 2027-04-13 |  | 2027-04-27 | 2027-05-20 | PO MR-ME-002 | G-PRC-FAB MR-ME-002 | 2027-07-21 | G-PRC-FAB MR-ME-002 ACCEPTED
8 | ALP-M02-20LCB-PR-PID-0001 | Condensate Extraction Pumps - Supplier P&IDs |  | M02 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-09 | 2027-04-13 |  | 2027-05-18 | 2027-05-20 | PO MR-ME-002 | G-PRC-FAB MR-ME-002 | 2027-07-21 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-002 ACCEPTED
8 | ALP-M03-00PAC-EL-WIR-0001 | CW Pumps - Supplier Electrical Schematics and Wiring Diagrams |  | M03 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-04 | 2027-03-25 |  | 2027-04-08 | 2027-05-20 | PO MR-ME-003 | G-CON-CWP CWP-05-ME-01 | 2027-12-20 | G-COM-MC-FF 00PAC IFC G-CON-CWP CWP-05-ME-01 IFC G-CON-IWP CWP-05-ME-01 IFC
8 | ALP-M03-00PAC-IC-DSH-0001 | CW Pumps - Supplier Instrument List and Datasheets |  | M03 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-05-20 | PO MR-ME-003
8 | ALP-M09-00QHA-EL-WIR-0001 | Auxiliary Boiler - Supplier Electrical Schematics and Wiring Diagrams |  | M09 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-04 | 2027-03-25 |  | 2027-04-08 | 2027-05-20 | PO MR-ME-009 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-COM-MC-FF 00QHA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC
8 | ALP-M09-00QHA-IC-DSH-0001 | Auxiliary Boiler - Supplier Instrument List and Datasheets |  | M09 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-05-20 | PO MR-ME-009
8 | ALP-M15-00EKA-EL-WIR-0001 | Gas Receiving and Metering Station - Supplier Electrical Schematics and Wiring Diagrams |  | M15 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-04 | 2027-03-25 |  | 2027-04-08 | 2027-05-20 | PO MR-ME-015 | G-CON-CWP CWP-09-ME-01 | 2027-11-01 | G-COM-MC-FF 00EKA IFC G-CON-CWP CWP-09-ME-01 IFC G-CON-IWP CWP-09-ME-01 IFC
8 | ALP-M15-00EKA-IC-DSH-0001 | Gas Receiving and Metering Station - Supplier Instrument List and Datasheets |  | M15 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-03-25 |  | 2027-04-08 | 2027-05-20 | PO MR-ME-015
8 | ALP-M16-00EGA-ME-LST-0001 | LDO Unloading and Forwarding / Treatment Skids - Spare Parts and Special Tools Lists |  | M16 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-10 | 2027-03-31 |  | 2027-04-14 | 2027-05-20 | PO MR-ME-016
8 | ALP-M20-00SGA-ME-LST-0001 | Fire Pumps and Fire Protection Systems - Spare Parts and Special Tools Lists |  | M20 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-16 | 2027-04-06 |  | 2027-04-20 | 2027-05-20 | PO MR-ME-020
8 | ALP-M21-00SMA-ME-LST-0001 | EOT Cranes - Spare Parts and Special Tools Lists |  | M21 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-10 | 2027-03-31 |  | 2027-04-14 | 2027-05-20 | PO MR-ME-021
8 | ALP-EPC-00UBF-CV-RBR-0001 | Transformer Bays - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBF-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-03-29 | 2027-04-30 |  | 2027-05-14 | 2027-05-21 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
8 | ALP-I02-00CQA-ME-GAD-0001 | Continuous Emission Monitoring System - Supplier GA Drawings |  | I02 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-23 | 2027-04-20 |  | 2027-05-04 | 2027-05-21 | PO MR-IC-002 | G-PRC-FAB MR-IC-002 | 2027-10-04 | G-COM-MC-FF 00CQA IFC G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC G-PRC-FAB MR-IC-002 ACCEPTED
8 | ALP-EPC-00EKA-CM-OMM-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-03-16 | 2027-04-27 |  | 2027-05-11 | 2027-05-25 | ALP-EPC-00EKA-CM-CMP-0001 | G-COM-SC-FF 00EKA | 2028-07-24 | G-COM-SC-FF 00EKA IFR G-OPS-HO-FF 00EKA IFC
8 | ALP-EPC-00QJA-GE-RPT-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-18 |  | 2027-05-18 | 2027-05-25 | bids MR-ME-010 | G-PRC-PO MR-ME-010 | 2027-06-28 | G-PRC-PO MR-ME-010 IFR
8 | ALP-I03-00QUA-ME-GAD-0001 | Steam/Water Analysis System - Supplier GA Drawings |  | I03 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-22 |  | 2027-05-06 | 2027-05-25 | PO MR-IC-003 | G-PRC-FAB MR-IC-003 | 2027-10-04 | G-COM-MC-FF 00QUA IFC G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC G-PRC-FAB MR-IC-003 ACCEPTED
8 | ALP-M07-00PGA-EL-WIR-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Electrical Schematics and Wiring Diagrams |  | M07 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-23 | 2027-04-13 |  | 2027-04-27 | 2027-05-25 | PO MR-ME-007 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-COM-MC-FF 00PGA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC
8 | ALP-M07-00PGA-IC-DSH-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Instrument List and Datasheets |  | M07 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-30 | 2027-04-13 |  | 2027-04-27 | 2027-05-25 | PO MR-ME-007
8 | ALP-M08-00QEA-EL-WIR-0001 | Air Compressors and Dryers - Supplier Electrical Schematics and Wiring Diagrams |  | M08 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-23 | 2027-04-13 |  | 2027-04-27 | 2027-05-25 | PO MR-ME-008 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-COM-MC-FF 00QEA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC
8 | ALP-M08-00QEA-IC-DSH-0001 | Air Compressors and Dryers - Supplier Instrument List and Datasheets |  | M08 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-30 | 2027-04-13 |  | 2027-04-27 | 2027-05-25 | PO MR-ME-008
8 | ALP-EPC-00EGC-CM-OMM-0001 | LDO Forwarding and Treatment - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-29 |  | 2027-05-13 | 2027-05-27 | ALP-EPC-00EGC-CM-CMP-0001 | G-COM-SC-FF 00EGC | 2028-07-24 | G-COM-SC-FF 00EGC IFR G-OPS-HO-FF 00EGC IFC
8 | ALP-M18-10HSB-EL-WIR-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Electrical Schematics and Wiring Diagrams |  | M18 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-25 | 2027-04-15 |  | 2027-04-29 | 2027-05-27 | PO MR-ME-018 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-COM-MC-FF 10HSB IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC
8 | ALP-M18-10HSB-IC-DSH-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Instrument List and Datasheets |  | M18 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-01 | 2027-04-15 |  | 2027-04-29 | 2027-05-27 | PO MR-ME-018
8 | ALP-M06-00PAH-IC-IOL-0001 | Condenser Tube Cleaning System - Supplier I/O List, Control Philosophy and Interface Signals |  | M06 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-07 | 2027-04-28 |  | 2027-05-12 | 2027-05-28 | PO MR-ME-006
8 | ALP-M06-00PAH-ME-CAL-0001 | Condenser Tube Cleaning System - Supplier Design Calculations |  | M06 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-07 | 2027-04-28 |  | 2027-05-12 | 2027-05-28 | PO MR-ME-006 | G-PRC-FAB MR-ME-006 | 2027-09-27 | G-PRC-FAB MR-ME-006 ACCEPTED
8 | ALP-M06-00PAH-PR-PID-0001 | Condenser Tube Cleaning System - Supplier P&IDs |  | M06 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-24 | 2027-04-28 |  | 2027-05-28 | 2027-05-28 | PO MR-ME-006 | G-PRC-FAB MR-ME-006 | 2027-09-27 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-006 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0005 | LV Schematic and Wiring Diagrams, Part 13 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-03-31 | 2027-05-24 |  | 2027-05-24 | 2027-05-31 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-EPC-00CYA-GE-RPT-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-24 |  | 2027-05-24 | 2027-05-31 | bids MR-IC-007 | G-PRC-PO MR-IC-007 | 2027-07-19 | G-PRC-PO MR-IC-007 IFR
8 | ALP-I02-00CQA-IC-IOL-0001 | Continuous Emission Monitoring System - Supplier I/O List, Control Philosophy and Interface Signals |  | I02 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-04-30 |  | 2027-05-14 | 2027-06-01 | PO MR-IC-002
8 | ALP-I02-00CQA-ME-CAL-0001 | Continuous Emission Monitoring System - Supplier Design Calculations |  | I02 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-04-30 |  | 2027-05-14 | 2027-06-01 | PO MR-IC-002 | G-PRC-FAB MR-IC-002 | 2027-10-04 | G-PRC-FAB MR-IC-002 ACCEPTED
8 | ALP-I03-00QUA-IC-IOL-0001 | Steam/Water Analysis System - Supplier I/O List, Control Philosophy and Interface Signals |  | I03 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-13 | 2027-05-04 |  | 2027-05-18 | 2027-06-03 | PO MR-IC-003
8 | ALP-I03-00QUA-ME-CAL-0001 | Steam/Water Analysis System - Supplier Design Calculations |  | I03 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-13 | 2027-05-04 |  | 2027-05-18 | 2027-06-03 | PO MR-IC-003 | G-PRC-FAB MR-IC-003 | 2027-10-04 | G-PRC-FAB MR-IC-003 ACCEPTED
8 | ALP-I03-00QUA-PR-PID-0001 | Steam/Water Analysis System - Supplier P&IDs |  | I03 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-30 | 2027-05-04 |  | 2027-06-03 | 2027-06-03 | PO MR-IC-003 | G-PRC-FAB MR-IC-003 | 2027-10-04 | G-OPS-AB 00000 AB G-PRC-FAB MR-IC-003 ACCEPTED
8 | ALP-M01-10LAC-ME-LST-0001 | Boiler Feed Pumps - Spare Parts and Special Tools Lists |  | M01 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-08 |  | 2027-04-22 | 2027-06-03 | PO MR-ME-001
8 | ALP-M03-00PAC-ME-LST-0001 | CW Pumps - Spare Parts and Special Tools Lists |  | M03 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-08 |  | 2027-04-22 | 2027-06-03 | PO MR-ME-003
8 | ALP-M07-00PGA-ME-LST-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Spare Parts and Special Tools Lists |  | M07 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-01 | 2027-04-22 |  | 2027-05-06 | 2027-06-03 | PO MR-ME-007
8 | ALP-M08-00QEA-ME-LST-0001 | Air Compressors and Dryers - Spare Parts and Special Tools Lists |  | M08 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-01 | 2027-04-22 |  | 2027-05-06 | 2027-06-03 | PO MR-ME-008
8 | ALP-M09-00QHA-ME-LST-0001 | Auxiliary Boiler - Spare Parts and Special Tools Lists |  | M09 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-08 |  | 2027-04-22 | 2027-06-03 | PO MR-ME-009
8 | ALP-M12-00GBA-EL-WIR-0001 | Water Treatment Package - Supplier Electrical Schematics and Wiring Diagrams | SWRO, demin, condensate polishing | M12 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-18 | 2027-04-08 |  | 2027-04-22 | 2027-06-03 | PO MR-ME-012 | G-CON-CWP CWP-07-ME-01 | 2027-12-27 | G-COM-MC-FF 00GBA IFC G-CON-CWP CWP-07-ME-01 IFC G-CON-IWP CWP-07-ME-01 IFC
8 | ALP-M12-00GBA-IC-DSH-0001 | Water Treatment Package - Supplier Instrument List and Datasheets | SWRO, demin, condensate polishing | M12 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-08 |  | 2027-04-22 | 2027-06-03 | PO MR-ME-012
8 | ALP-M15-00EKA-ME-LST-0001 | Gas Receiving and Metering Station - Spare Parts and Special Tools Lists |  | M15 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-08 |  | 2027-04-22 | 2027-06-03 | PO MR-ME-015
8 | ALP-I08-00CJG-ME-ITP-0001 | BOP Safety Instrumented System - Supplier Inspection and Test Plan | IEC 61511 | I08 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-04 | 2027-05-18 |  | 2027-06-04 | 2027-06-04 | PO MR-IC-008 | G-PRC-FAB MR-IC-008 | 2027-08-18 | G-PRC-FAB MR-IC-008 ACCEPTED
8 | ALP-M04-00PAA-EL-WIR-0001 | Travelling Band Screens and Trash Rakes - Supplier Electrical Schematics and Wiring Diagrams |  | M04 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-26 | 2027-04-16 |  | 2027-04-30 | 2027-06-07 | PO MR-ME-004 | G-CON-CWP CWP-05-ME-01 | 2027-12-20 | G-COM-MC-FF 00PAA IFC G-CON-CWP CWP-05-ME-01 IFC G-CON-IWP CWP-05-ME-01 IFC
8 | ALP-M04-00PAA-IC-DSH-0001 | Travelling Band Screens and Trash Rakes - Supplier Instrument List and Datasheets |  | M04 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-02 | 2027-04-16 |  | 2027-04-30 | 2027-06-07 | PO MR-ME-004
8 | ALP-M18-10HSB-ME-LST-0001 | Aqueous Ammonia Storage and Forwarding - Spare Parts and Special Tools Lists |  | M18 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-04-26 |  | 2027-05-10 | 2027-06-07 | PO MR-ME-018
8 | ALP-M19-10HAN-ME-TST-0001 | HRSG Blowdown and Drain Tanks - Factory Acceptance Test Procedure |  | M19 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-04-26 |  | 2027-05-24 | 2027-06-07 | PO MR-ME-019 | G-PRC-FAT MR-ME-019 | 2027-07-19 | G-PRC-FAT MR-ME-019 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0006 | LV Schematic and Wiring Diagrams, Part 2 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-04-19 | 2027-06-01 |  | 2027-06-01 | 2027-06-08 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-M05-00PBA-EL-WIR-0001 | Electro-Chlorination Package - Supplier Electrical Schematics and Wiring Diagrams |  | M05 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-29 | 2027-04-19 |  | 2027-05-03 | 2027-06-08 | PO MR-ME-005 | G-CON-CWP CWP-05-ME-01 | 2027-12-20 | G-COM-MC-FF 00PBA IFC G-CON-CWP CWP-05-ME-01 IFC G-CON-IWP CWP-05-ME-01 IFC
8 | ALP-M05-00PBA-IC-DSH-0001 | Electro-Chlorination Package - Supplier Instrument List and Datasheets |  | M05 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-04-19 |  | 2027-05-03 | 2027-06-08 | PO MR-ME-005
8 | ALP-M13-00GHA-ME-PRC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Installation and Erection Manual |  | M13 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-04-30 |  | 2027-05-14 | 2027-06-11 | PO MR-ME-013 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-07-ME-01 IFR G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-EPC-00BFA-EL-WIR-0007 | LV Schematic and Wiring Diagrams, Part 3 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-04-23 | 2027-06-07 |  | 2027-06-07 | 2027-06-14 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-I08-00CJG-ME-DSH-0001 | BOP Safety Instrumented System - Supplier Certified Datasheets and Performance Curves | IEC 61511 | I08 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-04 | 2027-05-18 |  | 2027-06-01 | 2027-06-14 | PO MR-IC-008 | G-PRC-FAB MR-IC-008 | 2027-08-18 | G-PRC-FAB MR-IC-008 ACCEPTED
8 | ALP-M02-20LCB-EL-WIR-0001 | Condensate Extraction Pumps - Supplier Electrical Schematics and Wiring Diagrams |  | M02 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-04-05 | 2027-04-26 |  | 2027-05-10 | 2027-06-15 | PO MR-ME-002 | G-CON-CWP CWP-02-ME-01 | 2027-12-20 | G-COM-MC-WS 20LCB IFC G-CON-CWP CWP-02-ME-01 IFC G-CON-IWP CWP-02-ME-01 IFC
8 | ALP-M02-20LCB-IC-DSH-0001 | Condensate Extraction Pumps - Supplier Instrument List and Datasheets |  | M02 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-12 | 2027-04-26 |  | 2027-05-10 | 2027-06-15 | PO MR-ME-002
8 | ALP-M10-00QJA-ME-ITP-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Inspection and Test Plan |  | M10 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-01 |  | 2027-06-15 | 2027-06-15 | PO MR-ME-010 | G-PRC-FAB MR-ME-010 | 2027-08-23 | G-PRC-FAB MR-ME-010 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0008 | LV Schematic and Wiring Diagrams, Part 4 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-04-26 | 2027-06-09 |  | 2027-06-09 | 2027-06-16 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-H01-00SAA-ME-TST-0001 | HVAC Plant and Equipment - Factory Acceptance Test Procedure |  | H01 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-05-06 |  | 2027-06-03 | 2027-06-17 | PO MR-HV-001 | G-PRC-FAT MR-HV-001 | 2027-07-29 | G-PRC-FAT MR-HV-001 ACCEPTED
8 | ALP-M11-00QCA-ME-ITP-0001 | Chemical Dosing Skid - Supplier Inspection and Test Plan |  | M11 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-05-31 |  | 2027-06-17 | 2027-06-17 | PO MR-ME-011 | G-PRC-FAB MR-ME-011 | 2027-07-28 | G-PRC-FAB MR-ME-011 ACCEPTED
8 | ALP-M12-00GBA-ME-LST-0001 | Water Treatment Package - Spare Parts and Special Tools Lists | SWRO, demin, condensate polishing | M12 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-01 | 2027-04-22 |  | 2027-05-06 | 2027-06-17 | PO MR-ME-012
8 | ALP-M14-00GNA-ME-TST-0001 | Waste Water and Sanitary Treatment Packages - Factory Acceptance Test Procedure |  | M14 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-05-06 |  | 2027-06-03 | 2027-06-17 | PO MR-ME-014 | G-PRC-FAT MR-ME-014 | 2027-07-29 | G-PRC-FAT MR-ME-014 ACCEPTED
8 | ALP-EPC-10UHN-CV-EFD-0001 | Stack Foundation - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UHN-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-S02-10HNE-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-03-17 | 2027-05-14 | 2027-06-11 | 2027-06-11 | 2027-06-18 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
8 | ALP-M04-00PAA-ME-LST-0001 | Travelling Band Screens and Trash Rakes - Spare Parts and Special Tools Lists |  | M04 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-08 | 2027-04-29 |  | 2027-05-13 | 2027-06-18 | PO MR-ME-004
8 | ALP-I07-00CYA-ME-ITP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Inspection and Test Plan |  | I07 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-07 |  | 2027-06-21 | 2027-06-21 | PO MR-IC-007 | G-PRC-FAB MR-IC-007 | 2027-09-13 | G-PRC-FAB MR-IC-007 ACCEPTED
8 | ALP-M05-00PBA-ME-LST-0001 | Electro-Chlorination Package - Spare Parts and Special Tools Lists |  | M05 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-04-30 |  | 2027-05-14 | 2027-06-21 | PO MR-ME-005
8 | ALP-M06-00PAH-EL-WIR-0001 | Condenser Tube Cleaning System - Supplier Electrical Schematics and Wiring Diagrams |  | M06 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-04-19 | 2027-05-10 |  | 2027-05-24 | 2027-06-21 | PO MR-ME-006 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-FF 00PAH IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC
8 | ALP-M06-00PAH-IC-DSH-0001 | Condenser Tube Cleaning System - Supplier Instrument List and Datasheets |  | M06 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-26 | 2027-05-10 |  | 2027-05-24 | 2027-06-21 | PO MR-ME-006
8 | ALP-EPC-00BFA-EL-WIR-0009 | LV Schematic and Wiring Diagrams, Part 5 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-04-30 | 2027-06-15 |  | 2027-06-15 | 2027-06-22 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-M10-00QJA-ME-DSH-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Certified Datasheets and Performance Curves |  | M10 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-01 |  | 2027-06-15 | 2027-06-22 | PO MR-ME-010 | G-PRC-FAB MR-ME-010 | 2027-08-23 | G-PRC-FAB MR-ME-010 ACCEPTED
8 | ALP-I02-00CQA-EL-WIR-0001 | Continuous Emission Monitoring System - Supplier Electrical Schematics and Wiring Diagrams |  | I02 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-04-21 | 2027-05-12 |  | 2027-05-26 | 2027-06-23 | PO MR-IC-002 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-COM-MC-FF 00CQA IFC G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
8 | ALP-I02-00CQA-IC-DSH-0001 | Continuous Emission Monitoring System - Supplier Instrument List and Datasheets |  | I02 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-28 | 2027-05-12 |  | 2027-05-26 | 2027-06-23 | PO MR-IC-002
8 | ALP-I08-00CJG-ME-GAD-0001 | BOP Safety Instrumented System - Supplier GA Drawings | IEC 61511 | I08 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-29 | 2027-05-27 |  | 2027-06-10 | 2027-06-23 | PO MR-IC-008 | G-PRC-FAB MR-IC-008 | 2027-08-18 | G-COM-MC-FF 00CJG IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC G-PRC-FAB MR-IC-008 ACCEPTED
8 | ALP-I03-00QUA-EL-WIR-0001 | Steam/Water Analysis System - Supplier Electrical Schematics and Wiring Diagrams |  | I03 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-04-23 | 2027-05-14 |  | 2027-05-28 | 2027-06-25 | PO MR-IC-003 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-COM-MC-FF 00QUA IFC G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
8 | ALP-I03-00QUA-IC-DSH-0001 | Steam/Water Analysis System - Supplier Instrument List and Datasheets |  | I03 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-05-14 |  | 2027-05-28 | 2027-06-25 | PO MR-IC-003
8 | ALP-M11-00QCA-ME-DSH-0001 | Chemical Dosing Skid - Supplier Certified Datasheets and Performance Curves |  | M11 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-05-31 |  | 2027-06-14 | 2027-06-25 | PO MR-ME-011 | G-PRC-FAB MR-ME-011 | 2027-07-28 | G-PRC-FAB MR-ME-011 ACCEPTED
8 | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | subcontract | EPC | general | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2027-06-16 | 2027-06-23 |  | 2027-06-23 | 2027-06-28 | ALP-EPC-00UZF-GE-SPC-0001 | G-PRC-ENQ MR-ME-024 | 2027-09-20 | G-PRC-ENQ MR-ME-024 IFR G-PRC-PO MR-ME-024 IFC
8 | ALP-I07-00CYA-ME-DSH-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Certified Datasheets and Performance Curves |  | I07 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-07 |  | 2027-06-21 | 2027-06-28 | PO MR-IC-007 | G-PRC-FAB MR-IC-007 | 2027-09-13 | G-PRC-FAB MR-IC-007 ACCEPTED
8 | ALP-M02-20LCB-ME-LST-0001 | Condensate Extraction Pumps - Spare Parts and Special Tools Lists |  | M02 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-16 | 2027-05-07 |  | 2027-05-21 | 2027-06-28 | PO MR-ME-002
8 | ALP-EPC-00GBA-CM-OMM-0001 | Seawater Reverse Osmosis - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-04-20 | 2027-06-01 |  | 2027-06-15 | 2027-06-29 | ALP-EPC-00GBA-CM-CMP-0001 | G-COM-SC-FF 00GBA | 2028-07-24 | G-COM-SC-FF 00GBA IFR G-OPS-HO-FF 00GBA IFC
8 | ALP-M10-00QJA-ME-GAD-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier GA Drawings |  | M10 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-11 | 2027-06-08 |  | 2027-06-22 | 2027-06-29 | PO MR-ME-010 | G-PRC-FAB MR-ME-010 | 2027-08-23 | G-COM-MC-FF 00QJA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-PRC-FAB MR-ME-010 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0010 | LV Schematic and Wiring Diagrams, Part 6 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-05-06 | 2027-06-23 |  | 2027-06-23 | 2027-06-30 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-M06-00PAH-ME-LST-0001 | Condenser Tube Cleaning System - Spare Parts and Special Tools Lists |  | M06 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-28 | 2027-05-19 |  | 2027-06-02 | 2027-06-30 | PO MR-ME-006
8 | ALP-M20-00SGA-ME-TST-0001 | Fire Pumps and Fire Protection Systems - Factory Acceptance Test Procedure |  | M20 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-29 | 2027-05-20 |  | 2027-06-17 | 2027-07-01 | PO MR-ME-020 | G-PRC-FAT MR-ME-020 | 2027-08-12 | G-PRC-FAT MR-ME-020 ACCEPTED
8 | ALP-I02-00CQA-ME-LST-0001 | Continuous Emission Monitoring System - Spare Parts and Special Tools Lists |  | I02 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-30 | 2027-05-21 |  | 2027-06-04 | 2027-07-02 | PO MR-IC-002
8 | ALP-I08-00CJG-IC-IOL-0001 | BOP Safety Instrumented System - Supplier I/O List, Control Philosophy and Interface Signals | IEC 61511 | I08 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-14 | 2027-06-04 |  | 2027-06-18 | 2027-07-02 | PO MR-IC-008
8 | ALP-I08-00CJG-ME-CAL-0001 | BOP Safety Instrumented System - Supplier Design Calculations | IEC 61511 | I08 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-14 | 2027-06-04 |  | 2027-06-18 | 2027-07-02 | PO MR-IC-008 | G-PRC-FAB MR-IC-008 | 2027-08-18 | G-PRC-FAB MR-IC-008 ACCEPTED
8 | ALP-EPC-00GMA-CM-OMM-0001 | Process Drains and Waste Water Collection - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-04-22 | 2027-06-07 |  | 2027-06-21 | 2027-07-05 | capacity commissioning | G-COM-SC-FF 00GMA | 2028-07-24 | G-COM-SC-FF 00GMA IFR G-OPS-HO-FF 00GMA IFC
8 | ALP-I07-00CYA-ME-GAD-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier GA Drawings |  | I07 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-17 | 2027-06-14 |  | 2027-06-28 | 2027-07-05 | PO MR-IC-007 | G-PRC-FAB MR-IC-007 | 2027-09-13 | G-COM-MC-FF 00CYA IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC G-PRC-FAB MR-IC-007 ACCEPTED
8 | ALP-M19-10HAN-ME-PRC-0001 | HRSG Blowdown and Drain Tanks - Supplier Installation and Erection Manual |  | M19 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-03 | 2027-05-24 |  | 2027-06-07 | 2027-07-05 | PO MR-ME-019 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-CON-CWP CWP-01-ME-01 IFR
8 | ALP-I03-00QUA-ME-LST-0001 | Steam/Water Analysis System - Spare Parts and Special Tools Lists |  | I03 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-04 | 2027-05-25 |  | 2027-06-08 | 2027-07-06 | PO MR-IC-003
8 | ALP-M10-00QJA-IC-IOL-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier I/O List, Control Philosophy and Interface Signals |  | M10 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-25 | 2027-06-15 |  | 2027-06-29 | 2027-07-06 | PO MR-ME-010
8 | ALP-M10-00QJA-ME-CAL-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Design Calculations |  | M10 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-25 | 2027-06-15 |  | 2027-06-29 | 2027-07-06 | PO MR-ME-010 | G-PRC-FAB MR-ME-010 | 2027-08-23 | G-PRC-FAB MR-ME-010 ACCEPTED
8 | ALP-M10-00QJA-PR-PID-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier P&IDs |  | M10 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-11 | 2027-06-15 |  | 2027-07-06 | 2027-07-06 | PO MR-ME-010 | G-PRC-FAB MR-ME-010 | 2027-08-23 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-010 ACCEPTED
8 | ALP-M11-00QCA-ME-GAD-0001 | Chemical Dosing Skid - Supplier GA Drawings |  | M11 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-12 | 2027-06-09 |  | 2027-06-23 | 2027-07-06 | PO MR-ME-011 | G-PRC-FAB MR-ME-011 | 2027-07-28 | G-COM-MC-FF 00QCA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC G-PRC-FAB MR-ME-011 ACCEPTED
8 | ALP-I09-00CKA-ME-ITP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Inspection and Test Plan |  | I09 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-10 |  | 2027-07-01 | 2027-07-08 | PO MR-IC-009 | G-PRC-FAB MR-IC-009 | 2027-10-11 | G-PRC-FAB MR-IC-009 ACCEPTED
8 | ALP-M07-00PGA-ME-TST-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Factory Acceptance Test Procedure |  | M07 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-06 | 2027-05-27 |  | 2027-06-24 | 2027-07-08 | PO MR-ME-007 | G-PRC-FAT MR-ME-007 | 2027-08-19 | G-PRC-FAT MR-ME-007 ACCEPTED
8 | ALP-M08-00QEA-ME-TST-0001 | Air Compressors and Dryers - Factory Acceptance Test Procedure |  | M08 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-06 | 2027-05-27 |  | 2027-06-24 | 2027-07-08 | PO MR-ME-008 | G-PRC-FAT MR-ME-008 | 2027-08-19 | G-PRC-FAT MR-ME-008 ACCEPTED
8 | ALP-M13-00GHA-ME-TRP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Factory Acceptance Test Report |  | M13 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-18 | 2027-06-25 |  | 2027-07-09 | 2027-07-09 | PO MR-ME-013 | G-PRC-SHP MR-ME-013 | 2027-07-23 | G-PRC-SHP MR-ME-013 ACCEPTED
8 | ALP-I07-00CYA-IC-IOL-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier I/O List, Control Philosophy and Interface Signals |  | I07 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-21 |  | 2027-07-05 | 2027-07-12 | PO MR-IC-007
8 | ALP-I07-00CYA-ME-CAL-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Design Calculations |  | I07 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-21 |  | 2027-07-05 | 2027-07-12 | PO MR-IC-007 | G-PRC-FAB MR-IC-007 | 2027-09-13 | G-PRC-FAB MR-IC-007 ACCEPTED
8 | ALP-M18-10HSB-ME-TST-0001 | Aqueous Ammonia Storage and Forwarding - Factory Acceptance Test Procedure |  | M18 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-10 | 2027-05-31 |  | 2027-06-28 | 2027-07-12 | PO MR-ME-018 | G-PRC-FAT MR-ME-018 | 2027-08-23 | G-PRC-FAT MR-ME-018 ACCEPTED
8 | ALP-EPC-00BFA-EL-WIR-0011 | LV Schematic and Wiring Diagrams, Part 7 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-05-24 | 2027-07-06 |  | 2027-07-06 | 2027-07-13 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-H01-00SAA-ME-PRC-0001 | HVAC Plant and Equipment - Supplier Installation and Erection Manual |  | H01 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-03 |  | 2027-06-17 | 2027-07-15 | PO MR-HV-001 | G-CON-CWP CWP-03-HV-01 | 2027-10-11 | G-CON-CWP CWP-01-HV-01 IFR G-CON-CWP CWP-03-HV-01 IFR G-CON-CWP CWP-11-HV-01 IFR
8 | ALP-M11-00QCA-IC-IOL-0001 | Chemical Dosing Skid - Supplier I/O List, Control Philosophy and Interface Signals |  | M11 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-17 |  | 2027-07-01 | 2027-07-15 | PO MR-ME-011
8 | ALP-M11-00QCA-ME-CAL-0001 | Chemical Dosing Skid - Supplier Design Calculations |  | M11 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-17 |  | 2027-07-01 | 2027-07-15 | PO MR-ME-011 | G-PRC-FAB MR-ME-011 | 2027-07-28 | G-PRC-FAB MR-ME-011 ACCEPTED
8 | ALP-M11-00QCA-PR-PID-0001 | Chemical Dosing Skid - Supplier P&IDs |  | M11 | process | PID | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-17 |  | 2027-07-15 | 2027-07-15 | PO MR-ME-011 | G-PRC-FAB MR-ME-011 | 2027-07-28 | G-OPS-AB 00000 AB G-PRC-FAB MR-ME-011 ACCEPTED
8 | ALP-M14-00GNA-IC-LOG-0001 | Waste Water and Sanitary Treatment Packages - Supplier Logic Diagrams |  | M14 | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-05-13 |  | 2027-05-27 | 2027-07-15 | PO MR-ME-014
8 | ALP-M14-00GNA-ME-PRC-0001 | Waste Water and Sanitary Treatment Packages - Supplier Installation and Erection Manual |  | M14 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-03 |  | 2027-06-17 | 2027-07-15 | PO MR-ME-014 | G-CON-CWP CWP-07-ME-01 | 2027-12-27 | G-CON-CWP CWP-07-ME-01 IFR
8 | ALP-M16-00EGA-ME-TST-0001 | LDO Unloading and Forwarding / Treatment Skids - Factory Acceptance Test Procedure |  | M16 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-03 |  | 2027-07-01 | 2027-07-15 | PO MR-ME-016 | G-PRC-FAT MR-ME-016 | 2027-08-26 | G-PRC-FAT MR-ME-016 ACCEPTED
8 | ALP-M21-00SMA-ME-TST-0001 | EOT Cranes - Factory Acceptance Test Procedure |  | M21 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-03 |  | 2027-07-01 | 2027-07-15 | PO MR-ME-021 | G-PRC-FAT MR-ME-021 | 2027-08-26 | G-PRC-FAT MR-ME-021 ACCEPTED
8 | ALP-M10-00QJA-EL-WIR-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Electrical Schematics and Wiring Diagrams |  | M10 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-06-01 | 2027-06-22 |  | 2027-07-06 | 2027-07-20 | PO MR-ME-010 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-COM-MC-FF 00QJA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC
8 | ALP-M10-00QJA-IC-DSH-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Instrument List and Datasheets |  | M10 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-06-22 |  | 2027-07-06 | 2027-07-20 | PO MR-ME-010
8 | ALP-EPC-00BFA-EL-WIR-0012 | LV Schematic and Wiring Diagrams, Part 8 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-06-01 | 2027-07-14 |  | 2027-07-14 | 2027-07-21 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-EPC-00GNA-CM-OMM-0001 | Waste Water Treatment - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-04-23 | 2027-06-23 |  | 2027-07-07 | 2027-07-21 | capacity commissioning | G-COM-SC-FF 00GNA | 2028-07-24 | G-COM-SC-FF 00GNA IFR G-OPS-HO-FF 00GNA IFC
8 | ALP-I08-00CJG-EL-WIR-0001 | BOP Safety Instrumented System - Supplier Electrical Schematics and Wiring Diagrams | IEC 61511 | I08 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-05-24 | 2027-06-14 |  | 2027-06-28 | 2027-07-21 | PO MR-IC-008 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-COM-MC-FF 00CJG IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
8 | ALP-EPC-00EGA-CM-OMM-0001 | LDO Unloading - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-24 |  | 2027-07-08 | 2027-07-22 | ALP-EPC-00EGA-CM-CMP-0001 | G-COM-SC-FF 00EGA | 2028-07-24 | G-COM-SC-FF 00EGA IFR G-OPS-HO-FF 00EGA IFC
8 | ALP-I09-00CKA-ME-DSH-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Certified Datasheets and Performance Curves |  | I09 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-10 |  | 2027-06-24 | 2027-07-22 | PO MR-IC-009 | G-PRC-FAB MR-IC-009 | 2027-10-11 | G-PRC-FAB MR-IC-009 ACCEPTED
8 | ALP-EPC-00PAA-CM-OMM-0001 | CW Intake, Screens and Outfall - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-04-23 | 2027-06-25 |  | 2027-07-09 | 2027-07-23 | capacity commissioning | G-COM-SC-FF 00PAA | 2028-07-24 | G-COM-SC-FF 00PAA IFR G-OPS-HO-FF 00PAA IFC
8 | ALP-EPC-00BFA-EL-WIR-0013 | LV Schematic and Wiring Diagrams, Part 9 of 13 |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-LST-0001 is NONE, IFR needs it at IFC |  | 2027-06-04 | 2027-07-19 |  | 2027-07-19 | 2027-07-26 | capacity electrical | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-I07-00CYA-EL-WIR-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Electrical Schematics and Wiring Diagrams |  | I07 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-06-07 | 2027-06-28 |  | 2027-07-12 | 2027-07-26 | PO MR-IC-007 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-COM-MC-FF 00CYA IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
8 | ALP-EPC-00PGA-CM-OMM-0001 | Closed Cooling Water - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-06-29 |  | 2027-07-13 | 2027-07-27 | capacity commissioning | G-COM-SC-FF 00PGA | 2028-07-24 | G-COM-SC-FF 00PGA IFR G-OPS-HO-FF 00PGA IFC
8 | ALP-M10-00QJA-ME-LST-0001 | Nitrogen, Hydrogen and CO2 Supply - Spare Parts and Special Tools Lists |  | M10 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-06-29 |  | 2027-07-13 | 2027-07-27 | PO MR-ME-010
8 | ALP-M10-00QJA-ME-TST-0001 | Nitrogen, Hydrogen and CO2 Supply - Factory Acceptance Test Procedure |  | M10 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-25 | 2027-06-15 |  | 2027-07-13 | 2027-07-27 | PO MR-ME-010 | G-PRC-FAT MR-ME-010 | 2027-09-07 | G-PRC-FAT MR-ME-010 ACCEPTED
8 | ALP-EPC-00UEK-EL-ELY-0002 | Fuel Gas Station - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-07-01 |  | 2027-07-15 | 2027-07-29 | capacity electrical | G-CON-CWP CWP-09-EL-01 | 2027-12-27 | G-CON-CWP CWP-09-EL-01 IFC G-CON-IWP CWP-09-EL-01 IFC
8 | ALP-I08-00CJG-ME-LST-0001 | BOP Safety Instrumented System - Spare Parts and Special Tools Lists | IEC 61511 | I08 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-02 | 2027-06-23 |  | 2027-07-07 | 2027-07-29 | PO MR-IC-008
8 | ALP-M20-00SGA-ME-PRC-0001 | Fire Pumps and Fire Protection Systems - Supplier Installation and Erection Manual |  | M20 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-17 |  | 2027-07-01 | 2027-07-29 | PO MR-ME-020 | G-CON-CWP CWP-01-HV-01 | 2027-11-01 | G-CON-CWP CWP-01-HV-01 IFR G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-I07-00CYA-ME-LST-0001 | Telecom, CCTV, Access Control and Perimeter Security - Spare Parts and Special Tools Lists |  | I07 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-14 | 2027-07-05 |  | 2027-07-19 | 2027-08-02 | PO MR-IC-007
8 | ALP-I07-00CYA-ME-TST-0001 | Telecom, CCTV, Access Control and Perimeter Security - Factory Acceptance Test Procedure |  | I07 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-21 |  | 2027-07-19 | 2027-08-02 | PO MR-IC-007 | G-PRC-FAT MR-IC-007 | 2027-09-13 | G-PRC-FAT MR-IC-007 ACCEPTED
8 | ALP-M19-10HAN-ME-TRP-0001 | HRSG Blowdown and Drain Tanks - Factory Acceptance Test Report |  | M19 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-12 | 2027-07-19 |  | 2027-08-02 | 2027-08-02 | PO MR-ME-019 | G-PRC-SHP MR-ME-019 | 2027-08-16 | G-PRC-SHP MR-ME-019 ACCEPTED
8 | ALP-EPC-00EGB-CM-OMM-0001 | LDO Storage - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-05-25 | 2027-07-06 |  | 2027-07-20 | 2027-08-03 | ALP-EPC-00EGB-CM-CMP-0001 | G-COM-SC-FF 00EGB | 2028-07-24 | G-COM-SC-FF 00EGB IFR G-OPS-HO-FF 00EGB IFC
8 | ALP-M11-00QCA-EL-WIR-0001 | Chemical Dosing Skid - Supplier Electrical Schematics and Wiring Diagrams |  | M11 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-06-04 | 2027-06-25 |  | 2027-07-09 | 2027-08-03 | PO MR-ME-011 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-COM-MC-FF 00QCA IFC G-CON-CWP CWP-08-ME-01 IFC G-CON-IWP CWP-08-ME-01 IFC
8 | ALP-M11-00QCA-IC-DSH-0001 | Chemical Dosing Skid - Supplier Instrument List and Datasheets |  | M11 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-11 | 2027-06-25 |  | 2027-07-09 | 2027-08-03 | PO MR-ME-011
8 | ALP-M06-00PAH-ME-TST-0001 | Condenser Tube Cleaning System - Factory Acceptance Test Procedure |  | M06 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-02 | 2027-06-23 |  | 2027-07-21 | 2027-08-04 | PO MR-ME-006 | G-PRC-FAT MR-ME-006 | 2027-09-15 | G-PRC-FAT MR-ME-006 ACCEPTED
8 | ALP-I09-00CKA-ME-GAD-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier GA Drawings |  | I09 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-06-24 |  | 2027-07-08 | 2027-08-05 | PO MR-IC-009 | G-PRC-FAB MR-IC-009 | 2027-10-11 | G-COM-MC-FF 00CKA IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC G-PRC-FAB MR-IC-009 ACCEPTED
8 | ALP-M07-00PGA-ME-PRC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Installation and Erection Manual |  | M07 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-03 | 2027-06-24 |  | 2027-07-08 | 2027-08-05 | PO MR-ME-007 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-M08-00QEA-IC-LOG-0001 | Air Compressors and Dryers - Supplier Logic Diagrams |  | M08 | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-06 | 2027-06-03 |  | 2027-06-17 | 2027-08-05 | PO MR-ME-008
8 | ALP-M08-00QEA-ME-PRC-0001 | Air Compressors and Dryers - Supplier Installation and Erection Manual |  | M08 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-03 | 2027-06-24 |  | 2027-07-08 | 2027-08-05 | PO MR-ME-008 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-EPC-00EKC-CM-OMM-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-05-28 | 2027-07-09 |  | 2027-07-23 | 2027-08-06 | ALP-EPC-00EKC-CM-CMP-0001 | G-COM-SC-FF 00EKC | 2028-07-24 | G-COM-SC-FF 00EKC IFR G-OPS-HO-FF 00EKC IFC
8 | ALP-EPC-00GCA-CM-OMM-0001 | Demineralisation - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-05-28 | 2027-07-09 |  | 2027-07-23 | 2027-08-06 | ALP-EPC-00GCA-CM-CMP-0001 | G-COM-SC-FF 00GCA | 2028-07-24 | G-COM-SC-FF 00GCA IFR G-OPS-HO-FF 00GCA IFC
8 | ALP-EPC-00PBA-CM-OMM-0001 | Electro-Chlorination - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-04-23 | 2027-07-09 |  | 2027-07-23 | 2027-08-06 | capacity commissioning | G-COM-SC-FF 00PBA | 2028-07-24 | G-COM-SC-FF 00PBA IFR G-OPS-HO-FF 00PBA IFC
8 | ALP-I02-00CQA-ME-TST-0001 | Continuous Emission Monitoring System - Factory Acceptance Test Procedure |  | I02 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-04 | 2027-06-25 |  | 2027-07-23 | 2027-08-06 | PO MR-IC-002 | G-PRC-FAT MR-IC-002 | 2027-09-17 | G-PRC-FAT MR-IC-002 ACCEPTED
8 | ALP-EPC-00GHA-CM-OMM-0001 | Demineralised Water Storage and Distribution - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-07-12 |  | 2027-07-26 | 2027-08-09 | ALP-EPC-00GHA-CM-CMP-0001 | G-COM-SC-FF 00GHA | 2028-07-24 | G-COM-SC-FF 00GHA IFR G-OPS-HO-FF 00GHA IFC
8 | ALP-EPC-00GMA-PI-ISO-0001 | Process Drains and Waste Water Collection - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GMA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-06-04 | 2027-08-02 |  | 2027-08-02 | 2027-08-09 | capacity piping | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-COM-MC-FF 00GMA IFC G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00LDA-CM-OMM-0001 | Condensate Polishing - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-07-12 |  | 2027-07-26 | 2027-08-09 | ALP-EPC-00LDA-CM-CMP-0001 | G-COM-SC-FF 00LDA | 2028-07-24 | G-COM-SC-FF 00LDA IFR G-OPS-HO-FF 00LDA IFC
8 | ALP-EPC-00PAB-CM-OMM-0001 | CW Piping - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-07-12 |  | 2027-07-26 | 2027-08-09 | ALP-EPC-00PAB-CM-CMP-0001 | G-COM-SC-FF 00PAB | 2028-07-24 | G-COM-SC-FF 00PAB IFR G-OPS-HO-FF 00PAB IFC
8 | ALP-M18-10HSB-ME-PRC-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Installation and Erection Manual |  | M18 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-28 |  | 2027-07-12 | 2027-08-09 | PO MR-ME-018 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-I03-00QUA-ME-TST-0001 | Steam/Water Analysis System - Factory Acceptance Test Procedure |  | I03 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-08 | 2027-06-29 |  | 2027-07-27 | 2027-08-10 | PO MR-IC-003 | G-PRC-FAT MR-IC-003 | 2027-09-21 | G-PRC-FAT MR-IC-003 ACCEPTED
8 | ALP-M11-00QCA-ME-LST-0001 | Chemical Dosing Skid - Spare Parts and Special Tools Lists |  | M11 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-15 | 2027-07-06 |  | 2027-07-20 | 2027-08-11 | PO MR-ME-011
8 | ALP-EPC-00SAA-CM-OMM-0001 | HVAC - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-03-24 | 2027-07-15 |  | 2027-07-29 | 2027-08-12 | capacity commissioning | G-COM-SC-FF 00SAA | 2028-07-24 | G-COM-SC-FF 00SAA IFR G-OPS-HO-FF 00SAA IFC
8 | ALP-H01-00SAA-ME-TRP-0001 | HVAC Plant and Equipment - Factory Acceptance Test Report |  | H01 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-22 | 2027-07-29 |  | 2027-08-12 | 2027-08-12 | PO MR-HV-001 | G-PRC-SHP MR-HV-001 | 2027-08-26 | G-PRC-SHP MR-HV-001 ACCEPTED
8 | ALP-M01-10LAC-ME-TST-0001 | Boiler Feed Pumps - Factory Acceptance Test Procedure |  | M01 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-01 |  | 2027-07-29 | 2027-08-12 | PO MR-ME-001 | G-PRC-FAT MR-ME-001 | 2027-09-23 | G-PRC-FAT MR-ME-001 ACCEPTED
8 | ALP-M09-00QHA-ME-TST-0001 | Auxiliary Boiler - Factory Acceptance Test Procedure |  | M09 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-01 |  | 2027-07-29 | 2027-08-12 | PO MR-ME-009 | G-PRC-FAT MR-ME-009 | 2027-09-23 | G-PRC-FAT MR-ME-009 ACCEPTED
8 | ALP-M14-00GNA-ME-TRP-0001 | Waste Water and Sanitary Treatment Packages - Factory Acceptance Test Report |  | M14 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-22 | 2027-07-29 |  | 2027-08-12 | 2027-08-12 | PO MR-ME-014 | G-PRC-SHP MR-ME-014 | 2027-08-26 | G-PRC-SHP MR-ME-014 ACCEPTED
8 | ALP-M15-00EKA-ME-TST-0001 | Gas Receiving and Metering Station - Factory Acceptance Test Procedure |  | M15 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-01 |  | 2027-07-29 | 2027-08-12 | PO MR-ME-015 | G-PRC-FAT MR-ME-015 | 2027-09-23 | G-PRC-FAT MR-ME-015 ACCEPTED
8 | ALP-M16-00EGA-ME-PRC-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Installation and Erection Manual |  | M16 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-01 |  | 2027-07-15 | 2027-08-12 | PO MR-ME-016 | G-CON-CWP CWP-10-ME-01 | 2027-10-04 | G-CON-CWP CWP-10-ME-01 IFR
8 | ALP-M21-00SMA-ME-PRC-0001 | EOT Cranes - Supplier Installation and Erection Manual |  | M21 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-01 |  | 2027-07-15 | 2027-08-12 | PO MR-ME-021 | G-CON-CWP CWP-01-ME-01 | 2027-10-18 | G-CON-CWP CWP-01-ME-01 IFR G-CON-CWP CWP-02-ME-01 IFR
8 | ALP-M04-00PAA-ME-TST-0001 | Travelling Band Screens and Trash Rakes - Factory Acceptance Test Procedure |  | M04 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-11 | 2027-07-02 |  | 2027-07-30 | 2027-08-13 | PO MR-ME-004 | G-PRC-FAT MR-ME-004 | 2027-09-24 | G-PRC-FAT MR-ME-004 ACCEPTED
8 | ALP-EPC-00SGA-CM-OMM-0001 | Fire Water System - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-03-17 | 2027-07-19 |  | 2027-08-02 | 2027-08-16 | capacity commissioning | G-COM-SC-FF 00SGA | 2028-07-24 | G-COM-SC-FF 00SGA IFR G-OPS-HO-FF 00SGA IFC
8 | ALP-M05-00PBA-ME-TST-0001 | Electro-Chlorination Package - Factory Acceptance Test Procedure |  | M05 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-14 | 2027-07-05 |  | 2027-08-02 | 2027-08-16 | PO MR-ME-005 | G-PRC-FAT MR-ME-005 | 2027-09-27 | G-PRC-FAT MR-ME-005 ACCEPTED
8 | ALP-EPC-00PAC-CM-OMM-0001 | CW Pumps - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-07-21 |  | 2027-08-04 | 2027-08-18 | capacity commissioning | G-COM-SC-FF 00PAC | 2028-07-24 | G-COM-SC-FF 00PAC IFR G-OPS-HO-FF 00PAC IFC
8 | ALP-EPC-00QCA-CM-OMM-0001 | Chemical Dosing - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-04-23 | 2027-07-21 |  | 2027-08-04 | 2027-08-18 | capacity commissioning | G-COM-SC-FF 00QCA | 2028-07-24 | G-COM-SC-FF 00QCA IFR G-OPS-HO-FF 00QCA IFC
8 | ALP-EPC-00PAH-CM-OMM-0001 | Condenser Tube Cleaning - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-06-01 | 2027-07-22 |  | 2027-08-05 | 2027-08-19 | capacity commissioning | G-COM-SC-FF 00PAH | 2028-07-24 | G-COM-SC-FF 00PAH IFR G-OPS-HO-FF 00PAH IFC
8 | ALP-EPC-00UZF-CV-RBR-0001 | Temporary Barge Landing - Reinforcement Drawings |  | EPC | civil | RBR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-CV-FND-0001 is NONE, IFR needs it at IFR |  | 2027-07-02 | 2027-07-29 |  | 2027-08-12 | 2027-08-19 | ALP-EPC-00UZF-CV-FND-0001 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
8 | ALP-I08-00CJG-ME-TST-0001 | BOP Safety Instrumented System - Factory Acceptance Test Procedure | IEC 61511 | I08 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-17 | 2027-07-08 |  | 2027-08-05 | 2027-08-19 | PO MR-IC-008 | G-PRC-FAT MR-IC-008 | 2027-09-30 | G-PRC-FAT MR-IC-008 ACCEPTED
8 | ALP-I09-00CKA-IC-IOL-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier I/O List, Control Philosophy and Interface Signals |  | I09 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-17 | 2027-07-08 |  | 2027-07-22 | 2027-08-19 | PO MR-IC-009
8 | ALP-I09-00CKA-ME-CAL-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Design Calculations |  | I09 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-17 | 2027-07-08 |  | 2027-07-22 | 2027-08-19 | PO MR-IC-009 | G-PRC-FAB MR-IC-009 | 2027-10-11 | G-PRC-FAB MR-IC-009 ACCEPTED
8 | ALP-M02-20LCB-ME-TST-0001 | Condensate Extraction Pumps - Factory Acceptance Test Procedure |  | M02 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-21 | 2027-07-12 |  | 2027-08-09 | 2027-08-23 | PO MR-ME-002 | G-PRC-FAT MR-ME-002 | 2027-10-04 | G-PRC-FAT MR-ME-002 ACCEPTED
8 | ALP-M10-00QJA-ME-PRC-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Installation and Erection Manual |  | M10 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-22 | 2027-07-13 |  | 2027-07-27 | 2027-08-24 | PO MR-ME-010 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-EPC-00SGC-CM-OMM-0001 | Deluge, Spray and Foam Systems - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-03-17 | 2027-07-28 |  | 2027-08-11 | 2027-08-25 | capacity commissioning | G-COM-SC-FF 00SGC | 2028-07-24 | G-COM-SC-FF 00SGC IFR G-OPS-HO-FF 00SGC IFC
8 | ALP-EPC-00GKA-PI-ISO-0001 | Potable Water - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-06-24 | 2027-08-19 |  | 2027-08-19 | 2027-08-26 | capacity piping | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-COM-MC-FF 00GKA IFC G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00QEA-CM-OMM-0001 | Compressed Air - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-04-26 | 2027-07-29 |  | 2027-08-12 | 2027-08-26 | capacity commissioning | G-COM-SC-FF 00QEA | 2028-07-24 | G-COM-SC-FF 00QEA IFR G-OPS-HO-FF 00QEA IFC
8 | ALP-M09-00QHA-IC-LOG-0001 | Auxiliary Boiler - Supplier Logic Diagrams |  | M09 | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-06 | 2027-06-03 |  | 2027-06-17 | 2027-08-26 | PO MR-ME-009
8 | ALP-M20-00SGA-ME-TRP-0001 | Fire Pumps and Fire Protection Systems - Factory Acceptance Test Report |  | M20 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-05 | 2027-08-12 |  | 2027-08-26 | 2027-08-26 | PO MR-ME-020 | G-PRC-SHP MR-ME-020 | 2027-09-09 | G-PRC-SHP MR-ME-020 ACCEPTED
8 | ALP-EPC-00PAA-PI-ISO-0001 | CW Intake, Screens and Outfall - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PAA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-08-20 |  | 2027-08-20 | 2027-08-27 | capacity piping | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PAA IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00PAC-PI-ISO-0001 | CW Pumps - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-08-20 |  | 2027-08-20 | 2027-08-27 | capacity piping | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PAC IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00UAC-IC-LOP-0001 | 380 kV GIS Switchyard - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-IC-ELY-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-07-28 | 2027-08-20 |  | 2027-08-20 | 2027-08-27 | ALP-EPC-00UAC-IC-ELY-0002 | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
8 | ALP-EPC-00UZA-IC-LOP-0001 | Site-Wide Infrastructure - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZA-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-07-28 | 2027-08-20 |  | 2027-08-20 | 2027-08-27 | ALP-EPC-00UZA-IC-ELY-0001 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
8 | ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00PAB-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-08-23 |  | 2027-08-23 | 2027-08-30 | capacity piping | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PAB IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00PBA-PI-ISO-0001 | Electro-Chlorination - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-08-23 |  | 2027-08-23 | 2027-08-30 | capacity piping | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PBA IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-I07-00CYA-ME-PRC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Installation and Erection Manual |  | I07 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-28 | 2027-07-19 |  | 2027-08-02 | 2027-08-30 | PO MR-IC-007 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFR
8 | ALP-EPC-00UZF-EL-ELY-0001 | Temporary Barge Landing - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-07-02 | 2027-08-03 |  | 2027-08-17 | 2027-08-31 | ALP-EPC-00UZF-CV-FND-0001 | G-CON-CWP CWP-06-CV-01 | 2027-09-03 | G-CON-CWP CWP-06-CV-01 IFC G-CON-IWP CWP-06-CV-01 IFC
8 | ALP-M06-00PAH-ME-PRC-0001 | Condenser Tube Cleaning System - Supplier Installation and Erection Manual |  | M06 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-21 |  | 2027-08-04 | 2027-09-01 | PO MR-ME-006 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-CON-CWP CWP-02-PI-01 IFR
8 | ALP-M11-00QCA-ME-TST-0001 | Chemical Dosing Skid - Factory Acceptance Test Procedure |  | M11 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-30 | 2027-07-21 |  | 2027-08-18 | 2027-09-01 | PO MR-ME-011 | G-PRC-FAT MR-ME-011 | 2027-10-13 | G-PRC-FAT MR-ME-011 ACCEPTED
8 | ALP-M07-00PGA-ME-TRP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Factory Acceptance Test Report |  | M07 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-12 | 2027-08-19 |  | 2027-09-02 | 2027-09-02 | PO MR-ME-007 | G-PRC-SHP MR-ME-007 | 2027-09-16 | G-PRC-SHP MR-ME-007 ACCEPTED
8 | ALP-M08-00QEA-ME-TRP-0001 | Air Compressors and Dryers - Factory Acceptance Test Report |  | M08 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-12 | 2027-08-19 |  | 2027-09-02 | 2027-09-02 | PO MR-ME-008 | G-PRC-SHP MR-ME-008 | 2027-09-16 | G-PRC-SHP MR-ME-008 ACCEPTED
8 | ALP-EPC-00QHA-CM-OMM-0001 | Auxiliary Boiler - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-06-25 | 2027-08-06 |  | 2027-08-20 | 2027-09-03 | capacity commissioning | G-COM-SC-FF 00QHA | 2028-07-24 | G-COM-SC-FF 00QHA IFR G-OPS-HO-FF 00QHA IFC
8 | ALP-EPC-00QJA-CM-OMM-0001 | Nitrogen Supply - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-06-25 | 2027-08-06 |  | 2027-08-20 | 2027-09-03 | capacity commissioning | G-COM-SC-FF 00QJA | 2028-07-24 | G-COM-SC-FF 00QJA IFR G-OPS-HO-FF 00QJA IFC
8 | ALP-EPC-00QJB-CM-OMM-0001 | Hydrogen and CO2 Supply - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-06-25 | 2027-08-06 |  | 2027-08-20 | 2027-09-03 | capacity commissioning | G-COM-SC-FF 00QJB | 2028-07-24 | G-COM-SC-FF 00QJB IFR G-OPS-HO-FF 00QJB IFC
8 | ALP-I02-00CQA-ME-PRC-0001 | Continuous Emission Monitoring System - Supplier Installation and Erection Manual |  | I02 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-02 | 2027-07-23 |  | 2027-08-06 | 2027-09-03 | PO MR-IC-002 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFR
8 | ALP-M05-00PBA-IC-LOG-0001 | Electro-Chlorination Package - Supplier Logic Diagrams |  | M05 | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-21 |  | 2027-07-05 | 2027-09-03 | PO MR-ME-005
8 | ALP-M13-00GHA-ME-MDB-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Manufacturing Record Book and Conformity Certificates |  | M13 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-25 | 2027-07-09 |  | 2027-07-09 | 2027-09-03 | PO MR-ME-013 | G-PRC-SHP MR-ME-013 | 2027-07-23 | G-PRC-SHP MR-ME-013 IFR
8 | ALP-M18-10HSB-ME-TRP-0001 | Aqueous Ammonia Storage and Forwarding - Factory Acceptance Test Report |  | M18 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-16 | 2027-08-23 |  | 2027-09-06 | 2027-09-06 | PO MR-ME-018 | G-PRC-SHP MR-ME-018 | 2027-09-20 | G-PRC-SHP MR-ME-018 ACCEPTED
8 | ALP-EPC-00QUA-CM-OMM-0001 | Sampling and SWAS - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-06-29 | 2027-08-10 |  | 2027-08-24 | 2027-09-07 | capacity commissioning | G-COM-SC-FF 00QUA | 2028-07-24 | G-COM-SC-FF 00QUA IFR G-OPS-HO-FF 00QUA IFC
8 | ALP-EPC-00UBA-EL-ELY-0002 | Electrical Building and Emergency Power - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-08-10 |  | 2027-08-24 | 2027-09-07 | ALP-EPC-00UBA-PI-PPL-0001 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-EPC-00UCA-EL-ELY-0002 | Control, Administration and Workshop Buildings - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-07-09 | 2027-08-10 |  | 2027-08-24 | 2027-09-07 | ALP-EPC-00UCA-PI-PPL-0001 | G-CON-CWP CWP-11-EL-01 | 2027-11-08 | G-CON-CWP CWP-11-EL-01 IFC G-CON-IWP CWP-11-EL-01 IFC
8 | ALP-I03-00QUA-ME-PRC-0001 | Steam/Water Analysis System - Supplier Installation and Erection Manual |  | I03 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-06 | 2027-07-27 |  | 2027-08-10 | 2027-09-07 | PO MR-IC-003 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFR
8 | ALP-EPC-00UAC-IC-LOP-0002 | 380 kV GIS Switchyard - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
8 | ALP-EPC-00UBA-IC-LOP-0002 | Electrical Building and Emergency Power - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-EPC-00UCA-IC-LOP-0001 | Control, Administration and Workshop Buildings - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
8 | ALP-EPC-00UEG-IC-LOP-0001 | LDO Tank Farm and Unloading - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-10-IC-01 | 2028-02-21 | G-CON-CWP CWP-10-IC-01 IFC G-CON-IWP CWP-10-IC-01 IFC
8 | ALP-EPC-00UEG-IC-LOP-0002 | LDO Tank Farm and Unloading - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-02 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00UEG-IC-ELY-0001 | G-CON-CWP CWP-10-IC-01 | 2028-02-21 | G-CON-CWP CWP-10-IC-01 IFC G-CON-IWP CWP-10-IC-01 IFC
8 | ALP-EPC-00UEK-IC-LOP-0001 | Fuel Gas Station - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-09-IC-01 | 2028-01-24 | G-CON-CWP CWP-09-IC-01 IFC G-CON-IWP CWP-09-IC-01 IFC
8 | ALP-EPC-00UPC-IC-LOP-0001 | CW Pump House and Onshore CW - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-05-IC-01 | 2028-02-28 | G-CON-CWP CWP-05-IC-01 IFC G-CON-IWP CWP-05-IC-01 IFC
8 | ALP-EPC-00UPC-IC-LOP-0002 | CW Pump House and Onshore CW - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-02 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00UPC-IC-ELY-0001 | G-CON-CWP CWP-05-IC-01 | 2028-02-28 | G-CON-CWP CWP-05-IC-01 IFC G-CON-IWP CWP-05-IC-01 IFC
8 | ALP-EPC-00UQA-IC-LOP-0001 | BOP Utilities - Loop and Connection Diagrams, Part 1 of 2 |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-08-IC-01 | 2028-02-21 | G-CON-CWP CWP-08-IC-01 IFC G-CON-IWP CWP-08-IC-01 IFC
8 | ALP-EPC-00UQA-IC-LOP-0003 | BOP Utilities - Loop and Connection Diagrams, Part 2 of 2 |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-08-IC-01 | 2028-02-21 | G-CON-CWP CWP-08-IC-01 IFC G-CON-IWP CWP-08-IC-01 IFC
8 | ALP-EPC-00UZA-IC-LOP-0002 | Site-Wide Infrastructure - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
8 | ALP-EPC-10UMA-IC-LOP-0001 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 1 of 2 |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBY-IC-CBL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBY-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
8 | ALP-EPC-10UMA-IC-LOP-0003 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 2 of 2 |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-09-01 |  | 2027-09-01 | 2027-09-08 | ALP-EPC-00000-IC-IOL-0001 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
8 | ALP-EPC-00UEK-IC-LOP-0002 | Fuel Gas Station - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-02 | 2027-09-02 |  | 2027-09-02 | 2027-09-09 | ALP-EPC-00UEK-IC-ELY-0001 | G-CON-CWP CWP-09-IC-01 | 2028-01-24 | G-CON-CWP CWP-09-IC-01 IFC G-CON-IWP CWP-09-IC-01 IFC
8 | ALP-EPC-10UMA-EL-ELY-0002 | Power Block - GT and HRSG - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-06-15 | 2027-08-12 |  | 2027-08-26 | 2027-09-09 | capacity electrical | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
8 | ALP-M01-10LAC-ME-PRC-0001 | Boiler Feed Pumps - Supplier Installation and Erection Manual |  | M01 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-07-29 |  | 2027-08-12 | 2027-09-09 | PO MR-ME-001 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-M03-00PAC-ME-TST-0001 | CW Pumps - Factory Acceptance Test Procedure |  | M03 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-07-29 |  | 2027-08-26 | 2027-09-09 | PO MR-ME-003 | G-PRC-FAT MR-ME-003 | 2027-10-21 | G-PRC-FAT MR-ME-003 ACCEPTED
8 | ALP-M09-00QHA-ME-PRC-0001 | Auxiliary Boiler - Supplier Installation and Erection Manual |  | M09 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-07-29 |  | 2027-08-12 | 2027-09-09 | PO MR-ME-009 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-M12-00GBA-IC-LOG-0001 | Water Treatment Package - Supplier Logic Diagrams | SWRO, demin, condensate polishing | M12 | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-20 | 2027-06-17 |  | 2027-07-01 | 2027-09-09 | PO MR-ME-012
8 | ALP-M15-00EKA-ME-PRC-0001 | Gas Receiving and Metering Station - Supplier Installation and Erection Manual |  | M15 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-08 | 2027-07-29 |  | 2027-08-12 | 2027-09-09 | PO MR-ME-015 | G-CON-CWP CWP-09-ME-01 | 2027-11-01 | G-CON-CWP CWP-09-ME-01 IFR
8 | ALP-M16-00EGA-ME-TRP-0001 | LDO Unloading and Forwarding / Treatment Skids - Factory Acceptance Test Report |  | M16 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-08-26 |  | 2027-09-09 | 2027-09-09 | PO MR-ME-016 | G-PRC-SHP MR-ME-016 | 2027-09-23 | G-PRC-SHP MR-ME-016 ACCEPTED
8 | ALP-M21-00SMA-ME-TRP-0001 | EOT Cranes - Factory Acceptance Test Report |  | M21 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-08-26 |  | 2027-09-09 | 2027-09-09 | PO MR-ME-021 | G-PRC-SHP MR-ME-021 | 2027-09-23 | G-PRC-SHP MR-ME-021 ACCEPTED
8 | ALP-EPC-00UAC-EL-ELY-0002 | 380 kV GIS Switchyard - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-07-16 | 2027-08-13 |  | 2027-08-27 | 2027-09-10 | capacity electrical | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
8 | ALP-EPC-00UCA-IC-LOP-0002 | Control, Administration and Workshop Buildings - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UCA-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-02 | 2027-09-03 |  | 2027-09-03 | 2027-09-10 | ALP-EPC-00UCA-IC-ELY-0001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
8 | ALP-M04-00PAA-ME-PRC-0001 | Travelling Band Screens and Trash Rakes - Supplier Installation and Erection Manual |  | M04 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-09 | 2027-07-30 |  | 2027-08-13 | 2027-09-10 | PO MR-ME-004 | G-CON-CWP CWP-05-ME-01 | 2027-12-20 | G-CON-CWP CWP-05-ME-01 IFR
8 | ALP-EPC-00GKA-CM-OMM-0001 | Potable Water - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-07-05 | 2027-08-16 |  | 2027-08-30 | 2027-09-13 | ALP-EPC-00GKA-CM-CMP-0001 | G-COM-SC-FF 00GKA | 2028-07-24 | G-COM-SC-FF 00GKA IFR G-OPS-HO-FF 00GKA IFC
8 | ALP-EPC-00GUA-CM-OMM-0001 | Sanitary Waste Water Treatment - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GUA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-07-05 | 2027-08-16 |  | 2027-08-30 | 2027-09-13 | ALP-EPC-00GUA-CM-CMP-0001 | G-COM-SC-FF 00GUA | 2028-07-24 | G-COM-SC-FF 00GUA IFR G-OPS-HO-FF 00GUA IFC
8 | ALP-M05-00PBA-ME-PRC-0001 | Electro-Chlorination Package - Supplier Installation and Erection Manual |  | M05 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-12 | 2027-08-02 |  | 2027-08-16 | 2027-09-13 | PO MR-ME-005 | G-CON-CWP CWP-05-ME-01 | 2027-12-20 | G-CON-CWP CWP-05-ME-01 IFR
8 | ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-07-13 | 2027-09-07 |  | 2027-09-07 | 2027-09-14 | ALP-EPC-00EKA-PI-STR-0001 | G-CON-CWP CWP-09-PI-01 | 2027-11-29 | G-COM-MC-FF 00EKA IFC G-CON-CWP CWP-09-PI-01 IFC G-CON-IWP CWP-09-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10HSB-CM-OMM-0001 | Ammonia Storage and Supply - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-07-06 | 2027-08-17 |  | 2027-08-31 | 2027-09-14 | capacity commissioning | G-COM-SC-FF 10HSB | 2028-07-24 | G-COM-SC-FF 10HSB IFR G-OPS-HO-FF 10HSB IFC
8 | ALP-EPC-00000-HS-RPT-0005 | Explosion Protection Document | ATEX 2014/34/EU, workplace directive | EPC | hse | RPT | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0008 is NONE, IFR needs it at IFR |  | 2027-08-04 | 2027-08-25 |  | 2027-09-08 | 2027-09-15 | capacity hse
8 | ALP-EPC-00UBA-IC-LOP-0001 | Electrical Building and Emergency Power - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-IC-ELY-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-03 | 2027-09-08 |  | 2027-09-08 | 2027-09-15 | ALP-EPC-00UBA-IC-ELY-0002 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
8 | ALP-I08-00CJG-ME-PRC-0001 | BOP Safety Instrumented System - Supplier Installation and Erection Manual | IEC 61511 | I08 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-15 | 2027-08-05 |  | 2027-08-19 | 2027-09-16 | PO MR-IC-008 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFR
8 | ALP-I09-00CKA-EL-WIR-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Electrical Schematics and Wiring Diagrams |  | I09 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-07-01 | 2027-07-22 |  | 2027-08-05 | 2027-09-16 | PO MR-IC-009 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-COM-MC-FF 00CKA IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
8 | ALP-EPC-00UGA-IC-LOP-0001 | Water Treatment and Effluents - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR |  | 2027-07-28 | 2027-09-10 |  | 2027-09-10 | 2027-09-17 | capacity i_and_c | G-CON-CWP CWP-07-IC-01 | 2028-03-20 | G-CON-CWP CWP-07-IC-01 IFC G-CON-IWP CWP-07-IC-01 IFC
8 | ALP-EPC-00UGA-IC-LOP-0002 | Water Treatment and Effluents - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-04 | 2027-09-13 |  | 2027-09-13 | 2027-09-20 | ALP-EPC-00UGA-IC-ELY-0001 | G-CON-CWP CWP-07-IC-01 | 2028-03-20 | G-CON-CWP CWP-07-IC-01 IFC G-CON-IWP CWP-07-IC-01 IFC
8 | ALP-EPC-20UMB-IC-LOP-0002 | Power Block - ST and Condenser - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-10 | 2027-09-13 |  | 2027-09-13 | 2027-09-20 | capacity i_and_c | G-CON-CWP CWP-02-IC-01 | 2028-03-27 | G-CON-CWP CWP-02-IC-01 IFC G-CON-IWP CWP-02-IC-01 IFC
8 | ALP-M02-20LCB-ME-PRC-0001 | Condensate Extraction Pumps - Supplier Installation and Erection Manual |  | M02 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-19 | 2027-08-09 |  | 2027-08-23 | 2027-09-20 | PO MR-ME-002 | G-CON-CWP CWP-02-ME-01 | 2027-12-20 | G-CON-CWP CWP-02-ME-01 IFR
8 | ALP-M10-00QJA-ME-TRP-0001 | Nitrogen, Hydrogen and CO2 Supply - Factory Acceptance Test Report |  | M10 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-31 | 2027-09-07 |  | 2027-09-21 | 2027-09-21 | PO MR-ME-010 | G-PRC-SHP MR-ME-010 | 2027-10-05 | G-PRC-SHP MR-ME-010 ACCEPTED
8 | ALP-EPC-00UQA-EL-ELY-0002 | BOP Utilities - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-08-25 |  | 2027-09-08 | 2027-09-22 | ALP-EPC-00UQA-PI-PPL-0003 | G-CON-CWP CWP-08-EL-01 | 2028-01-10 | G-CON-CWP CWP-08-EL-01 IFC G-CON-IWP CWP-08-EL-01 IFC
8 | ALP-I08-00CJG-IC-LOG-0001 | BOP Safety Instrumented System - Supplier Logic Diagrams | IEC 61511 | I08 | i_and_c | LOG | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-01 | 2027-07-29 |  | 2027-08-12 | 2027-09-22 | PO MR-IC-008
8 | ALP-P04-00PAB-ME-MDB-0001 | GRP CW Pipes and Fittings - Manufacturing Record Book and Conformity Certificates |  | P04 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-MRQ-0004 is NONE, IFR needs it at IFR |  | 2027-07-14 | 2027-07-28 |  | 2027-07-28 | 2027-09-22 | PO MR-PI-004 | G-PRC-SHP MR-PI-004 | 2027-08-11 | G-PRC-SHP MR-PI-004 IFR
8 | ALP-M12-00GBA-ME-TST-0001 | Water Treatment Package - Factory Acceptance Test Procedure | SWRO, demin, condensate polishing | M12 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-22 | 2027-08-12 |  | 2027-09-09 | 2027-09-23 | PO MR-ME-012 | G-PRC-FAT MR-ME-012 | 2027-11-04 | G-PRC-FAT MR-ME-012 ACCEPTED
8 | ALP-EPC-00UEG-EL-ELY-0002 | LDO Tank Farm and Unloading - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-07-19 | 2027-08-30 |  | 2027-09-13 | 2027-09-27 | capacity electrical | G-CON-CWP CWP-10-EL-01 | 2028-01-24 | G-CON-CWP CWP-10-EL-01 IFC G-CON-IWP CWP-10-EL-01 IFC
8 | ALP-EPC-10UHN-EL-ELY-0001 | Stack Foundation - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UHN-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-03-16 | 2027-08-30 |  | 2027-09-13 | 2027-09-27 | capacity electrical | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
8 | ALP-EPC-20UMB-IC-LOP-0001 | Power Block - ST and Condenser - Loop and Connection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-LST-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBY-IC-CBL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBY-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-09 | 2027-09-20 |  | 2027-09-20 | 2027-09-27 | capacity i_and_c | G-CON-CWP CWP-02-IC-01 | 2028-03-27 | G-CON-CWP CWP-02-IC-01 IFC G-CON-IWP CWP-02-IC-01 IFC
8 | ALP-I07-00CYA-ME-TRP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Factory Acceptance Test Report |  | I07 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-06 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-IC-007 | G-PRC-SHP MR-IC-007 | 2027-10-11 | G-PRC-SHP MR-IC-007 ACCEPTED
8 | ALP-M19-10HAN-ME-MDB-0001 | HRSG Blowdown and Drain Tanks - Manufacturing Record Book and Conformity Certificates |  | M19 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-19 | 2027-08-02 |  | 2027-08-02 | 2027-09-27 | PO MR-ME-019 | G-PRC-SHP MR-ME-019 | 2027-08-16 | G-PRC-SHP MR-ME-019 IFR
8 | ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-07-27 | 2027-09-21 |  | 2027-09-21 | 2027-09-28 | ALP-EPC-00EKC-PI-STR-0001 | G-CON-CWP CWP-09-PI-01 | 2027-11-29 | G-COM-MC-FF 00EKC IFC G-CON-CWP CWP-09-PI-01 IFC G-CON-IWP CWP-09-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10UMA-IC-LOP-0002 | Power Block - GT and HRSG - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-11 | 2027-09-22 |  | 2027-09-22 | 2027-09-29 | ALP-EPC-10UMA-IC-ELY-0001 | G-CON-CWP CWP-01-IC-01 | 2028-02-07 | G-CON-CWP CWP-01-IC-01 IFC G-CON-IWP CWP-01-IC-01 IFC
8 | ALP-M06-00PAH-ME-TRP-0001 | Condenser Tube Cleaning System - Factory Acceptance Test Report |  | M06 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-08 | 2027-09-15 |  | 2027-09-29 | 2027-09-29 | PO MR-ME-006 | G-PRC-SHP MR-ME-006 | 2027-10-13 | G-PRC-SHP MR-ME-006 ACCEPTED
8 | ALP-M11-00QCA-ME-PRC-0001 | Chemical Dosing Skid - Supplier Installation and Erection Manual |  | M11 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-28 | 2027-08-18 |  | 2027-09-01 | 2027-09-29 | PO MR-ME-011 | G-CON-CWP CWP-08-ME-01 | 2027-11-01 | G-CON-CWP CWP-08-ME-01 IFR
8 | ALP-EPC-00000-IC-LST-0003 | Interlock and Trip List |  | EPC | i_and_c | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-08-11 | 2027-09-02 |  | 2027-09-16 | 2027-09-30 | capacity i_and_c | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
8 | ALP-I09-00CKA-ME-LST-0001 | Operator Training Simulator, Historian and Performance Monitoring - Spare Parts and Special Tools Lists |  | I09 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-15 | 2027-08-05 |  | 2027-08-19 | 2027-09-30 | PO MR-IC-009
8 | ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-07-26 | 2027-09-24 |  | 2027-09-24 | 2027-10-01 | capacity piping | G-CON-CWP CWP-10-PI-01 | 2027-12-27 | G-COM-MC-FF 00EGC IFC G-CON-CWP CWP-10-PI-01 IFC G-CON-IWP CWP-10-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-I02-00CQA-ME-TRP-0001 | Continuous Emission Monitoring System - Factory Acceptance Test Report |  | I02 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-10 | 2027-09-17 |  | 2027-10-01 | 2027-10-01 | PO MR-IC-002 | G-PRC-SHP MR-IC-002 | 2027-10-15 | G-PRC-SHP MR-IC-002 ACCEPTED
8 | ALP-EPC-00UQA-IC-LOP-0002 | BOP Utilities - Junction Box and Cabinet Interconnection Diagrams |  | EPC | i_and_c | LOP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-IC-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-08-16 | 2027-09-27 |  | 2027-09-27 | 2027-10-04 | ALP-EPC-00UQA-IC-ELY-0001 | G-CON-CWP CWP-08-IC-01 | 2028-02-21 | G-CON-CWP CWP-08-IC-01 IFC G-CON-IWP CWP-08-IC-01 IFC
8 | ALP-I03-00QUA-ME-TRP-0001 | Steam/Water Analysis System - Factory Acceptance Test Report |  | I03 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-14 | 2027-09-21 |  | 2027-10-05 | 2027-10-05 | PO MR-IC-003 | G-PRC-SHP MR-IC-003 | 2027-10-19 | G-PRC-SHP MR-IC-003 ACCEPTED
8 | ALP-EPC-00UBF-EL-ELY-0001 | Transformer Bays - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBF-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-08-10 | 2027-09-08 |  | 2027-09-22 | 2027-10-06 | capacity electrical | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
8 | ALP-EPC-00UPC-EL-ELY-0002 | CW Pump House and Onshore CW - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-08-10 | 2027-09-08 |  | 2027-09-22 | 2027-10-06 | capacity electrical | G-CON-CWP CWP-05-EL-01 | 2028-01-31 | G-CON-CWP CWP-05-EL-01 IFC G-CON-IWP CWP-05-EL-01 IFC
8 | ALP-EPC-10UHA-EL-ELY-0001 | HRSG Foundations and Structures - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UHA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-08-10 | 2027-09-09 |  | 2027-09-23 | 2027-10-07 | capacity electrical | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
8 | ALP-EPC-10UMA-EL-ELY-0003 | Gas Turbine Hall - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-CV-FND-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-08-09 | 2027-09-09 |  | 2027-09-23 | 2027-10-07 | capacity electrical | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
8 | ALP-H01-00SAA-ME-MDB-0001 | HVAC Plant and Equipment - Manufacturing Record Book and Conformity Certificates |  | H01 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-29 | 2027-08-12 |  | 2027-08-12 | 2027-10-07 | PO MR-HV-001 | G-PRC-SHP MR-HV-001 | 2027-08-26 | G-PRC-SHP MR-HV-001 IFR
8 | ALP-M01-10LAC-ME-TRP-0001 | Boiler Feed Pumps - Factory Acceptance Test Report |  | M01 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-16 | 2027-09-23 |  | 2027-10-07 | 2027-10-07 | PO MR-ME-001 | G-PRC-SHP MR-ME-001 | 2027-10-21 | G-PRC-SHP MR-ME-001 ACCEPTED
8 | ALP-M03-00PAC-ME-PRC-0001 | CW Pumps - Supplier Installation and Erection Manual |  | M03 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-05 | 2027-08-26 |  | 2027-09-09 | 2027-10-07 | PO MR-ME-003 | G-CON-CWP CWP-05-ME-01 | 2027-12-20 | G-CON-CWP CWP-05-ME-01 IFR
8 | ALP-M09-00QHA-ME-TRP-0001 | Auxiliary Boiler - Factory Acceptance Test Report |  | M09 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-16 | 2027-09-23 |  | 2027-10-07 | 2027-10-07 | PO MR-ME-009 | G-PRC-SHP MR-ME-009 | 2027-10-21 | G-PRC-SHP MR-ME-009 ACCEPTED
8 | ALP-M14-00GNA-ME-MDB-0001 | Waste Water and Sanitary Treatment Packages - Manufacturing Record Book and Conformity Certificates |  | M14 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-29 | 2027-08-12 |  | 2027-08-12 | 2027-10-07 | PO MR-ME-014 | G-PRC-SHP MR-ME-014 | 2027-08-26 | G-PRC-SHP MR-ME-014 IFR
8 | ALP-M15-00EKA-ME-TRP-0001 | Gas Receiving and Metering Station - Factory Acceptance Test Report |  | M15 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-16 | 2027-09-23 |  | 2027-10-07 | 2027-10-07 | PO MR-ME-015 | G-PRC-SHP MR-ME-015 | 2027-10-21 | G-PRC-SHP MR-ME-015 ACCEPTED
8 | ALP-EPC-00UPC-EL-ELY-0003 | CW Pump House - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-08-11 | 2027-09-10 |  | 2027-09-24 | 2027-10-08 | capacity electrical | G-CON-CWP CWP-05-EL-01 | 2028-01-31 | G-CON-CWP CWP-05-EL-01 IFC G-CON-IWP CWP-05-EL-01 IFC
8 | ALP-M04-00PAA-ME-TRP-0001 | Travelling Band Screens and Trash Rakes - Factory Acceptance Test Report |  | M04 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-17 | 2027-09-24 |  | 2027-10-08 | 2027-10-08 | PO MR-ME-004 | G-PRC-SHP MR-ME-004 | 2027-10-22 | G-PRC-SHP MR-ME-004 ACCEPTED
8 | ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QEA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-07-21 | 2027-10-04 |  | 2027-10-04 | 2027-10-11 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00QEA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M05-00PBA-ME-TRP-0001 | Electro-Chlorination Package - Factory Acceptance Test Report |  | M05 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-20 | 2027-09-27 |  | 2027-10-11 | 2027-10-11 | PO MR-ME-005 | G-PRC-SHP MR-ME-005 | 2027-10-25 | G-PRC-SHP MR-ME-005 ACCEPTED
8 | ALP-EPC-00000-HS-STU-0003 | Fire and Gas Detector Mapping Study |  | EPC | hse | STU | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0008 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0009 is NONE, IFR needs it at IFR |  | 2027-08-10 | 2027-09-15 |  | 2027-09-29 | 2027-10-13 | capacity hse
8 | ALP-I08-00CJG-ME-TRP-0001 | BOP Safety Instrumented System - Factory Acceptance Test Report | IEC 61511 | I08 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-09-30 |  | 2027-10-14 | 2027-10-14 | PO MR-IC-008 | G-PRC-SHP MR-IC-008 | 2027-10-28 | G-PRC-SHP MR-IC-008 ACCEPTED
8 | ALP-M13-00GHA-ME-OMM-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Operation and Maintenance Manual |  | M13 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-16 | 2027-05-28 |  | 2027-06-11 | 2027-10-15 | PO MR-ME-013 | G-COM-SC-FF 00GHA | 2028-07-24 | G-COM-SC-FF 00GHA IFR G-COM-SC-FF 00GKA IFR G-OPS-HO-FF 00GHA IFC G-OPS-HO-FF 00GKA IFC
8 | ALP-EPC-00EGA-IC-CEM-0001 | LDO Unloading - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-08-20 | 2027-09-13 | 2027-10-11 | 2027-10-11 | 2027-10-18 | capacity i_and_c
8 | ALP-M02-20LCB-ME-TRP-0001 | Condensate Extraction Pumps - Factory Acceptance Test Report |  | M02 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-27 | 2027-10-04 |  | 2027-10-18 | 2027-10-18 | PO MR-ME-002 | G-PRC-SHP MR-ME-002 | 2027-11-01 | G-PRC-SHP MR-ME-002 ACCEPTED
8 | ALP-EPC-00000-HS-PLN-0005 | Emergency Response Plan | construction and operation | EPC | hse | PLN | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0010 is NONE, IFR needs it at IFR |  | 2027-08-17 | 2027-09-14 | 2027-10-12 | 2027-10-12 | 2027-10-19 | ALP-EPC-00000-HS-HAZ-0010
8 | ALP-EPC-00UGA-EL-ELY-0002 | Water Treatment and Effluents - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-08-20 | 2027-09-21 |  | 2027-10-05 | 2027-10-19 | ALP-EPC-00UGA-EL-ELY-0001 | G-CON-CWP CWP-07-EL-01 | 2028-02-21 | G-CON-CWP CWP-07-EL-01 IFC G-CON-IWP CWP-07-EL-01 IFC
8 | ALP-EPC-00EKC-IC-CEM-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-08-10 | 2027-09-15 | 2027-10-13 | 2027-10-13 | 2027-10-20 | capacity i_and_c
8 | ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR input ALP-EPC-00SGA-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-08-18 | 2027-10-13 |  | 2027-10-13 | 2027-10-20 | ALP-EPC-00SGA-PI-STR-0001 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-COM-MC-FF 00SGA IFC G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR input ALP-EPC-00PGA-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-10-14 |  | 2027-10-14 | 2027-10-21 | ALP-EPC-00PGA-PI-STR-0001 | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00PGA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M12-00GBA-ME-PRC-0001 | Water Treatment Package - Supplier Installation and Erection Manual | SWRO, demin, condensate polishing | M12 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-09-09 |  | 2027-09-23 | 2027-10-21 | PO MR-ME-012 | G-CON-CWP CWP-07-ME-01 | 2027-12-27 | G-CON-CWP CWP-07-ME-01 IFR
8 | ALP-M20-00SGA-ME-MDB-0001 | Fire Pumps and Fire Protection Systems - Manufacturing Record Book and Conformity Certificates |  | M20 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-12 | 2027-08-26 |  | 2027-08-26 | 2027-10-21 | PO MR-ME-020 | G-PRC-SHP MR-ME-020 | 2027-09-09 | G-PRC-SHP MR-ME-020 IFR
8 | ALP-EPC-00SAA-PI-SUP-0001 | HVAC - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-09-09 | 2027-10-15 |  | 2027-10-15 | 2027-10-22 | ALP-EPC-00SAA-PI-ISO-0001 | G-CON-CWP CWP-03-HV-01 | 2027-10-11 | G-COM-MC-FF 00SAA IFC G-CON-CWP CWP-03-HV-01 IFC G-CON-IWP CWP-03-HV-01 IFC
8 | ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00SGC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-08-13 | 2027-10-15 |  | 2027-10-15 | 2027-10-22 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00SGC IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-20UMB-EL-ELY-0003 | Steam Turbine Hall - Earthing and Lightning Protection Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-CV-FND-0002 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0003 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-STU-0004 is NONE, IFR needs it at IFR |  | 2027-08-25 | 2027-09-27 |  | 2027-10-11 | 2027-10-25 | capacity electrical | G-CON-CWP CWP-02-EL-01 | 2028-02-28 | G-CON-CWP CWP-02-EL-01 IFC G-CON-IWP CWP-02-EL-01 IFC
8 | ALP-EPC-00000-EL-LST-0004 | Hazardous Area Electrical Equipment Register | Ex | EPC | electrical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0008 is NONE, IFR needs it at IFR |  | 2027-09-08 | 2027-09-29 |  | 2027-10-13 | 2027-10-27 | capacity electrical | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
8 | ALP-EPC-00LBG-IC-CEM-0001 | Auxiliary Steam - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-22 | 2027-10-20 | 2027-10-20 | 2027-10-27 | capacity i_and_c
8 | ALP-EPC-00QJA-IC-CEM-0001 | Nitrogen Supply - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-22 | 2027-10-20 | 2027-10-20 | 2027-10-27 | capacity i_and_c
8 | ALP-EPC-00QJB-IC-CEM-0001 | Hydrogen and CO2 Supply - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-22 | 2027-10-20 | 2027-10-20 | 2027-10-27 | capacity i_and_c
8 | ALP-M11-00QCA-ME-TRP-0001 | Chemical Dosing Skid - Factory Acceptance Test Report |  | M11 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-06 | 2027-10-13 |  | 2027-10-27 | 2027-10-27 | PO MR-ME-011 | G-PRC-SHP MR-ME-011 | 2027-11-10 | G-PRC-SHP MR-ME-011 ACCEPTED
8 | ALP-EPC-00EGB-IC-CEM-0001 | LDO Storage - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-23 | 2027-10-21 | 2027-10-21 | 2027-10-28 | capacity i_and_c
8 | ALP-EPC-00EGC-IC-CEM-0001 | LDO Forwarding and Treatment - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-23 | 2027-10-21 | 2027-10-21 | 2027-10-28 | capacity i_and_c
8 | ALP-EPC-00QCA-IC-CEM-0001 | Chemical Dosing - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-23 | 2027-10-21 | 2027-10-21 | 2027-10-28 | capacity i_and_c
8 | ALP-EPC-00QEA-IC-CEM-0001 | Compressed Air - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-23 | 2027-10-21 | 2027-10-21 | 2027-10-28 | capacity i_and_c
8 | ALP-EPC-00QHA-IC-CEM-0001 | Auxiliary Boiler - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-23 | 2027-10-21 | 2027-10-21 | 2027-10-28 | capacity i_and_c
8 | ALP-EPC-00QUA-IC-CEM-0001 | Sampling and SWAS - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-23 | 2027-10-21 | 2027-10-21 | 2027-10-28 | capacity i_and_c
8 | ALP-M07-00PGA-ME-MDB-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Manufacturing Record Book and Conformity Certificates |  | M07 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-09-02 |  | 2027-09-02 | 2027-10-28 | PO MR-ME-007 | G-PRC-SHP MR-ME-007 | 2027-09-16 | G-PRC-SHP MR-ME-007 IFR
8 | ALP-M08-00QEA-ME-MDB-0001 | Air Compressors and Dryers - Manufacturing Record Book and Conformity Certificates |  | M08 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-09-02 |  | 2027-09-02 | 2027-10-28 | PO MR-ME-008 | G-PRC-SHP MR-ME-008 | 2027-09-16 | G-PRC-SHP MR-ME-008 IFR
8 | ALP-EPC-00EKA-IC-CEM-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-24 | 2027-10-22 | 2027-10-22 | 2027-10-29 | capacity i_and_c
8 | ALP-EPC-00SGA-IC-CEM-0001 | Fire Water System - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-02 | 2027-09-24 | 2027-10-22 | 2027-10-22 | 2027-10-29 | capacity i_and_c
8 | ALP-M18-10HSB-ME-MDB-0001 | Aqueous Ammonia Storage and Forwarding - Manufacturing Record Book and Conformity Certificates |  | M18 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-23 | 2027-09-06 |  | 2027-09-06 | 2027-11-01 | PO MR-ME-018 | G-PRC-SHP MR-ME-018 | 2027-09-20 | G-PRC-SHP MR-ME-018 IFR
8 | ALP-EPC-00000-IC-SPC-0006 | BOP SIS - Safety Requirements Specification | IEC 61511 | EPC | i_and_c | SPC | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-09-29 | 2027-10-27 | 2027-10-27 | 2027-11-03 | capacity i_and_c
8 | ALP-EPC-20UMB-EL-ELY-0002 | Power Block - ST and Condenser - Cable Routing, Tray and Trench Layouts |  | EPC | electrical | ELY | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-EL-ELY-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-10-07 |  | 2027-10-21 | 2027-11-04 | ALP-EPC-20UMB-EL-ELY-0001 | G-CON-CWP CWP-02-EL-01 | 2028-02-28 | G-CON-CWP CWP-02-EL-01 IFC G-CON-IWP CWP-02-EL-01 IFC
8 | ALP-M03-00PAC-ME-TRP-0001 | CW Pumps - Factory Acceptance Test Report |  | M03 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-14 | 2027-10-21 |  | 2027-11-04 | 2027-11-04 | PO MR-ME-003 | G-PRC-SHP MR-ME-003 | 2027-11-18 | G-PRC-SHP MR-ME-003 ACCEPTED
8 | ALP-M16-00EGA-ME-MDB-0001 | LDO Unloading and Forwarding / Treatment Skids - Manufacturing Record Book and Conformity Certificates |  | M16 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-26 | 2027-09-09 |  | 2027-09-09 | 2027-11-04 | PO MR-ME-016 | G-PRC-SHP MR-ME-016 | 2027-09-23 | G-PRC-SHP MR-ME-016 IFR
8 | ALP-M21-00SMA-ME-MDB-0001 | EOT Cranes - Manufacturing Record Book and Conformity Certificates |  | M21 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-26 | 2027-09-09 |  | 2027-09-09 | 2027-11-04 | PO MR-ME-021 | G-PRC-SHP MR-ME-021 | 2027-09-23 | G-PRC-SHP MR-ME-021 IFR
8 | ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-08-26 | 2027-10-29 |  | 2027-10-29 | 2027-11-05 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-WS 10LAB IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M19-10HAN-ME-OMM-0001 | HRSG Blowdown and Drain Tanks - Supplier Operation and Maintenance Manual |  | M19 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-10 | 2027-06-21 |  | 2027-07-05 | 2027-11-08 | PO MR-ME-019 | G-COM-SC-WS 10HAN | 2028-09-25 | G-COM-SC-WS 10HAN IFR G-OPS-HO-WS 10HAN IFC
8 | ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00LBG-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00LBG-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-09-07 | 2027-11-02 |  | 2027-11-02 | 2027-11-09 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-WS 00LBG IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00SGC-IC-CEM-0001 | Deluge, Spray and Foam Systems - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-13 | 2027-10-05 | 2027-11-02 | 2027-11-02 | 2027-11-09 | capacity i_and_c
8 | ALP-EPC-00LBG-CM-OMM-0001 | Auxiliary Steam - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-10-13 |  | 2027-10-27 | 2027-11-10 | capacity commissioning | G-COM-SC-WS 00LBG | 2028-09-25 | G-COM-SC-WS 00LBG IFR G-OPS-HO-WS 00LBG IFC
8 | ALP-EPC-10HAN-CM-OMM-0001 | HRSG Blowdown and Drains - Operating Procedures | English / Turkish; EPC tanks and headers | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-01 | 2027-10-13 |  | 2027-10-27 | 2027-11-10 | ALP-EPC-10HAN-CM-CMP-0001 | G-COM-SC-WS 10HAN | 2028-09-25 | G-COM-SC-WS 10HAN IFR G-OPS-HO-WS 10HAN IFC
8 | ALP-EPC-10LAB-CM-OMM-0001 | Feedwater Piping - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-03 | 2027-10-15 |  | 2027-10-29 | 2027-11-12 | capacity commissioning | G-COM-SC-WS 10LAB | 2028-09-25 | G-COM-SC-WS 10LAB IFR G-OPS-HO-WS 10LAB IFC
8 | ALP-EPC-10LAC-CM-OMM-0001 | Boiler Feed Pumps - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-03 | 2027-10-15 |  | 2027-10-29 | 2027-11-12 | ALP-EPC-10LAC-CM-CMP-0001 | G-COM-SC-WS 10LAC | 2028-09-25 | G-COM-SC-WS 10LAC IFR G-OPS-HO-WS 10LAC IFC
8 | ALP-EPC-10LAE-CM-OMM-0001 | HP Attemperation Spray Water - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-03 | 2027-10-15 |  | 2027-10-29 | 2027-11-12 | ALP-EPC-10LAE-CM-CMP-0001 | G-COM-SC-WS 10LAE | 2028-09-25 | G-COM-SC-WS 10LAE IFR G-OPS-HO-WS 10LAE IFC
8 | ALP-EPC-10LAF-CM-OMM-0001 | Reheat Attemperation Spray Water - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-03 | 2027-10-15 |  | 2027-10-29 | 2027-11-12 | ALP-EPC-10LAF-CM-CMP-0001 | G-COM-SC-WS 10LAF | 2028-09-25 | G-COM-SC-WS 10LAF IFR G-OPS-HO-WS 10LAF IFC
8 | ALP-EPC-10HAN-IC-CEM-0001 | HRSG Blowdown and Drains - Cause and Effect Matrix | EPC tanks and headers | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-02 | 2027-10-11 | 2027-11-08 | 2027-11-08 | 2027-11-15 | capacity i_and_c
8 | ALP-M10-00QJA-ME-MDB-0001 | Nitrogen, Hydrogen and CO2 Supply - Manufacturing Record Book and Conformity Certificates |  | M10 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-07 | 2027-09-21 |  | 2027-09-21 | 2027-11-16 | PO MR-ME-010 | G-PRC-SHP MR-ME-010 | 2027-10-05 | G-PRC-SHP MR-ME-010 IFR
8 | ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR input ALP-EPC-00QHA-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-09-07 | 2027-11-11 |  | 2027-11-11 | 2027-11-18 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00QHA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10LAB-IC-CEM-0001 | Feedwater Piping - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-10-14 | 2027-11-11 | 2027-11-11 | 2027-11-18 | capacity i_and_c
8 | ALP-H01-00SAA-ME-OMM-0001 | HVAC Plant and Equipment - Supplier Operation and Maintenance Manual |  | H01 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-HV-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-20 | 2027-07-01 |  | 2027-07-15 | 2027-11-18 | PO MR-HV-001 | G-COM-SC-FF 00SAA | 2028-07-24 | G-COM-SC-FF 00SAA IFR G-OPS-HO-FF 00SAA IFC
8 | ALP-M12-00GBA-ME-TRP-0001 | Water Treatment Package - Factory Acceptance Test Report | SWRO, demin, condensate polishing | M12 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-28 | 2027-11-04 |  | 2027-11-18 | 2027-11-18 | PO MR-ME-012 | G-PRC-SHP MR-ME-012 | 2027-12-02 | G-PRC-SHP MR-ME-012 ACCEPTED
8 | ALP-M14-00GNA-ME-OMM-0001 | Waste Water and Sanitary Treatment Packages - Supplier Operation and Maintenance Manual |  | M14 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-20 | 2027-07-01 |  | 2027-07-15 | 2027-11-18 | PO MR-ME-014 | G-COM-SC-FF 00GMA | 2028-07-24 | G-COM-SC-FF 00GMA IFR G-COM-SC-FF 00GNA IFR G-COM-SC-FF 00GUA IFR G-OPS-HO-FF 00GMA IFC G-OPS-HO-FF 00GNA IFC G-OPS-HO-FF 00GUA IFC
8 | ALP-EPC-10HSB-IC-CEM-0001 | Ammonia Storage and Supply - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-10-15 | 2027-11-12 | 2027-11-12 | 2027-11-19 | capacity i_and_c
8 | ALP-EPC-10LBA-CM-OMM-0001 | Main Steam Piping - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-13 | 2027-10-25 |  | 2027-11-08 | 2027-11-22 | ALP-EPC-10LBA-CM-CMP-0001 | G-COM-SC-WS 10LBA | 2028-09-25 | G-COM-SC-WS 10LBA IFR G-OPS-HO-WS 10LBA IFC
8 | ALP-I07-00CYA-ME-MDB-0001 | Telecom, CCTV, Access Control and Perimeter Security - Manufacturing Record Book and Conformity Certificates |  | I07 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-13 | 2027-09-27 |  | 2027-09-27 | 2027-11-22 | PO MR-IC-007 | G-PRC-SHP MR-IC-007 | 2027-10-11 | G-PRC-SHP MR-IC-007 IFR
8 | ALP-EPC-00EGA-PI-ISO-0001 | LDO Unloading - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00EGA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-07-09 | 2027-11-16 |  | 2027-11-16 | 2027-11-23 | capacity piping | G-CON-CWP CWP-10-PI-01 | 2027-12-27 | G-COM-MC-FF 00EGA IFC G-CON-CWP CWP-10-PI-01 IFC G-CON-IWP CWP-10-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10LBB-CM-OMM-0001 | Hot Reheat Piping - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-14 | 2027-10-26 |  | 2027-11-09 | 2027-11-23 | ALP-EPC-10LBB-CM-CMP-0001 | G-COM-SC-WS 10LBB | 2028-09-25 | G-COM-SC-WS 10LBB IFR G-OPS-HO-WS 10LBB IFC
8 | ALP-EPC-10LBC-CM-OMM-0001 | Cold Reheat Piping - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-14 | 2027-10-26 |  | 2027-11-09 | 2027-11-23 | ALP-EPC-10LBC-CM-CMP-0001 | G-COM-SC-WS 10LBC | 2028-09-25 | G-COM-SC-WS 10LBC IFR G-OPS-HO-WS 10LBC IFC
8 | ALP-EPC-10LAC-IC-CEM-0001 | Boiler Feed Pumps - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-09-28 | 2027-10-20 | 2027-11-17 | 2027-11-17 | 2027-11-24 | capacity i_and_c
8 | ALP-M06-00PAH-ME-MDB-0001 | Condenser Tube Cleaning System - Manufacturing Record Book and Conformity Certificates |  | M06 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-15 | 2027-09-29 |  | 2027-09-29 | 2027-11-24 | PO MR-ME-006 | G-PRC-SHP MR-ME-006 | 2027-10-13 | G-PRC-SHP MR-ME-006 IFR
8 | ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR input ALP-EPC-10LAC-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-09-22 | 2027-11-18 |  | 2027-11-18 | 2027-11-25 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-WS 10LAC IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10LBD-CM-OMM-0001 | LP Steam Piping - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-16 | 2027-10-28 |  | 2027-11-11 | 2027-11-25 | ALP-EPC-10LBD-CM-CMP-0001 | G-COM-SC-WS 10LBD | 2028-09-25 | G-COM-SC-WS 10LBD IFR G-OPS-HO-WS 10LBD IFC
8 | ALP-EPC-20LCA-CM-OMM-0001 | Main Condensate Piping - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-16 | 2027-10-28 |  | 2027-11-11 | 2027-11-25 | ALP-EPC-20LCA-CM-CMP-0001 | G-COM-SC-WS 20LCA | 2028-09-25 | G-COM-SC-WS 20LCA IFR G-OPS-HO-WS 20LCA IFC
8 | ALP-EPC-00000-EL-BLK-0001 | Cable Block Diagrams, Part 1 of 2 |  | EPC | electrical | BLK | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-09-09 | 2027-10-22 | 2027-11-19 | 2027-11-19 | 2027-11-26 | capacity electrical
8 | ALP-I02-00CQA-ME-MDB-0001 | Continuous Emission Monitoring System - Manufacturing Record Book and Conformity Certificates |  | I02 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-17 | 2027-10-01 |  | 2027-10-01 | 2027-11-26 | PO MR-IC-002 | G-PRC-SHP MR-IC-002 | 2027-10-15 | G-PRC-SHP MR-IC-002 IFR
8 | ALP-EPC-10LAE-IC-CEM-0001 | HP Attemperation Spray Water - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-05 | 2027-10-26 | 2027-11-23 | 2027-11-23 | 2027-11-30 | capacity i_and_c
8 | ALP-EPC-20LCB-CM-OMM-0001 | Condensate Extraction Pumps - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-21 | 2027-11-02 |  | 2027-11-16 | 2027-11-30 | ALP-EPC-20LCB-CM-CMP-0001 | G-COM-SC-WS 20LCB | 2028-09-25 | G-COM-SC-WS 20LCB IFR G-OPS-HO-WS 20LCB IFC
8 | ALP-I03-00QUA-ME-MDB-0001 | Steam/Water Analysis System - Manufacturing Record Book and Conformity Certificates |  | I03 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-21 | 2027-10-05 |  | 2027-10-05 | 2027-11-30 | PO MR-IC-003 | G-PRC-SHP MR-IC-003 | 2027-10-19 | G-PRC-SHP MR-IC-003 IFR
8 | ALP-EPC-00000-CM-CMP-0003 | Grid Code Compliance Test Programme |  | EPC | commissioning | CMP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-STU-0006 is NONE, IFR needs it at IFR input ALP-IEC-10MKA-EL-RPT-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-10-27 | 2027-11-24 | 2027-11-24 | 2027-12-01 | ALP-EPC-00000-EL-STU-0006 | G-OWN-TOC 00000 | 2028-08-21 | G-OWN-TOC 00000 ACCEPTED
8 | ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-11-24 |  | 2027-11-24 | 2027-12-01 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00QCA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10LAF-IC-CEM-0001 | Reheat Attemperation Spray Water - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-07 | 2027-10-28 | 2027-11-25 | 2027-11-25 | 2027-12-02 | capacity i_and_c
8 | ALP-M01-10LAC-ME-MDB-0001 | Boiler Feed Pumps - Manufacturing Record Book and Conformity Certificates |  | M01 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-10-07 |  | 2027-10-07 | 2027-12-02 | PO MR-ME-001 | G-PRC-SHP MR-ME-001 | 2027-10-21 | G-PRC-SHP MR-ME-001 IFR
8 | ALP-M09-00QHA-ME-MDB-0001 | Auxiliary Boiler - Manufacturing Record Book and Conformity Certificates |  | M09 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-10-07 |  | 2027-10-07 | 2027-12-02 | PO MR-ME-009 | G-PRC-SHP MR-ME-009 | 2027-10-21 | G-PRC-SHP MR-ME-009 IFR
8 | ALP-M15-00EKA-ME-MDB-0001 | Gas Receiving and Metering Station - Manufacturing Record Book and Conformity Certificates |  | M15 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-10-07 |  | 2027-10-07 | 2027-12-02 | PO MR-ME-015 | G-PRC-SHP MR-ME-015 | 2027-10-21 | G-PRC-SHP MR-ME-015 IFR
8 | ALP-M20-00SGA-ME-OMM-0001 | Fire Pumps and Fire Protection Systems - Supplier Operation and Maintenance Manual |  | M20 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-03 | 2027-07-15 |  | 2027-07-29 | 2027-12-02 | PO MR-ME-020 | G-COM-SC-FF 00SGA | 2028-07-24 | G-COM-SC-FF 00SGA IFR G-COM-SC-FF 00SGC IFR G-OPS-HO-FF 00SGA IFC G-OPS-HO-FF 00SGC IFC
8 | ALP-EPC-10LBA-IC-CEM-0001 | Main Steam Piping - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-08 | 2027-10-29 | 2027-11-26 | 2027-11-26 | 2027-12-03 | capacity i_and_c
8 | ALP-M04-00PAA-ME-MDB-0001 | Travelling Band Screens and Trash Rakes - Manufacturing Record Book and Conformity Certificates |  | M04 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-24 | 2027-10-08 |  | 2027-10-08 | 2027-12-03 | PO MR-ME-004 | G-PRC-SHP MR-ME-004 | 2027-10-22 | G-PRC-SHP MR-ME-004 IFR
8 | ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HSB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-10-01 | 2027-11-29 |  | 2027-11-29 | 2027-12-06 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 10HSB IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10LBB-IC-CEM-0001 | Hot Reheat Piping - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-11 | 2027-11-01 | 2027-11-29 | 2027-11-29 | 2027-12-06 | capacity i_and_c
8 | ALP-M05-00PBA-ME-MDB-0001 | Electro-Chlorination Package - Manufacturing Record Book and Conformity Certificates |  | M05 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-27 | 2027-10-11 |  | 2027-10-11 | 2027-12-06 | PO MR-ME-005 | G-PRC-SHP MR-ME-005 | 2027-10-25 | G-PRC-SHP MR-ME-005 IFR
8 | ALP-EPC-10LBC-IC-CEM-0001 | Cold Reheat Piping - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-12 | 2027-11-03 | 2027-12-01 | 2027-12-01 | 2027-12-08 | capacity i_and_c
8 | ALP-EPC-20MAN-CM-OMM-0001 | Turbine Bypass Stations and Piping - Operating Procedures | English / Turkish | EPC | commissioning | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2027-09-29 | 2027-11-10 |  | 2027-11-24 | 2027-12-08 | ALP-EPC-20MAN-CM-CMP-0001 | G-COM-SC-WS 20MAN | 2028-09-25 | G-COM-SC-WS 20MAN IFR G-OPS-HO-WS 20MAN IFC
8 | ALP-EPC-00000-EL-BLK-0002 | Cable Block Diagrams, Part 2 of 2 |  | EPC | electrical | BLK | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-IOL-0001 is NONE, IFR needs it at IFR |  | 2027-09-21 | 2027-11-04 | 2027-12-02 | 2027-12-02 | 2027-12-09 | capacity electrical
8 | ALP-I08-00CJG-ME-MDB-0001 | BOP Safety Instrumented System - Manufacturing Record Book and Conformity Certificates | IEC 61511 | I08 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-30 | 2027-10-14 |  | 2027-10-14 | 2027-12-09 | PO MR-IC-008 | G-PRC-SHP MR-IC-008 | 2027-10-28 | G-PRC-SHP MR-IC-008 IFR
8 | ALP-I09-00CKA-ME-TST-0001 | Operator Training Simulator, Historian and Performance Monitoring - Factory Acceptance Test Procedure |  | I09 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-07 | 2027-10-28 |  | 2027-11-25 | 2027-12-09 | PO MR-IC-009 | G-PRC-FAT MR-IC-009 | 2028-01-20 | G-PRC-FAT MR-IC-009 ACCEPTED
8 | ALP-M07-00PGA-ME-OMM-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Operation and Maintenance Manual |  | M07 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-22 |  | 2027-08-05 | 2027-12-09 | PO MR-ME-007 | G-COM-SC-FF 00PGA | 2028-07-24 | G-COM-SC-FF 00PGA IFR G-OPS-HO-FF 00PGA IFC
8 | ALP-M08-00QEA-ME-OMM-0001 | Air Compressors and Dryers - Supplier Operation and Maintenance Manual |  | M08 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-22 |  | 2027-08-05 | 2027-12-09 | PO MR-ME-008 | G-COM-SC-FF 00QEA | 2028-07-24 | G-COM-SC-FF 00QEA IFR G-OPS-HO-FF 00QEA IFC
8 | ALP-EPC-10LBD-IC-CEM-0001 | LP Steam Piping - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-15 | 2027-11-05 | 2027-12-03 | 2027-12-03 | 2027-12-10 | capacity i_and_c
8 | ALP-M02-20LCB-ME-MDB-0001 | Condensate Extraction Pumps - Manufacturing Record Book and Conformity Certificates |  | M02 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-04 | 2027-10-18 |  | 2027-10-18 | 2027-12-13 | PO MR-ME-002 | G-PRC-SHP MR-ME-002 | 2027-11-01 | G-PRC-SHP MR-ME-002 IFR
8 | ALP-M18-10HSB-ME-OMM-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Operation and Maintenance Manual |  | M18 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-14 | 2027-07-26 |  | 2027-08-09 | 2027-12-13 | PO MR-ME-018 | G-COM-SC-FF 10HSB | 2028-07-24 | G-COM-SC-FF 10HSB IFR G-OPS-HO-FF 10HSB IFC
8 | ALP-EPC-00EGB-PI-ISO-0001 | LDO Storage - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-07-20 | 2027-12-07 |  | 2027-12-07 | 2027-12-14 | capacity piping | G-CON-CWP CWP-10-PI-01 | 2027-12-27 | G-COM-MC-FF 00EGB IFC G-CON-CWP CWP-10-PI-01 IFC G-CON-IWP CWP-10-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-20LCA-IC-CEM-0001 | Main Condensate Piping - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-19 | 2027-11-09 | 2027-12-07 | 2027-12-07 | 2027-12-14 | capacity i_and_c
8 | ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QJA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0002 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-PI-PPL-0003 is NONE, IFR needs it at IFR |  | 2027-10-13 | 2027-12-08 |  | 2027-12-08 | 2027-12-15 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00QJA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | EPC tanks and headers | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10HAN-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-10-14 | 2027-12-09 |  | 2027-12-09 | 2027-12-16 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10HAN IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-10LBA-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-10-13 | 2027-12-09 |  | 2027-12-09 | 2027-12-16 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LBA IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-10LBB-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-10-14 | 2027-12-09 |  | 2027-12-09 | 2027-12-16 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LBB IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M16-00EGA-ME-OMM-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Operation and Maintenance Manual |  | M16 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-17 | 2027-07-29 |  | 2027-08-12 | 2027-12-16 | PO MR-ME-016 | G-COM-SC-FF 00EGA | 2028-07-24 | G-COM-SC-FF 00EGA IFR G-COM-SC-FF 00EGC IFR G-OPS-HO-FF 00EGA IFC G-OPS-HO-FF 00EGC IFC
8 | ALP-M21-00SMA-ME-OMM-0001 | EOT Cranes - Supplier Operation and Maintenance Manual |  | M21 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SMA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-17 | 2027-07-29 |  | 2027-08-12 | 2027-12-16 | PO MR-ME-021 | G-COM-SC-FF 00SMA | 2028-07-24 | G-COM-SC-FF 00SMA IFR G-OPS-HO-FF 00SMA IFC
8 | ALP-EPC-20LCB-IC-CEM-0001 | Condensate Extraction Pumps - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-22 | 2027-11-15 | 2027-12-13 | 2027-12-13 | 2027-12-20 | capacity i_and_c
8 | ALP-M11-00QCA-ME-MDB-0001 | Chemical Dosing Skid - Manufacturing Record Book and Conformity Certificates |  | M11 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-13 | 2027-10-27 |  | 2027-10-27 | 2027-12-22 | PO MR-ME-011 | G-PRC-SHP MR-ME-011 | 2027-11-10 | G-PRC-SHP MR-ME-011 IFR
8 | ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-10LBC-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBC-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-10-14 | 2027-12-16 |  | 2027-12-16 | 2027-12-23 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LBC IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-20MAN-IC-CEM-0001 | Turbine Bypass Stations and Piping - Cause and Effect Matrix |  | EPC | i_and_c | CEM | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-IC-CNR-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-HS-HAZ-0007 is NONE, IFR needs it at IFR |  | 2027-10-28 | 2027-11-18 | 2027-12-16 | 2027-12-16 | 2027-12-23 | capacity i_and_c
8 | ALP-M10-00QJA-ME-OMM-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Operation and Maintenance Manual |  | M10 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-29 | 2027-08-10 |  | 2027-08-24 | 2027-12-28 | PO MR-ME-010 | G-COM-SC-FF 00QJA | 2028-07-24 | G-COM-SC-FF 00QJA IFR G-COM-SC-FF 00QJB IFR G-OPS-HO-FF 00QJA IFC G-OPS-HO-FF 00QJB IFC
8 | ALP-M03-00PAC-ME-MDB-0001 | CW Pumps - Manufacturing Record Book and Conformity Certificates |  | M03 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-21 | 2027-11-04 |  | 2027-11-04 | 2027-12-30 | PO MR-ME-003 | G-PRC-SHP MR-ME-003 | 2027-11-18 | G-PRC-SHP MR-ME-003 IFR
8 | ALP-EPC-00QUA-PI-ISO-0001 | Sampling and SWAS - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-07-20 | 2027-12-24 |  | 2027-12-24 | 2027-12-31 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-FF 00QUA IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-I07-00CYA-ME-OMM-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Operation and Maintenance Manual |  | I07 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CYA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-05 | 2027-08-16 |  | 2027-08-30 | 2028-01-03 | PO MR-IC-007 | G-COM-SC-FF 00CYA | 2028-07-24 | G-COM-SC-FF 00CYA IFR G-OPS-HO-FF 00CYA IFC
8 | ALP-EPC-00GBA-PI-ISO-0001 | Seawater Reverse Osmosis - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-10-29 | 2027-12-28 |  | 2027-12-28 | 2028-01-04 | capacity piping | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GBA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M06-00PAH-ME-OMM-0001 | Condenser Tube Cleaning System - Supplier Operation and Maintenance Manual |  | M06 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-07 | 2027-08-18 |  | 2027-09-01 | 2028-01-05 | PO MR-ME-006 | G-COM-SC-FF 00PAH | 2028-07-24 | G-COM-SC-FF 00PAH IFR G-OPS-HO-FF 00PAH IFC
8 | ALP-I09-00CKA-ME-PRC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Installation and Erection Manual |  | I09 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-11-04 | 2027-11-25 |  | 2027-12-09 | 2028-01-06 | PO MR-IC-009
8 | ALP-I02-00CQA-ME-OMM-0001 | Continuous Emission Monitoring System - Supplier Operation and Maintenance Manual |  | I02 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CQA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-09 | 2027-08-20 |  | 2027-09-03 | 2028-01-07 | PO MR-IC-002 | G-COM-SC-FF 00CQA | 2028-07-24 | G-COM-SC-FF 00CQA IFR G-OPS-HO-FF 00CQA IFC
8 | ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-10LBD-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LBD-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-11-02 | 2028-01-03 |  | 2028-01-03 | 2028-01-10 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LBD IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-I03-00QUA-ME-OMM-0001 | Steam/Water Analysis System - Supplier Operation and Maintenance Manual |  | I03 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-13 | 2027-08-24 |  | 2027-09-07 | 2028-01-11 | PO MR-IC-003 | G-COM-SC-FF 00QUA | 2028-07-24 | G-COM-SC-FF 00QUA IFR G-OPS-HO-FF 00QUA IFC
8 | ALP-EPC-00GCA-PI-ISO-0001 | Demineralisation - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-11-11 | 2028-01-06 |  | 2028-01-06 | 2028-01-13 | capacity piping | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GCA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M01-10LAC-ME-OMM-0001 | Boiler Feed Pumps - Supplier Operation and Maintenance Manual |  | M01 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-15 | 2027-08-26 |  | 2027-09-09 | 2028-01-13 | PO MR-ME-001 | G-COM-SC-WS 10LAC | 2028-09-25 | G-COM-SC-WS 10LAC IFR G-OPS-HO-WS 10LAC IFC
8 | ALP-M09-00QHA-ME-OMM-0001 | Auxiliary Boiler - Supplier Operation and Maintenance Manual |  | M09 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-15 | 2027-08-26 |  | 2027-09-09 | 2028-01-13 | PO MR-ME-009 | G-COM-SC-FF 00QHA | 2028-07-24 | G-COM-SC-FF 00QHA IFR G-OPS-HO-FF 00QHA IFC
8 | ALP-M12-00GBA-ME-MDB-0001 | Water Treatment Package - Manufacturing Record Book and Conformity Certificates | SWRO, demin, condensate polishing | M12 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-11-04 | 2027-11-18 |  | 2027-11-18 | 2028-01-13 | PO MR-ME-012 | G-PRC-SHP MR-ME-012 | 2027-12-02 | G-PRC-SHP MR-ME-012 IFR
8 | ALP-M15-00EKA-ME-OMM-0001 | Gas Receiving and Metering Station - Supplier Operation and Maintenance Manual |  | M15 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-15 | 2027-08-26 |  | 2027-09-09 | 2028-01-13 | PO MR-ME-015 | G-COM-SC-FF 00EKA | 2028-07-24 | G-COM-SC-FF 00EKA IFR G-OPS-HO-FF 00EKA IFC
8 | ALP-M04-00PAA-ME-OMM-0001 | Travelling Band Screens and Trash Rakes - Supplier Operation and Maintenance Manual |  | M04 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-16 | 2027-08-27 |  | 2027-09-10 | 2028-01-14 | PO MR-ME-004 | G-COM-SC-FF 00PAA | 2028-07-24 | G-COM-SC-FF 00PAA IFR G-OPS-HO-FF 00PAA IFC
8 | ALP-M05-00PBA-ME-OMM-0001 | Electro-Chlorination Package - Supplier Operation and Maintenance Manual |  | M05 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-19 | 2027-08-30 |  | 2027-09-13 | 2028-01-17 | PO MR-ME-005 | G-COM-SC-FF 00PBA | 2028-07-24 | G-COM-SC-FF 00PBA IFR G-OPS-HO-FF 00PBA IFC
8 | ALP-EPC-00GNA-PI-ISO-0001 | Waste Water Treatment - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GNA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-11-15 | 2028-01-11 |  | 2028-01-11 | 2028-01-18 | capacity piping | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GNA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00LDA-PI-ISO-0001 | Condensate Polishing - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00LDA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-11-17 | 2028-01-13 |  | 2028-01-13 | 2028-01-20 | capacity piping | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00LDA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-I08-00CJG-ME-OMM-0001 | BOP Safety Instrumented System - Supplier Operation and Maintenance Manual | IEC 61511 | I08 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJG-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-22 | 2027-09-02 |  | 2027-09-16 | 2028-01-20 | PO MR-IC-008 | G-COM-SC-FF 00CJG | 2028-07-24 | G-COM-SC-FF 00CJG IFR G-OPS-HO-FF 00CJG IFC
8 | ALP-EPC-00QJB-PI-ISO-0001 | Hydrogen and CO2 Supply - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00QJB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-11-18 | 2028-01-17 |  | 2028-01-17 | 2028-01-24 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-FF 00QJB IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M02-20LCB-ME-OMM-0001 | Condensate Extraction Pumps - Supplier Operation and Maintenance Manual |  | M02 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-26 | 2027-09-06 |  | 2027-09-20 | 2028-01-24 | PO MR-ME-002 | G-COM-SC-WS 20LCB | 2028-09-25 | G-COM-SC-WS 20LCB IFR G-OPS-HO-WS 20LCB IFC
8 | ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAE-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-11-24 | 2028-01-19 |  | 2028-01-19 | 2028-01-26 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LAE IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-10LAF-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-10LAF-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2027-11-24 | 2028-01-19 |  | 2028-01-19 | 2028-01-26 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LAF IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-00GHA-PI-ISO-0001 | Demineralised Water Storage and Distribution - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GHA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-11-24 | 2028-01-21 |  | 2028-01-21 | 2028-01-28 | capacity piping | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GHA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M11-00QCA-ME-OMM-0001 | Chemical Dosing Skid - Supplier Operation and Maintenance Manual |  | M11 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-04 | 2027-09-15 |  | 2027-09-29 | 2028-02-02 | PO MR-ME-011 | G-COM-SC-FF 00QCA | 2028-07-24 | G-COM-SC-FF 00QCA IFR G-OPS-HO-FF 00QCA IFC
8 | ALP-I09-00CKA-ME-TRP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Factory Acceptance Test Report |  | I09 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2028-01-13 | 2028-01-20 |  | 2028-02-03 | 2028-02-03 | PO MR-IC-009 | G-PRC-SHP MR-IC-009 | 2028-02-17 | G-PRC-SHP MR-IC-009 ACCEPTED
8 | ALP-EPC-00GUA-PI-ISO-0001 | Sanitary Waste Water Treatment - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00GUA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-12-08 | 2028-02-01 |  | 2028-02-01 | 2028-02-08 | capacity piping | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GUA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M03-00PAC-ME-OMM-0001 | CW Pumps - Supplier Operation and Maintenance Manual |  | M03 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-12 | 2027-09-23 |  | 2027-10-07 | 2028-02-10 | PO MR-ME-003 | G-COM-SC-FF 00PAC | 2028-07-24 | G-COM-SC-FF 00PAC IFR G-OPS-HO-FF 00PAC IFC
8 | ALP-EPC-00PAH-PI-ISO-0001 | Condenser Tube Cleaning - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-00PAH-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-12-09 | 2028-02-07 |  | 2028-02-07 | 2028-02-14 | capacity piping | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-FF 00PAH IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-M12-00GBA-ME-OMM-0001 | Water Treatment Package - Supplier Operation and Maintenance Manual | SWRO, demin, condensate polishing | M12 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-ME-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-26 | 2027-10-07 |  | 2027-10-21 | 2028-02-24 | PO MR-ME-012 | G-COM-SC-FF 00GBA | 2028-07-24 | G-COM-SC-FF 00GBA IFR G-COM-SC-FF 00GCA IFR G-COM-SC-FF 00LDA IFR G-OPS-HO-FF 00GBA IFC G-OPS-HO-FF 00GCA IFC G-OPS-HO-FF 00LDA IFC
8 | ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-20MAN-PI-STR-0001 is NONE, IFR needs it at IFR input ALP-EPC-20MAN-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-PPL-0001 is NONE, IFR needs it at IFR |  | 2027-12-31 | 2028-02-25 |  | 2028-02-25 | 2028-03-03 | ALP-EPC-20MAN-PI-STR-0001 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-WS 20MAN IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCB-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2028-01-05 | 2028-03-01 |  | 2028-03-01 | 2028-03-08 | ALP-EPC-20LCB-PI-STR-0001 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-WS 20LCB IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings |  | EPC | piping | ISO | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0002 is NONE, IFR needs it at IFR input ALP-EPC-20LCA-PR-PID-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-PI-PPL-0001 is NONE, IFR needs it at IFR input ALP-EPC-20LCA-PI-STR-0001 is NONE, IFR needs it at IFR |  | 2028-01-06 | 2028-03-02 |  | 2028-03-02 | 2028-03-09 | ALP-EPC-20LCA-PI-STR-0001 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-WS 20LCA IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC G-OPS-AB 00000 AB
8 | ALP-I09-00CKA-ME-MDB-0001 | Operator Training Simulator, Historian and Performance Monitoring - Manufacturing Record Book and Conformity Certificates |  | I09 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2028-01-20 | 2028-02-03 |  | 2028-02-03 | 2028-03-30 | PO MR-IC-009 | G-PRC-SHP MR-IC-009 | 2028-02-17 | G-PRC-SHP MR-IC-009 IFR
8 | ALP-EPC-00EGA-CM-MDB-0001 | LDO Unloading - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00EGA | 2028-06-26 | G-COM-MC-FF 00EGA IFR G-COM-SC-FF 00EGA IFR G-OPS-HO-FF 00EGA IFC
8 | ALP-EPC-00EGB-CM-MDB-0001 | LDO Storage - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00EGB | 2028-06-26 | G-COM-MC-FF 00EGB IFR G-COM-SC-FF 00EGB IFR G-OPS-HO-FF 00EGB IFC
8 | ALP-EPC-00EGC-CM-MDB-0001 | LDO Forwarding and Treatment - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00EGC | 2028-06-26 | G-COM-MC-FF 00EGC IFR G-COM-SC-FF 00EGC IFR G-OPS-HO-FF 00EGC IFC
8 | ALP-EPC-00EKA-CM-MDB-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00EKA | 2028-06-26 | G-COM-MC-FF 00EKA IFR G-COM-SC-FF 00EKA IFR G-OPS-HO-FF 00EKA IFC
8 | ALP-EPC-00EKC-CM-MDB-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00EKC | 2028-06-26 | G-COM-MC-FF 00EKC IFR G-COM-SC-FF 00EKC IFR G-OPS-HO-FF 00EKC IFC
8 | ALP-EPC-00GBA-CM-MDB-0001 | Seawater Reverse Osmosis - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00GBA | 2028-06-26 | G-COM-MC-FF 00GBA IFR G-COM-SC-FF 00GBA IFR G-OPS-HO-FF 00GBA IFC
8 | ALP-EPC-00GCA-CM-MDB-0001 | Demineralisation - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00GCA | 2028-06-26 | G-COM-MC-FF 00GCA IFR G-COM-SC-FF 00GCA IFR G-OPS-HO-FF 00GCA IFC
8 | ALP-EPC-00GHA-CM-MDB-0001 | Demineralised Water Storage and Distribution - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00GHA | 2028-06-26 | G-COM-MC-FF 00GHA IFR G-COM-SC-FF 00GHA IFR G-OPS-HO-FF 00GHA IFC
8 | ALP-EPC-00GKA-CM-MDB-0001 | Potable Water - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-03-20 | 2028-04-03 |  | 2028-04-03 | 2028-04-10 | as late as possible (need) | G-COM-MC-FF 00GKA | 2028-06-26 | G-COM-MC-FF 00GKA IFR G-COM-SC-FF 00GKA IFR G-OPS-HO-FF 00GKA IFC
8 | ALP-EPC-00GMA-CM-MDB-0001 | Process Drains and Waste Water Collection - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00GMA | 2028-06-26 | G-COM-MC-FF 00GMA IFR G-COM-SC-FF 00GMA IFR G-OPS-HO-FF 00GMA IFC
8 | ALP-EPC-00GNA-CM-MDB-0001 | Waste Water Treatment - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00GNA | 2028-06-26 | G-COM-MC-FF 00GNA IFR G-COM-SC-FF 00GNA IFR G-OPS-HO-FF 00GNA IFC
8 | ALP-EPC-00GUA-CM-MDB-0001 | Sanitary Waste Water Treatment - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GUA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00GUA | 2028-06-26 | G-COM-MC-FF 00GUA IFR G-COM-SC-FF 00GUA IFR G-OPS-HO-FF 00GUA IFC
8 | ALP-EPC-00LDA-CM-MDB-0001 | Condensate Polishing - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00LDA | 2028-06-26 | G-COM-MC-FF 00LDA IFR G-COM-SC-FF 00LDA IFR G-OPS-HO-FF 00LDA IFC
8 | ALP-EPC-00PAA-CM-MDB-0001 | CW Intake, Screens and Outfall - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00PAA | 2028-06-26 | G-COM-MC-FF 00PAA IFR G-COM-SC-FF 00PAA IFR G-OPS-HO-FF 00PAA IFC
8 | ALP-EPC-00PAB-CM-MDB-0001 | CW Piping - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00PAB | 2028-06-26 | G-COM-MC-FF 00PAB IFR G-COM-SC-FF 00PAB IFR G-OPS-HO-FF 00PAB IFC
8 | ALP-EPC-00PAC-CM-MDB-0001 | CW Pumps - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00PAC | 2028-06-26 | G-COM-MC-FF 00PAC IFR G-COM-SC-FF 00PAC IFR G-OPS-HO-FF 00PAC IFC
8 | ALP-EPC-00PAH-CM-MDB-0001 | Condenser Tube Cleaning - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00PAH | 2028-06-26 | G-COM-MC-FF 00PAH IFR G-COM-SC-FF 00PAH IFR G-OPS-HO-FF 00PAH IFC
8 | ALP-EPC-00PBA-CM-MDB-0001 | Electro-Chlorination - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00PBA | 2028-06-26 | G-COM-MC-FF 00PBA IFR G-COM-SC-FF 00PBA IFR G-OPS-HO-FF 00PBA IFC
8 | ALP-EPC-00PGA-CM-MDB-0001 | Closed Cooling Water - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00PGA | 2028-06-26 | G-COM-MC-FF 00PGA IFR G-COM-SC-FF 00PGA IFR G-OPS-HO-FF 00PGA IFC
8 | ALP-EPC-00QCA-CM-MDB-0001 | Chemical Dosing - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00QCA | 2028-06-26 | G-COM-MC-FF 00QCA IFR G-COM-SC-FF 00QCA IFR G-OPS-HO-FF 00QCA IFC
8 | ALP-EPC-00QEA-CM-MDB-0001 | Compressed Air - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00QEA | 2028-06-26 | G-COM-MC-FF 00QEA IFR G-COM-SC-FF 00QEA IFR G-OPS-HO-FF 00QEA IFC
8 | ALP-EPC-00QHA-CM-MDB-0001 | Auxiliary Boiler - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00QHA | 2028-06-26 | G-COM-MC-FF 00QHA IFR G-COM-SC-FF 00QHA IFR G-OPS-HO-FF 00QHA IFC
8 | ALP-EPC-00QJA-CM-MDB-0001 | Nitrogen Supply - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-03 | 2028-04-17 |  | 2028-04-17 | 2028-04-24 | capacity commissioning | G-COM-MC-FF 00QJA | 2028-06-26 | G-COM-MC-FF 00QJA IFR G-COM-SC-FF 00QJA IFR G-OPS-HO-FF 00QJA IFC
8 | ALP-EPC-00QJB-CM-MDB-0001 | Hydrogen and CO2 Supply - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 00QJB | 2028-06-26 | G-COM-MC-FF 00QJB IFR G-COM-SC-FF 00QJB IFR G-OPS-HO-FF 00QJB IFC
8 | ALP-EPC-00QUA-CM-MDB-0001 | Sampling and SWAS - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 00QUA | 2028-06-26 | G-COM-MC-FF 00QUA IFR G-COM-SC-FF 00QUA IFR G-OPS-HO-FF 00QUA IFC
8 | ALP-EPC-00SAA-CM-MDB-0001 | HVAC - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SAA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 00SAA | 2028-06-26 | G-COM-MC-FF 00SAA IFR G-COM-SC-FF 00SAA IFR G-OPS-HO-FF 00SAA IFC
8 | ALP-EPC-00SGA-CM-MDB-0001 | Fire Water System - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 00SGA | 2028-06-26 | G-COM-MC-FF 00SGA IFR G-COM-SC-FF 00SGA IFR G-OPS-HO-FF 00SGA IFC
8 | ALP-EPC-00SGC-CM-MDB-0001 | Deluge, Spray and Foam Systems - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 00SGC | 2028-06-26 | G-COM-MC-FF 00SGC IFR G-COM-SC-FF 00SGC IFR G-OPS-HO-FF 00SGC IFC
8 | ALP-EPC-10HSB-CM-MDB-0001 | Ammonia Storage and Supply - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-04-17 | 2028-05-01 |  | 2028-05-01 | 2028-05-08 | capacity commissioning | G-COM-MC-FF 10HSB | 2028-06-26 | G-COM-MC-FF 10HSB IFR G-COM-SC-FF 10HSB IFR G-OPS-HO-FF 10HSB IFC
8 | ALP-I09-00CKA-ME-OMM-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Operation and Maintenance Manual |  | I09 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CKA-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-11-11 | 2027-12-23 |  | 2028-01-06 | 2028-05-11 | PO MR-IC-009 | G-COM-SC-FF 00CKA | 2028-07-24 | G-COM-SC-FF 00CKA IFR G-OPS-HO-FF 00CKA IFC
8 | ALP-EPC-00LBG-CM-MDB-0001 | Auxiliary Steam - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 00LBG | 2028-08-28 | G-COM-MC-WS 00LBG IFR G-COM-SC-WS 00LBG IFR G-OPS-HO-WS 00LBG IFC
8 | ALP-EPC-10HAN-CM-MDB-0001 | HRSG Blowdown and Drains - System Turnover Dossier | EPC tanks and headers | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10HAN | 2028-08-28 | G-COM-MC-WS 10HAN IFR G-COM-SC-WS 10HAN IFR G-OPS-HO-WS 10HAN IFC
8 | ALP-EPC-10LAB-CM-MDB-0001 | Feedwater Piping - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10LAB | 2028-08-28 | G-COM-MC-WS 10LAB IFR G-COM-SC-WS 10LAB IFR G-OPS-HO-WS 10LAB IFC
8 | ALP-EPC-10LAC-CM-MDB-0001 | Boiler Feed Pumps - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10LAC | 2028-08-28 | G-COM-MC-WS 10LAC IFR G-COM-SC-WS 10LAC IFR G-OPS-HO-WS 10LAC IFC
8 | ALP-EPC-10LAE-CM-MDB-0001 | HP Attemperation Spray Water - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10LAE | 2028-08-28 | G-COM-MC-WS 10LAE IFR G-COM-SC-WS 10LAE IFR G-OPS-HO-WS 10LAE IFC
8 | ALP-EPC-10LAF-CM-MDB-0001 | Reheat Attemperation Spray Water - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10LAF | 2028-08-28 | G-COM-MC-WS 10LAF IFR G-COM-SC-WS 10LAF IFR G-OPS-HO-WS 10LAF IFC
8 | ALP-EPC-10LBA-CM-MDB-0001 | Main Steam Piping - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10LBA | 2028-08-28 | G-COM-MC-WS 10LBA IFR G-COM-SC-WS 10LBA IFR G-OPS-HO-WS 10LBA IFC
8 | ALP-EPC-10LBB-CM-MDB-0001 | Hot Reheat Piping - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10LBB | 2028-08-28 | G-COM-MC-WS 10LBB IFR G-COM-SC-WS 10LBB IFR G-OPS-HO-WS 10LBB IFC
8 | ALP-EPC-10LBC-CM-MDB-0001 | Cold Reheat Piping - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10LBC | 2028-08-28 | G-COM-MC-WS 10LBC IFR G-COM-SC-WS 10LBC IFR G-OPS-HO-WS 10LBC IFC
8 | ALP-EPC-10LBD-CM-MDB-0001 | LP Steam Piping - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 10LBD | 2028-08-28 | G-COM-MC-WS 10LBD IFR G-COM-SC-WS 10LBD IFR G-OPS-HO-WS 10LBD IFC
8 | ALP-EPC-20LCA-CM-MDB-0001 | Main Condensate Piping - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 20LCA | 2028-08-28 | G-COM-MC-WS 20LCA IFR G-COM-SC-WS 20LCA IFR G-OPS-HO-WS 20LCA IFC
8 | ALP-EPC-20LCB-CM-MDB-0001 | Condensate Extraction Pumps - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-05-22 | 2028-06-05 |  | 2028-06-05 | 2028-06-12 | as late as possible (need) | G-COM-MC-WS 20LCB | 2028-08-28 | G-COM-MC-WS 20LCB IFR G-COM-SC-WS 20LCB IFR G-OPS-HO-WS 20LCB IFC
8 | ALP-EPC-20MAN-CM-MDB-0001 | Turbine Bypass Stations and Piping - System Turnover Dossier |  | EPC | commissioning | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-06-05 | 2028-06-19 |  | 2028-06-19 | 2028-06-26 | capacity commissioning | G-COM-MC-WS 20MAN | 2028-08-28 | G-COM-MC-WS 20MAN IFR G-COM-SC-WS 20MAN IFR G-OPS-HO-WS 20MAN IFC
8 | ALP-EPC-00000-CM-TRP-0007 | Fire Protection System Test Certificates |  | EPC | commissioning | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-CM-CMP-0001 is NONE, IFR needs it at IFR |  | 2028-07-04 | 2028-07-11 |  | 2028-07-25 | 2028-08-01 | after KD-010 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
8 | ALP-EPC-00000-EL-TRP-0001 | Revenue Metering and TSO SCADA Interface Test Report |  | EPC | electrical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-SPC-0003 is NONE, IFR needs it at IFR |  | 2028-07-04 | 2028-07-11 |  | 2028-07-25 | 2028-08-01 | after KD-010 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
9 | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | RMU, temporary distribution | EPC | general | MRQ | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-EL-011 | 2026-11-09 | G-PRC-ENQ MR-EL-011 IFR G-PRC-PO MR-EL-011 IFC
9 | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BBA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-EL-003 | 2026-12-07 | G-PRC-ENQ MR-EL-003 IFR G-PRC-PO MR-EL-003 IFC
9 | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BFA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BMA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BRA-EL-DSH-0002 is NONE, IFR needs it at IFR input ALP-EPC-00BRA-EL-DSH-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-EL-005 | 2027-01-18 | G-PRC-ENQ MR-EL-005 IFR G-PRC-PO MR-EL-005 IFC
9 | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00XJA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00XJA-ME-DSH-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-EL-006 | 2026-12-07 | G-PRC-ENQ MR-EL-006 IFR G-PRC-PO MR-EL-006 IFC
9 | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-10BBT-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-20BBT-EL-DSH-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-EL-002 | 2027-01-25 | G-PRC-ENQ MR-EL-002 IFR G-PRC-PO MR-EL-002 IFC
9 | ALP-EPC-00000-GE-ITP-0001 | Construction Power Supply - Inspection and Test Plan | RMU, temporary distribution | EPC | general | ITP | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-09 |  | G-PRC-PO MR-EL-011 | 2026-11-16 | G-PRC-PO MR-EL-011 IFR
9 | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BFT-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-16 | 2026-11-23 |  | 2026-11-23 | 2026-11-26 | capacity electrical | G-PRC-ENQ MR-EL-004 | 2027-03-22 | G-PRC-ENQ MR-EL-004 IFR G-PRC-PO MR-EL-004 IFC
9 | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BRA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BTA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BRA-EL-DSH-0002 is NONE, IFR needs it at IFR |  | 2026-11-16 | 2026-11-23 |  | 2026-11-23 | 2026-11-26 | ALP-EPC-00BRA-EL-DSH-0002 | G-PRC-ENQ MR-EL-007 | 2027-03-22 | G-PRC-ENQ MR-EL-007 IFR G-PRC-PO MR-EL-007 IFC
9 | ALP-EPC-00ACA-EL-DSH-0001 | 380 kV GIS Switchyard: Switchgear - Datasheet |  | EPC | electrical | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
9 | ALP-EPC-00CJA-IC-DSH-0001 | Plant DCS: Control Systems - Datasheet | 6 items | EPC | i_and_c | DSH | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-SPC-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-IC-DBR-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 | 2026-11-23 | 2026-11-23 | 2026-11-30
9 | ALP-EPC-00ACA-EL-ITP-0001 | 380 kV GIS - Inspection and Test Plan |  | EPC | electrical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-EL-001 | 2026-12-15 | G-PRC-PO MR-EL-001 IFR
9 | ALP-EPC-00CJA-IC-ITP-0001 | Plant DCS - Inspection and Test Plan |  | EPC | i_and_c | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 | 2026-12-07 | 2026-12-07 | 2026-12-14 |  | G-PRC-PO MR-IC-001 | 2027-02-15 | G-PRC-PO MR-IC-001 IFR
9 | ALP-EPC-00UZA-EL-CBL-0001 | Site-Wide Infrastructure - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UZA-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-26 |  | 2027-02-26 | 2027-03-05 | ALP-EPC-00000-EL-CAL-0001 | G-CON-CWP CWP-12-EL-01 | 2027-05-17 | G-CON-CWP CWP-12-EL-01 IFC G-CON-IWP CWP-12-EL-01 IFC
9 | ALP-EPC-00UBA-EL-CBL-0001 | Electrical Building and Emergency Power - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UBA-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-02-02 | 2027-03-08 |  | 2027-03-08 | 2027-03-15 | ALP-EPC-00UBA-EL-ELY-0001 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
9 | ALP-EPC-00UCA-EL-CBL-0001 | Control, Administration and Workshop Buildings - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UCA-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-03-18 |  | 2027-03-18 | 2027-03-25 | capacity electrical | G-CON-CWP CWP-11-EL-01 | 2027-11-08 | G-CON-CWP CWP-11-EL-01 IFC G-CON-IWP CWP-11-EL-01 IFC
9 | ALP-EPC-00BBA-EL-WIR-0001 | MV Schematic and Wiring Diagrams |  | EPC | electrical | WIR | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-SLD-0001 is NONE, IFR needs it at IFC input ALP-EPC-00000-EL-STU-0002 is NONE, IFR needs it at IFC |  | 2027-03-15 | 2027-04-26 |  | 2027-04-26 | 2027-05-03 | ALP-EPC-00000-EL-STU-0002 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BBA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
9 | ALP-EPC-00UGA-CV-EFD-0001 | Water Treatment Building and Basins - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UGA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-M12-00GBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M13-00GHA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M14-00GNA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-02 | 2027-04-27 | 2027-05-25 | 2027-05-25 | 2027-06-01 | capacity civil | G-CON-CWP CWP-07-CV-01 | 2027-04-05 | G-CON-CWP CWP-07-CV-01 IFC G-CON-IWP CWP-07-CV-01 IFC
9 | ALP-EPC-00UPC-CV-EFD-0001 | CW Pump House - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UPC-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-M03-00PAC-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M04-00PAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M05-00PBA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-06 | 2027-04-30 | 2027-05-28 | 2027-05-28 | 2027-06-04 | capacity civil | G-CON-CWP CWP-05-CV-01 | 2027-03-25 | G-CON-CWP CWP-05-CV-01 IFC G-CON-IWP CWP-05-CV-01 IFC
9 | ALP-EPC-00SGY-GE-RPT-0001 | Fire Detection and Alarm System - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-10 | 2027-05-31 |  | 2027-05-31 | 2027-06-07 | bids MR-IC-006 | G-PRC-PO MR-IC-006 | 2027-07-19 | G-PRC-PO MR-IC-006 IFR
9 | ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UQA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-M01-10LAC-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M07-00PGA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M08-00QEA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M09-00QHA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M18-10HSB-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-03 | 2027-05-31 | 2027-05-31 | 2027-06-07 | capacity civil | G-CON-CWP CWP-08-CV-01 | 2027-05-04 | G-CON-CWP CWP-08-CV-01 IFC G-CON-IWP CWP-08-CV-01 IFC
9 | ALP-EPC-00000-GE-RPT-0005 | Electrical and I&C Installation - Technical Bid Evaluation | subcontract | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-05-19 | 2027-06-09 |  | 2027-06-09 | 2027-06-16 | bids MR-EL-012 | G-PRC-PO MR-EL-012 | 2027-11-22 | G-PRC-PO MR-EL-012 IFR
9 | ALP-EPC-10UHA-CV-EFD-0001 | HRSG Foundations and Structures - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UHA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-M19-10HAN-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-16 | 2027-05-12 | 2027-06-09 | 2027-06-09 | 2027-06-16 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
9 | ALP-EPC-10UMA-CV-EFD-0001 | Gas Turbine Hall - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10UMA-CV-FND-0002 is NONE, IFR needs it at IFR input ALP-IEC-10MKA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M21-00SMA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-09 | 2027-05-12 | 2027-06-09 | 2027-06-09 | 2027-06-16 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
9 | ALP-EPC-00UEG-CV-EFD-0001 | LDO Tank Farm Structures - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEG-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-M16-00EGA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-19 | 2027-06-16 | 2027-06-16 | 2027-06-23 | capacity civil | G-CON-CWP CWP-10-CV-01 | 2027-06-03 | G-CON-CWP CWP-10-CV-01 IFC G-CON-IWP CWP-10-CV-01 IFC
9 | ALP-EPC-20UMB-CV-EFD-0001 | Steam Turbine Hall - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20UMB-CV-FND-0002 is NONE, IFR needs it at IFR input ALP-M02-20LCB-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-20MAA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MKA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-M21-00SMA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-27 | 2027-05-24 | 2027-06-21 | 2027-06-21 | 2027-06-28 | capacity civil | G-CON-CWP CWP-02-CV-02 | 2027-04-19 | G-CON-CWP CWP-02-CV-02 IFC G-CON-IWP CWP-02-CV-02 IFC
9 | ALP-I06-00SGY-ME-ITP-0001 | Fire Detection and Alarm System - Supplier Inspection and Test Plan |  | I06 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-14 |  | 2027-06-28 | 2027-06-28 | PO MR-IC-006 | G-PRC-FAB MR-IC-006 | 2027-09-13 | G-PRC-FAB MR-IC-006 ACCEPTED
9 | ALP-I06-00SGY-ME-DSH-0001 | Fire Detection and Alarm System - Supplier Certified Datasheets and Performance Curves |  | I06 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-14 |  | 2027-06-28 | 2027-07-05 | PO MR-IC-006 | G-PRC-FAB MR-IC-006 | 2027-09-13 | G-PRC-FAB MR-IC-006 ACCEPTED
9 | ALP-E12-00000-GE-ITP-0001 | Electrical and I&C Installation - Subcontractor Inspection and Test Plans | subcontract | E12 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-23 |  | 2027-07-07 | 2027-07-07 | PO MR-EL-012
9 | ALP-E12-00000-GE-MOS-0001 | Electrical and I&C Installation - Subcontractor Method Statements, Part 1 of 6 | subcontract | E12 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-23 |  | 2027-07-07 | 2027-07-07 | PO MR-EL-012
9 | ALP-E12-00000-GE-MOS-0002 | Electrical and I&C Installation - Subcontractor Method Statements, Part 2 of 6 | subcontract | E12 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-23 |  | 2027-07-07 | 2027-07-07 | PO MR-EL-012
9 | ALP-E12-00000-GE-MOS-0003 | Electrical and I&C Installation - Subcontractor Method Statements, Part 3 of 6 | subcontract | E12 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-23 |  | 2027-07-07 | 2027-07-07 | PO MR-EL-012
9 | ALP-E12-00000-GE-MOS-0004 | Electrical and I&C Installation - Subcontractor Method Statements, Part 4 of 6 | subcontract | E12 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-23 |  | 2027-07-07 | 2027-07-07 | PO MR-EL-012
9 | ALP-E12-00000-GE-MOS-0005 | Electrical and I&C Installation - Subcontractor Method Statements, Part 5 of 6 | subcontract | E12 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-23 |  | 2027-07-07 | 2027-07-07 | PO MR-EL-012
9 | ALP-E12-00000-GE-MOS-0006 | Electrical and I&C Installation - Subcontractor Method Statements, Part 6 of 6 | subcontract | E12 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0002 is NONE, IFR needs it at IFR |  | 2027-06-09 | 2027-06-23 |  | 2027-07-07 | 2027-07-07 | PO MR-EL-012
9 | ALP-I06-00SGY-ME-GAD-0001 | Fire Detection and Alarm System - Supplier GA Drawings |  | I06 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-24 | 2027-06-21 |  | 2027-07-05 | 2027-07-12 | PO MR-IC-006 | G-PRC-FAB MR-IC-006 | 2027-09-13 | G-COM-MC-FF 00SGY IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC G-PRC-FAB MR-IC-006 ACCEPTED
9 | ALP-I06-00SGY-IC-IOL-0001 | Fire Detection and Alarm System - Supplier I/O List, Control Philosophy and Interface Signals |  | I06 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-28 |  | 2027-07-12 | 2027-07-19 | PO MR-IC-006
9 | ALP-I06-00SGY-ME-CAL-0001 | Fire Detection and Alarm System - Supplier Design Calculations |  | I06 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-28 |  | 2027-07-12 | 2027-07-19 | PO MR-IC-006 | G-PRC-FAB MR-IC-006 | 2027-09-13 | G-PRC-FAB MR-IC-006 ACCEPTED
9 | ALP-EPC-00UEK-CV-EFD-0001 | Gas Station Structures - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UEK-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-M15-00EKA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-05-31 | 2027-06-22 | 2027-07-20 | 2027-07-20 | 2027-07-27 | ALP-EPC-00UEK-CV-FND-0001 | G-CON-CWP CWP-09-CV-01 | 2027-08-04 | G-CON-CWP CWP-09-CV-01 IFC G-CON-IWP CWP-09-CV-01 IFC
9 | ALP-I06-00SGY-EL-WIR-0001 | Fire Detection and Alarm System - Supplier Electrical Schematics and Wiring Diagrams |  | I06 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-06-14 | 2027-07-05 |  | 2027-07-19 | 2027-08-02 | PO MR-IC-006 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-COM-MC-FF 00SGY IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
9 | ALP-I06-00SGY-ME-LST-0001 | Fire Detection and Alarm System - Spare Parts and Special Tools Lists |  | I06 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-21 | 2027-07-12 |  | 2027-07-26 | 2027-08-09 | PO MR-IC-006
9 | ALP-I06-00SGY-ME-TST-0001 | Fire Detection and Alarm System - Factory Acceptance Test Procedure |  | I06 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-07 | 2027-06-28 |  | 2027-07-26 | 2027-08-09 | PO MR-IC-006 | G-PRC-FAT MR-IC-006 | 2027-09-20 | G-PRC-FAT MR-IC-006 ACCEPTED
9 | ALP-EPC-00UEK-EL-CBL-0001 | Fuel Gas Station - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEK-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-07-19 | 2027-08-18 |  | 2027-08-18 | 2027-08-25 | capacity electrical | G-CON-CWP CWP-09-EL-01 | 2027-12-27 | G-CON-CWP CWP-09-EL-01 IFC G-CON-IWP CWP-09-EL-01 IFC
9 | ALP-EPC-00UZF-GE-RPT-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Bid Evaluation | subcontract | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-09 | 2027-08-30 |  | 2027-08-30 | 2027-09-06 | bids MR-ME-024 | G-PRC-PO MR-ME-024 | 2027-11-15 | G-PRC-PO MR-ME-024 IFR
9 | ALP-I06-00SGY-ME-PRC-0001 | Fire Detection and Alarm System - Supplier Installation and Erection Manual |  | I06 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-05 | 2027-07-26 |  | 2027-08-09 | 2027-09-06 | PO MR-IC-006 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFR
9 | ALP-EPC-00UEG-EL-CBL-0001 | LDO Tank Farm and Unloading - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UEG-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-08-11 | 2027-09-07 |  | 2027-09-07 | 2027-09-14 | capacity electrical | G-CON-CWP CWP-10-EL-01 | 2028-01-24 | G-CON-CWP CWP-10-EL-01 IFC G-CON-IWP CWP-10-EL-01 IFC
9 | ALP-EPC-00UAC-EL-CBL-0001 | 380 kV GIS Switchyard - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UAC-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-08-11 | 2027-09-09 |  | 2027-09-09 | 2027-09-16 | capacity electrical | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
9 | ALP-EPC-00GMA-PI-SUP-0001 | Process Drains and Waste Water Collection - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GMA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-08-09 | 2027-09-14 |  | 2027-09-14 | 2027-09-21 | ALP-EPC-00GMA-PI-ISO-0001 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-COM-MC-FF 00GMA IFC G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
9 | ALP-EPC-00UPC-EL-CBL-0001 | CW Pump House and Onshore CW - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UPC-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-08-12 | 2027-09-16 |  | 2027-09-16 | 2027-09-23 | capacity electrical | G-CON-CWP CWP-05-EL-01 | 2028-01-31 | G-CON-CWP CWP-05-EL-01 IFC G-CON-IWP CWP-05-EL-01 IFC
9 | ALP-M24-00UZF-GE-ITP-0001 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Inspection and Test Plans | subcontract | M24 | general | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-ME-024
9 | ALP-M24-00UZF-GE-MOS-0001 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 1 of 6 | subcontract | M24 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-ME-024
9 | ALP-M24-00UZF-GE-MOS-0002 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 2 of 6 | subcontract | M24 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-ME-024
9 | ALP-M24-00UZF-GE-MOS-0003 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 3 of 6 | subcontract | M24 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-ME-024
9 | ALP-M24-00UZF-GE-MOS-0004 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 4 of 6 | subcontract | M24 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-ME-024
9 | ALP-M24-00UZF-GE-MOS-0005 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 5 of 6 | subcontract | M24 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-ME-024
9 | ALP-M24-00UZF-GE-MOS-0006 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 6 of 6 | subcontract | M24 | general | MOS | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UZF-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-09-13 |  | 2027-09-27 | 2027-09-27 | PO MR-ME-024
9 | ALP-EPC-00UQA-EL-CBL-0001 | BOP Utilities - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UQA-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-08-11 | 2027-09-21 |  | 2027-09-21 | 2027-09-28 | capacity electrical | G-CON-CWP CWP-08-EL-01 | 2028-01-10 | G-CON-CWP CWP-08-EL-01 IFC G-CON-IWP CWP-08-EL-01 IFC
9 | ALP-EPC-00PAA-PI-SUP-0001 | CW Intake, Screens and Outfall - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-08-27 | 2027-09-22 |  | 2027-09-22 | 2027-09-29 | ALP-EPC-00PAA-PI-ISO-0001 | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PAA IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC
9 | ALP-EPC-00PAC-PI-SUP-0001 | CW Pumps - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAC-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-08-27 | 2027-09-22 |  | 2027-09-22 | 2027-09-29 | ALP-EPC-00PAC-PI-ISO-0001 | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PAC IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC
9 | ALP-EPC-00GKA-PI-SUP-0001 | Potable Water - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GKA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-08-26 | 2027-09-23 |  | 2027-09-23 | 2027-09-30 | ALP-EPC-00GKA-PI-ISO-0001 | G-CON-CWP CWP-12-PI-01 | 2027-07-12 | G-COM-MC-FF 00GKA IFC G-CON-CWP CWP-12-PI-01 IFC G-CON-IWP CWP-12-PI-01 IFC
9 | ALP-EPC-00UGA-EL-CBL-0001 | Water Treatment and Effluents - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-00UGA-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-08-25 | 2027-09-24 |  | 2027-09-24 | 2027-10-01 | capacity electrical | G-CON-CWP CWP-07-EL-01 | 2028-02-21 | G-CON-CWP CWP-07-EL-01 IFC G-CON-IWP CWP-07-EL-01 IFC
9 | ALP-EPC-10UMA-EL-CBL-0001 | Power Block - GT and HRSG - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-10UMA-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-08-13 | 2027-09-27 |  | 2027-09-27 | 2027-10-04 | capacity electrical | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
9 | ALP-I06-00SGY-ME-TRP-0001 | Fire Detection and Alarm System - Factory Acceptance Test Report |  | I06 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-13 | 2027-09-20 |  | 2027-10-04 | 2027-10-04 | PO MR-IC-006 | G-PRC-SHP MR-IC-006 | 2027-10-18 | G-PRC-SHP MR-IC-006 ACCEPTED
9 | ALP-EPC-00PAB-PI-SUP-0001 | CW Piping - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAB-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-00PAB-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-08-30 | 2027-09-29 |  | 2027-09-29 | 2027-10-06 | ALP-EPC-00PAB-PI-ISO-0001 | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PAB IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC
9 | ALP-EPC-00PBA-PI-SUP-0001 | Electro-Chlorination - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PBA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-08-30 | 2027-10-01 |  | 2027-10-01 | 2027-10-08 | ALP-EPC-00PBA-PI-ISO-0001 | G-CON-CWP CWP-05-PI-01 | 2027-09-20 | G-COM-MC-FF 00PBA IFC G-CON-CWP CWP-05-PI-01 IFC G-CON-IWP CWP-05-PI-01 IFC
9 | ALP-EPC-20UMB-EL-CBL-0001 | Power Block - ST and Condenser - Cable Schedule and Routing |  | EPC | electrical | CBL | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-CAL-0001 is NONE, IFR needs it at IFR input ALP-EPC-00000-EL-SLD-0001 is NONE, IFR needs it at IFR input ALP-EPC-20UMB-EL-ELY-0001 is NONE, IFR needs it at IFR |  | 2027-08-30 | 2027-10-11 |  | 2027-10-11 | 2027-10-18 | ALP-EPC-20UMB-EL-ELY-0001 | G-CON-CWP CWP-02-EL-01 | 2028-02-28 | G-CON-CWP CWP-02-EL-01 IFC G-CON-IWP CWP-02-EL-01 IFC
9 | ALP-EPC-00000-EL-LST-0003 | Protection Relay Settings List |  | EPC | electrical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-EL-STU-0002 is NONE, IFR needs it at IFR |  | 2027-09-07 | 2027-09-29 |  | 2027-10-13 | 2027-10-27 | capacity electrical | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
9 | ALP-I06-00SGY-ME-MDB-0001 | Fire Detection and Alarm System - Manufacturing Record Book and Conformity Certificates |  | I06 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-20 | 2027-10-04 |  | 2027-10-04 | 2027-11-29 | PO MR-IC-006 | G-PRC-SHP MR-IC-006 | 2027-10-18 | G-PRC-SHP MR-IC-006 IFR
9 | ALP-EPC-00EKA-PI-SUP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKA-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-00EKA-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-10-13 | 2027-11-24 |  | 2027-11-24 | 2027-12-01 | capacity piping | G-CON-CWP CWP-09-PI-01 | 2027-11-29 | G-COM-MC-FF 00EKA IFC G-CON-CWP CWP-09-PI-01 IFC G-CON-IWP CWP-09-PI-01 IFC
9 | ALP-EPC-00EKC-PI-SUP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EKC-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-00EKC-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-10-28 | 2027-12-03 |  | 2027-12-03 | 2027-12-10 | capacity piping | G-CON-CWP CWP-09-PI-01 | 2027-11-29 | G-COM-MC-FF 00EKC IFC G-CON-CWP CWP-09-PI-01 IFC G-CON-IWP CWP-09-PI-01 IFC
9 | ALP-I06-00SGY-ME-OMM-0001 | Fire Detection and Alarm System - Supplier Operation and Maintenance Manual |  | I06 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGY-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-12 | 2027-08-23 |  | 2027-09-06 | 2028-01-10 | PO MR-IC-006 | G-COM-SC-FF 00SGY | 2028-07-24 | G-COM-SC-FF 00SGY IFR G-OPS-HO-FF 00SGY IFC
9 | ALP-EPC-00EGA-PI-SUP-0001 | LDO Unloading - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-14 |  | 2028-01-14 | 2028-01-21 | capacity piping | G-CON-CWP CWP-10-PI-01 | 2027-12-27 | G-COM-MC-FF 00EGA IFC G-CON-CWP CWP-10-PI-01 IFC G-CON-IWP CWP-10-PI-01 IFC
9 | ALP-EPC-00QCA-PI-SUP-0001 | Chemical Dosing - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QCA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-14 |  | 2028-01-14 | 2028-01-21 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00QCA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-00QJA-PI-SUP-0001 | Nitrogen Supply - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-12-15 | 2028-01-14 |  | 2028-01-14 | 2028-01-21 | ALP-EPC-00QJA-PI-ISO-0001 | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00QJA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-10HSB-PI-SUP-0001 | Ammonia Storage and Supply - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HSB-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-14 |  | 2028-01-14 | 2028-01-21 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 10HSB IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-00EGB-PI-SUP-0001 | LDO Storage - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGB-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-12-14 | 2028-01-17 |  | 2028-01-17 | 2028-01-24 | ALP-EPC-00EGB-PI-ISO-0001 | G-CON-CWP CWP-10-PI-01 | 2027-12-27 | G-COM-MC-FF 00EGB IFC G-CON-CWP CWP-10-PI-01 IFC G-CON-IWP CWP-10-PI-01 IFC
9 | ALP-EPC-10LAC-PI-SUP-0001 | Boiler Feed Pumps - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAC-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10LAC-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-18 |  | 2028-01-18 | 2028-01-25 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-WS 10LAC IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-00EGC-PI-SUP-0001 | LDO Forwarding and Treatment - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGC-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-00EGC-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-08 | 2028-01-19 |  | 2028-01-19 | 2028-01-26 | capacity piping | G-CON-CWP CWP-10-PI-01 | 2027-12-27 | G-COM-MC-FF 00EGC IFC G-CON-CWP CWP-10-PI-01 IFC G-CON-IWP CWP-10-PI-01 IFC
9 | ALP-EPC-00LBG-PI-SUP-0001 | Auxiliary Steam - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LBG-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-00LBG-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-19 |  | 2028-01-19 | 2028-01-26 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-WS 00LBG IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-00QHA-PI-SUP-0001 | Auxiliary Boiler - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QHA-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-00QHA-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-19 |  | 2028-01-19 | 2028-01-26 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00QHA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-00PGA-PI-SUP-0001 | Closed Cooling Water - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PGA-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-00PGA-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-08 | 2028-01-20 |  | 2028-01-20 | 2028-01-27 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00PGA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-00QEA-PI-SUP-0001 | Compressed Air - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QEA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-20 |  | 2028-01-20 | 2028-01-27 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00QEA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-00SGA-PI-SUP-0001 | Fire Water System - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGA-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-00SGA-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-20 |  | 2028-01-20 | 2028-01-27 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00SGA IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-00SGC-PI-SUP-0001 | Deluge, Spray and Foam Systems - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00SGC-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-20 |  | 2028-01-20 | 2028-01-27 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-FF 00SGC IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-10LAB-PI-SUP-0001 | Feedwater Piping - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAB-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10LAB-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-09 | 2028-01-20 |  | 2028-01-20 | 2028-01-27 | capacity piping | G-CON-CWP CWP-08-PI-01 | 2027-12-13 | G-COM-MC-WS 10LAB IFC G-CON-CWP CWP-08-PI-01 IFC G-CON-IWP CWP-08-PI-01 IFC
9 | ALP-EPC-10HAN-PI-SUP-0001 | HRSG Blowdown and Drains - Pipe Support Drawings | EPC tanks and headers | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10HAN-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10HAN-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-16 | 2028-01-26 |  | 2028-01-26 | 2028-02-02 | ALP-EPC-10HAN-PI-ISO-0001 | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10HAN IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-10LBA-PI-SUP-0001 | Main Steam Piping - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBA-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10LBA-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-16 | 2028-01-27 |  | 2028-01-27 | 2028-02-03 | ALP-EPC-10LBA-PI-ISO-0001 | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LBA IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-10LBC-PI-SUP-0001 | Cold Reheat Piping - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBC-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10LBC-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-23 | 2028-02-01 |  | 2028-02-01 | 2028-02-08 | ALP-EPC-10LBC-PI-ISO-0001 | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LBC IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-10LBB-PI-SUP-0001 | Hot Reheat Piping - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBB-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10LBB-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2027-12-23 | 2028-02-02 |  | 2028-02-02 | 2028-02-09 | capacity piping | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LBB IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-00QUA-PI-SUP-0001 | Sampling and SWAS - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QUA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2027-12-31 | 2028-02-07 |  | 2028-02-07 | 2028-02-14 | ALP-EPC-00QUA-PI-ISO-0001 | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-FF 00QUA IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-10LBD-PI-SUP-0001 | LP Steam Piping - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LBD-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10LBD-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2028-01-10 | 2028-02-11 |  | 2028-02-11 | 2028-02-18 | ALP-EPC-10LBD-PI-ISO-0001 | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LBD IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-00GBA-PI-SUP-0001 | Seawater Reverse Osmosis - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GBA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2028-01-04 | 2028-02-14 |  | 2028-02-14 | 2028-02-21 | ALP-EPC-00GBA-PI-ISO-0001 | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GBA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC
9 | ALP-EPC-00GCA-PI-SUP-0001 | Demineralisation - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GCA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2028-01-13 | 2028-02-18 |  | 2028-02-18 | 2028-02-25 | ALP-EPC-00GCA-PI-ISO-0001 | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GCA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC
9 | ALP-EPC-00QJB-PI-SUP-0001 | Hydrogen and CO2 Supply - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00QJB-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2028-01-24 | 2028-02-21 |  | 2028-02-21 | 2028-02-28 | ALP-EPC-00QJB-PI-ISO-0001 | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-FF 00QJB IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-00GNA-PI-SUP-0001 | Waste Water Treatment - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GNA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2028-01-18 | 2028-02-23 |  | 2028-02-23 | 2028-03-01 | ALP-EPC-00GNA-PI-ISO-0001 | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GNA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC
9 | ALP-EPC-10LAE-PI-SUP-0001 | HP Attemperation Spray Water - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAE-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10LAE-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2028-01-26 | 2028-02-23 |  | 2028-02-23 | 2028-03-01 | ALP-EPC-10LAE-PI-ISO-0001 | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LAE IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-10LAF-PI-SUP-0001 | Reheat Attemperation Spray Water - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10LAF-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-10LAF-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2028-01-26 | 2028-02-23 |  | 2028-02-23 | 2028-03-01 | ALP-EPC-10LAF-PI-ISO-0001 | G-CON-CWP CWP-01-PI-01 | 2027-12-13 | G-COM-MC-WS 10LAF IFC G-CON-CWP CWP-01-PI-01 IFC G-CON-IWP CWP-01-PI-01 IFC
9 | ALP-EPC-00LDA-PI-SUP-0001 | Condensate Polishing - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00LDA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2028-01-20 | 2028-02-25 |  | 2028-02-25 | 2028-03-03 | ALP-EPC-00LDA-PI-ISO-0001 | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00LDA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC
9 | ALP-EPC-00GHA-PI-SUP-0001 | Demineralised Water Storage and Distribution - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GHA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2028-01-28 | 2028-03-02 |  | 2028-03-02 | 2028-03-09 | ALP-EPC-00GHA-PI-ISO-0001 | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GHA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC
9 | ALP-EPC-00GUA-PI-SUP-0001 | Sanitary Waste Water Treatment - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00GUA-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2028-02-08 | 2028-03-03 |  | 2028-03-03 | 2028-03-10 | ALP-EPC-00GUA-PI-ISO-0001 | G-CON-CWP CWP-07-PI-01 | 2028-01-24 | G-COM-MC-FF 00GUA IFC G-CON-CWP CWP-07-PI-01 IFC G-CON-IWP CWP-07-PI-01 IFC
9 | ALP-EPC-00PAH-PI-SUP-0001 | Condenser Tube Cleaning - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00PAH-PI-ISO-0001 is NONE, IFR needs it at IFC |  | 2028-02-14 | 2028-03-13 |  | 2028-03-13 | 2028-03-20 | ALP-EPC-00PAH-PI-ISO-0001 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-FF 00PAH IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC
9 | ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report |  | EPC | piping | M3D | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00EGA-PI-ISO-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGB-PI-ISO-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EGC-PI-ISO-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKA-PI-ISO-0001 is NONE, IFR needs it at IFR input ALP-EPC-00EKC-PI-ISO-0001 is NONE, IFR needs it at IFR input ALP-EPC-00GBA-PI-ISO-0001 is NONE, IFR needs it at IFR |  | 2028-03-02 | 2028-03-23 |  | 2028-04-06 | 2028-04-13 | ALP-EPC-20LCA-PI-ISO-0001 | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
9 | ALP-EPC-20LCB-PI-SUP-0001 | Condensate Extraction Pumps - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCB-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-20LCB-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2028-03-08 | 2028-04-07 |  | 2028-04-07 | 2028-04-14 | ALP-EPC-20LCB-PI-ISO-0001 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-WS 20LCB IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC
9 | ALP-EPC-20MAN-PI-SUP-0001 | Turbine Bypass Stations and Piping - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20MAN-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-20MAN-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2028-03-03 | 2028-04-14 |  | 2028-04-14 | 2028-04-21 | ALP-EPC-20MAN-PI-ISO-0001 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-WS 20MAN IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC
9 | ALP-EPC-20LCA-PI-SUP-0001 | Main Condensate Piping - Pipe Support Drawings |  | EPC | piping | SUP | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-20LCA-PI-ISO-0001 is NONE, IFR needs it at IFC input ALP-EPC-20LCA-PI-STR-0001 is NONE, IFR needs it at IFC |  | 2028-03-09 | 2028-04-20 |  | 2028-04-20 | 2028-04-27 | ALP-EPC-20LCA-PI-ISO-0001 | G-CON-CWP CWP-02-PI-01 | 2028-01-31 | G-COM-MC-WS 20LCA IFC G-CON-CWP CWP-02-PI-01 IFC G-CON-IWP CWP-02-PI-01 IFC
9 | ALP-EPC-00000-CM-TRP-0003 | Grid Code Compliance Test Report |  | EPC | commissioning | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-CMP-0003 is NONE, IFR needs it at IFR |  | 2029-01-29 | 2029-02-05 |  | 2029-02-19 | 2029-02-26 | after COM-020 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 ACCEPTED
10 | ALP-E11-00000-ME-TST-0001 | Construction Power Supply - Factory Acceptance Test Procedure | RMU, temporary distribution | E11 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-02 | PO MR-EL-011 | G-PRC-FAT MR-EL-011 | 2026-12-14 | G-PRC-FAT MR-EL-011 ACCEPTED
10 | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition |  | EPC | electrical | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00ACA-EL-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-EL-001 | 2026-12-15 | G-PRC-ENQ MR-EL-001 IFR G-PRC-PO MR-EL-001 IFC
10 | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition |  | EPC | i_and_c | MRQ | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00CJA-IC-SPC-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-05 |  | G-PRC-ENQ MR-IC-001 | 2026-11-30 | G-PRC-ENQ MR-IC-001 IFR G-PRC-PO MR-IC-001 IFC
10 | ALP-EPC-00000-GE-RPT-0004 | Construction Power Supply - Technical Bid Evaluation | RMU, temporary distribution | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-02 | 2026-11-09 |  | G-PRC-PO MR-EL-011 | 2026-11-16 | G-PRC-PO MR-EL-011 IFR
10 | ALP-E11-00000-ME-PRC-0001 | Construction Power Supply - Supplier Installation and Erection Manual | RMU, temporary distribution | E11 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-02 |  | 2026-11-16 | 2026-11-30 | PO MR-EL-011 | G-CON-CWP CWP-12-CV-01 | 2027-01-18 | G-CON-CWP CWP-12-CV-01 IFR
10 | ALP-E11-00000-ME-ITP-0001 | Construction Power Supply - Supplier Inspection and Test Plan | RMU, temporary distribution | E11 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-11-09 | 2026-11-23 |  | 2026-12-07 | 2026-12-07 |  | G-PRC-FAB MR-EL-011 | 2026-12-08 | G-PRC-FAB MR-EL-011 ACCEPTED
10 | ALP-E11-00000-ME-TRP-0001 | Construction Power Supply - Factory Acceptance Test Report | RMU, temporary distribution | E11 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2026-12-14 |  | 2026-12-28 | 2026-12-28 | PO MR-EL-011 | G-PRC-SHP MR-EL-011 | 2027-01-11 | G-OWN-TO 00000 ACCEPTED G-PRC-SHP MR-EL-011 ACCEPTED
10 | ALP-E11-00000-IC-IOL-0001 | Construction Power Supply - Supplier I/O List, Control Philosophy and Interface Signals | RMU, temporary distribution | E11 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-11-23 | 2026-12-14 |  | 2026-12-28 | 2027-01-04 | PO MR-EL-011
10 | ALP-EPC-00BBA-GE-RPT-0001 | MV Switchgear 10.5 kV - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2027-01-07 |  | 2027-01-07 | 2027-01-14 | bids MR-EL-003 | G-PRC-PO MR-EL-003 | 2027-02-15 | G-PRC-PO MR-EL-003 IFR
10 | ALP-EPC-00XJA-GE-RPT-0001 | Emergency Diesel Generator - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-17 | 2027-01-07 |  | 2027-01-07 | 2027-01-14 | bids MR-EL-006 | G-PRC-PO MR-EL-006 | 2027-02-15 | G-PRC-PO MR-EL-006 IFR
10 | ALP-E11-00000-ME-LST-0001 | Construction Power Supply - Spare Parts and Special Tools Lists | RMU, temporary distribution | E11 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-07 | 2026-12-28 |  | 2027-01-11 | 2027-01-25 | PO MR-EL-011 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
10 | ALP-EPC-00BFA-GE-RPT-0001 | LV Switchboards and MCCs - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-14 | 2027-02-04 |  | 2027-02-04 | 2027-02-11 | capacity general | G-PRC-PO MR-EL-005 | 2027-03-29 | G-PRC-PO MR-EL-005 IFR
10 | ALP-E11-00000-ME-MDB-0001 | Construction Power Supply - Manufacturing Record Book and Conformity Certificates | RMU, temporary distribution | E11 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-14 | 2026-12-28 |  | 2026-12-28 | 2027-02-22 | PO MR-EL-011 | G-PRC-SHP MR-EL-011 | 2027-01-11 | G-PRC-SHP MR-EL-011 IFR
10 | ALP-EPC-10BBT-GE-RPT-0001 | Unit Auxiliary Transformers - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-28 | 2027-02-18 |  | 2027-02-18 | 2027-02-25 | capacity general | G-PRC-PO MR-EL-002 | 2027-04-05 | G-PRC-PO MR-EL-002 IFR
10 | ALP-E03-00BBA-ME-ITP-0001 | MV Switchgear 10.5 kV - Supplier Inspection and Test Plan |  | E03 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-09 |  | 2027-03-02 | 2027-03-05 | PO MR-EL-003 | G-PRC-FAB MR-EL-003 | 2027-05-26 | G-PRC-FAB MR-EL-003 ACCEPTED
10 | ALP-E06-00XJA-ME-ITP-0001 | Emergency Diesel Generator - Supplier Inspection and Test Plan |  | E06 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-09 |  | 2027-03-02 | 2027-03-05 | PO MR-EL-006 | G-PRC-FAB MR-EL-006 | 2027-05-26 | G-PRC-FAB MR-EL-006 ACCEPTED
10 | ALP-EPC-00BFT-GE-RPT-0001 | LV Transformers - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-03-02 |  | 2027-03-02 | 2027-03-09 | capacity general | G-PRC-PO MR-EL-004 | 2027-05-10 | G-PRC-PO MR-EL-004 IFR
10 | ALP-EPC-00BRA-GE-RPT-0001 | UPS, Batteries and DC Systems - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-10 |  | 2027-03-10 | 2027-03-17 | capacity general | G-PRC-PO MR-EL-007 | 2027-05-10 | G-PRC-PO MR-EL-007 IFR
10 | ALP-E03-00BBA-ME-DSH-0001 | MV Switchgear 10.5 kV - Supplier Certified Datasheets and Performance Curves |  | E03 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-09 |  | 2027-02-23 | 2027-03-18 | PO MR-EL-003 | G-PRC-FAB MR-EL-003 | 2027-05-26 | G-PRC-FAB MR-EL-003 ACCEPTED
10 | ALP-E05-00BFA-ME-ITP-0001 | LV Switchboards and MCCs - Supplier Inspection and Test Plan |  | E05 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-11 | 2027-02-25 |  | 2027-03-18 | 2027-03-18 | PO MR-EL-005 | G-PRC-FAB MR-EL-005 | 2027-06-21 | G-PRC-FAB MR-EL-005 ACCEPTED
10 | ALP-E06-00XJA-CV-CAL-0001 | Emergency Diesel Generator - Supplier Foundation Loads and Anchor Bolt Drawings |  | E06 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-01 | 2027-02-22 |  | 2027-03-08 | 2027-03-18 | PO MR-EL-006 | G-PRC-FAB MR-EL-006 | 2027-05-26 | G-PRC-FAB MR-EL-006 ACCEPTED
10 | ALP-E06-00XJA-ME-DSH-0001 | Emergency Diesel Generator - Supplier Certified Datasheets and Performance Curves |  | E06 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-26 | 2027-02-09 |  | 2027-02-23 | 2027-03-18 | PO MR-EL-006 | G-PRC-FAB MR-EL-006 | 2027-05-26 | G-PRC-FAB MR-EL-006 ACCEPTED
10 | ALP-E05-00BFA-ME-DSH-0001 | LV Switchboards and MCCs - Supplier Certified Datasheets and Performance Curves |  | E05 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-11 | 2027-02-25 |  | 2027-03-11 | 2027-03-30 | PO MR-EL-005 | G-PRC-FAB MR-EL-005 | 2027-06-21 | G-PRC-FAB MR-EL-005 ACCEPTED
10 | ALP-E03-00BBA-ME-GAD-0001 | MV Switchgear 10.5 kV - Supplier GA Drawings |  | E03 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-22 |  | 2027-03-08 | 2027-03-31 | PO MR-EL-003 | G-PRC-FAB MR-EL-003 | 2027-05-26 | G-COM-MC-EL 00BBA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC G-PRC-FAB MR-EL-003 ACCEPTED
10 | ALP-E06-00XJA-ME-GAD-0001 | Emergency Diesel Generator - Supplier GA Drawings |  | E06 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-25 | 2027-02-22 |  | 2027-03-08 | 2027-03-31 | PO MR-EL-006 | G-PRC-FAB MR-EL-006 | 2027-05-26 | G-COM-MC-EL 00XJA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC G-PRC-FAB MR-EL-006 ACCEPTED
10 | ALP-E11-00000-ME-OMM-0001 | Construction Power Supply - Supplier Operation and Maintenance Manual | RMU, temporary distribution | E11 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-GE-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-11-02 | 2026-11-16 |  | 2026-11-30 | 2027-04-05 | PO MR-EL-011
10 | ALP-E04-00BFT-ME-ITP-0001 | LV Transformers - Supplier Inspection and Test Plan |  | E04 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-03-19 |  | 2027-04-07 | 2027-04-07 | PO MR-EL-004 | G-PRC-FAB MR-EL-004 | 2027-07-21 | G-PRC-FAB MR-EL-004 ACCEPTED
10 | ALP-E05-00BFA-ME-GAD-0001 | LV Switchboards and MCCs - Supplier GA Drawings |  | E05 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-08 | 2027-03-08 |  | 2027-03-22 | 2027-04-08 | PO MR-EL-005 | G-PRC-FAB MR-EL-005 | 2027-06-21 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC G-PRC-FAB MR-EL-005 ACCEPTED
10 | ALP-E03-00BBA-IC-IOL-0001 | MV Switchgear 10.5 kV - Supplier I/O List, Control Philosophy and Interface Signals |  | E03 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-05 |  | 2027-03-19 | 2027-04-13 | PO MR-EL-003
10 | ALP-E03-00BBA-ME-CAL-0001 | MV Switchgear 10.5 kV - Supplier Design Calculations |  | E03 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-05 |  | 2027-03-19 | 2027-04-13 | PO MR-EL-003 | G-PRC-FAB MR-EL-003 | 2027-05-26 | G-PRC-FAB MR-EL-003 ACCEPTED
10 | ALP-E06-00XJA-IC-IOL-0001 | Emergency Diesel Generator - Supplier I/O List, Control Philosophy and Interface Signals |  | E06 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-05 |  | 2027-03-19 | 2027-04-13 | PO MR-EL-006
10 | ALP-E06-00XJA-ME-CAL-0001 | Emergency Diesel Generator - Supplier Design Calculations |  | E06 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-12 | 2027-03-05 |  | 2027-03-19 | 2027-04-13 | PO MR-EL-006 | G-PRC-FAB MR-EL-006 | 2027-05-26 | G-PRC-FAB MR-EL-006 ACCEPTED
10 | ALP-E02-10BBT-ME-ITP-0001 | Unit Auxiliary Transformers - Supplier Inspection and Test Plan |  | E02 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-18 |  | 2027-04-08 | 2027-04-15 | PO MR-EL-002 | G-PRC-FAB MR-EL-002 | 2027-07-26 | G-PRC-FAB MR-EL-002 ACCEPTED
10 | ALP-E04-00BFT-ME-DSH-0001 | LV Transformers - Supplier Certified Datasheets and Performance Curves |  | E04 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-05 | 2027-03-19 |  | 2027-04-02 | 2027-04-15 | PO MR-EL-004 | G-PRC-FAB MR-EL-004 | 2027-07-21 | G-PRC-FAB MR-EL-004 ACCEPTED
10 | ALP-E07-00BRA-ME-ITP-0001 | UPS, Batteries and DC Systems - Supplier Inspection and Test Plan |  | E07 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-03-29 |  | 2027-04-15 | 2027-04-15 | PO MR-EL-007 | G-PRC-FAB MR-EL-007 | 2027-07-21 | G-PRC-FAB MR-EL-007 ACCEPTED
10 | ALP-E05-00BFA-IC-IOL-0001 | LV Switchboards and MCCs - Supplier I/O List, Control Philosophy and Interface Signals |  | E05 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-18 |  | 2027-04-01 | 2027-04-19 | PO MR-EL-005
10 | ALP-E05-00BFA-ME-CAL-0001 | LV Switchboards and MCCs - Supplier Design Calculations |  | E05 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-18 |  | 2027-04-01 | 2027-04-19 | PO MR-EL-005 | G-PRC-FAB MR-EL-005 | 2027-06-21 | G-PRC-FAB MR-EL-005 ACCEPTED
10 | ALP-E07-00BRA-ME-DSH-0001 | UPS, Batteries and DC Systems - Supplier Certified Datasheets and Performance Curves |  | E07 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-15 | 2027-03-29 |  | 2027-04-12 | 2027-04-23 | PO MR-EL-007 | G-PRC-FAB MR-EL-007 | 2027-07-21 | G-PRC-FAB MR-EL-007 ACCEPTED
10 | ALP-E04-00BFT-ME-GAD-0001 | LV Transformers - Supplier GA Drawings |  | E04 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-02 | 2027-03-30 |  | 2027-04-13 | 2027-04-26 | PO MR-EL-004 | G-PRC-FAB MR-EL-004 | 2027-07-21 | G-COM-MC-EL 00BFT IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC G-PRC-FAB MR-EL-004 ACCEPTED
10 | ALP-E02-10BBT-CV-CAL-0001 | Unit Auxiliary Transformers - Supplier Foundation Loads and Anchor Bolt Drawings |  | E02 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-11 | 2027-04-01 |  | 2027-04-15 | 2027-04-29 | PO MR-EL-002 | G-PRC-FAB MR-EL-002 | 2027-07-26 | G-PRC-FAB MR-EL-002 ACCEPTED
10 | ALP-E02-10BBT-ME-DSH-0001 | Unit Auxiliary Transformers - Supplier Certified Datasheets and Performance Curves |  | E02 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-18 |  | 2027-04-01 | 2027-04-29 | PO MR-EL-002 | G-PRC-FAB MR-EL-002 | 2027-07-26 | G-PRC-FAB MR-EL-002 ACCEPTED
10 | ALP-E07-00BRA-ME-GAD-0001 | UPS, Batteries and DC Systems - Supplier GA Drawings |  | E07 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-10 | 2027-04-07 |  | 2027-04-21 | 2027-05-04 | PO MR-EL-007 | G-PRC-FAB MR-EL-007 | 2027-07-21 | G-COM-MC-EL 00BRA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC G-PRC-FAB MR-EL-007 ACCEPTED
10 | ALP-E04-00BFT-IC-IOL-0001 | LV Transformers - Supplier I/O List, Control Philosophy and Interface Signals |  | E04 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-17 | 2027-04-07 |  | 2027-04-21 | 2027-05-05 | PO MR-EL-004
10 | ALP-E04-00BFT-ME-CAL-0001 | LV Transformers - Supplier Design Calculations |  | E04 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-17 | 2027-04-07 |  | 2027-04-21 | 2027-05-05 | PO MR-EL-004 | G-PRC-FAB MR-EL-004 | 2027-07-21 | G-PRC-FAB MR-EL-004 ACCEPTED
10 | ALP-E06-00XJA-EL-WIR-0001 | Emergency Diesel Generator - Supplier Electrical Schematics and Wiring Diagrams |  | E06 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-02-25 | 2027-03-18 |  | 2027-04-01 | 2027-05-07 | PO MR-EL-006 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00XJA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
10 | ALP-E06-00XJA-IC-DSH-0001 | Emergency Diesel Generator - Supplier Instrument List and Datasheets |  | E06 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-03-18 |  | 2027-04-01 | 2027-05-07 | PO MR-EL-006
10 | ALP-E05-00BFA-EL-WIR-0001 | LV Switchboards and MCCs - Supplier Electrical Schematics and Wiring Diagrams |  | E05 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-09 | 2027-03-30 |  | 2027-04-13 | 2027-05-11 | PO MR-EL-005 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BFA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
10 | ALP-E02-10BBT-ME-GAD-0001 | Unit Auxiliary Transformers - Supplier GA Drawings |  | E02 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-04 | 2027-04-01 |  | 2027-04-15 | 2027-05-13 | PO MR-EL-002 | G-PRC-FAB MR-EL-002 | 2027-07-26 | G-COM-MC-EL 10BBT IFC G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC G-PRC-FAB MR-EL-002 ACCEPTED
10 | ALP-E07-00BRA-IC-IOL-0001 | UPS, Batteries and DC Systems - Supplier I/O List, Control Philosophy and Interface Signals |  | E07 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-15 |  | 2027-04-29 | 2027-05-13 | PO MR-EL-007
10 | ALP-E07-00BRA-ME-CAL-0001 | UPS, Batteries and DC Systems - Supplier Design Calculations |  | E07 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-15 |  | 2027-04-29 | 2027-05-13 | PO MR-EL-007 | G-PRC-FAB MR-EL-007 | 2027-07-21 | G-PRC-FAB MR-EL-007 ACCEPTED
10 | ALP-E03-00BBA-ME-LST-0001 | MV Switchgear 10.5 kV - Spare Parts and Special Tools Lists |  | E03 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-10 | 2027-03-31 |  | 2027-04-14 | 2027-05-20 | PO MR-EL-003
10 | ALP-E05-00BFA-ME-LST-0001 | LV Switchboards and MCCs - Spare Parts and Special Tools Lists |  | E05 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-18 | 2027-04-08 |  | 2027-04-22 | 2027-05-20 | PO MR-EL-005
10 | ALP-E06-00XJA-ME-LST-0001 | Emergency Diesel Generator - Spare Parts and Special Tools Lists |  | E06 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-10 | 2027-03-31 |  | 2027-04-14 | 2027-05-20 | PO MR-EL-006
10 | ALP-E02-10BBT-IC-IOL-0001 | Unit Auxiliary Transformers - Supplier I/O List, Control Philosophy and Interface Signals |  | E02 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-15 |  | 2027-04-29 | 2027-05-27 | PO MR-EL-002
10 | ALP-E02-10BBT-ME-CAL-0001 | Unit Auxiliary Transformers - Supplier Design Calculations |  | E02 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-15 |  | 2027-04-29 | 2027-05-27 | PO MR-EL-002 | G-PRC-FAB MR-EL-002 | 2027-07-26 | G-PRC-FAB MR-EL-002 ACCEPTED
10 | ALP-E04-00BFT-ME-LST-0001 | LV Transformers - Spare Parts and Special Tools Lists |  | E04 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-05 | 2027-04-26 |  | 2027-05-10 | 2027-06-01 | PO MR-EL-004
10 | ALP-E07-00BRA-EL-WIR-0001 | UPS, Batteries and DC Systems - Supplier Electrical Schematics and Wiring Diagrams |  | E07 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-04-02 | 2027-04-23 |  | 2027-05-07 | 2027-06-01 | PO MR-EL-007 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-COM-MC-EL 00BRA IFC G-CON-CWP CWP-03-EL-01 IFC G-CON-IWP CWP-03-EL-01 IFC
10 | ALP-E07-00BRA-ME-LST-0001 | UPS, Batteries and DC Systems - Spare Parts and Special Tools Lists |  | E07 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-13 | 2027-05-04 |  | 2027-05-18 | 2027-06-09 | PO MR-EL-007
10 | ALP-E04-00BFT-ME-TST-0001 | LV Transformers - Factory Acceptance Test Procedure |  | E04 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-20 | 2027-05-11 |  | 2027-06-08 | 2027-06-22 | PO MR-EL-004 | G-PRC-FAT MR-EL-004 | 2027-08-03 | G-PRC-FAT MR-EL-004 ACCEPTED
10 | ALP-E02-10BBT-EL-WIR-0001 | Unit Auxiliary Transformers - Supplier Electrical Schematics and Wiring Diagrams |  | E02 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-04-08 | 2027-04-29 |  | 2027-05-13 | 2027-06-24 | PO MR-EL-002 | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-COM-MC-EL 10BBT IFC G-CON-CWP CWP-01-EL-01 IFC G-CON-IWP CWP-01-EL-01 IFC
10 | ALP-E02-10BBT-IC-DSH-0001 | Unit Auxiliary Transformers - Supplier Instrument List and Datasheets |  | E02 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-15 | 2027-04-29 |  | 2027-05-13 | 2027-06-24 | PO MR-EL-002
10 | ALP-E05-00BFA-ME-TST-0001 | LV Switchboards and MCCs - Factory Acceptance Test Procedure |  | E05 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-22 | 2027-05-13 |  | 2027-06-10 | 2027-06-24 | PO MR-EL-005 | G-PRC-FAT MR-EL-005 | 2027-08-05 | G-PRC-FAT MR-EL-005 ACCEPTED
10 | ALP-E07-00BRA-ME-TST-0001 | UPS, Batteries and DC Systems - Factory Acceptance Test Procedure |  | E07 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-28 | 2027-05-19 |  | 2027-06-16 | 2027-06-30 | PO MR-EL-007 | G-PRC-FAT MR-EL-007 | 2027-08-11 | G-PRC-FAT MR-EL-007 ACCEPTED
10 | ALP-E02-10BBT-ME-LST-0001 | Unit Auxiliary Transformers - Spare Parts and Special Tools Lists |  | E02 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-04-22 | 2027-05-13 |  | 2027-05-27 | 2027-07-08 | PO MR-EL-002
10 | ALP-E03-00BBA-ME-TST-0001 | MV Switchgear 10.5 kV - Factory Acceptance Test Procedure |  | E03 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-03 |  | 2027-07-01 | 2027-07-15 | PO MR-EL-003 | G-PRC-FAT MR-EL-003 | 2027-08-26 | G-PRC-FAT MR-EL-003 ACCEPTED
10 | ALP-E06-00XJA-ME-TST-0001 | Emergency Diesel Generator - Factory Acceptance Test Procedure |  | E06 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-13 | 2027-06-03 |  | 2027-07-01 | 2027-07-15 | PO MR-EL-006 | G-PRC-FAT MR-EL-006 | 2027-08-26 | G-PRC-FAT MR-EL-006 ACCEPTED
10 | ALP-E04-00BFT-ME-PRC-0001 | LV Transformers - Supplier Installation and Erection Manual |  | E04 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-18 | 2027-06-08 |  | 2027-06-22 | 2027-07-20 | PO MR-EL-004 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFR
10 | ALP-E05-00BFA-ME-PRC-0001 | LV Switchboards and MCCs - Supplier Installation and Erection Manual |  | E05 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-20 | 2027-06-10 |  | 2027-06-24 | 2027-07-22 | PO MR-EL-005 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFR
10 | ALP-E07-00BRA-ME-PRC-0001 | UPS, Batteries and DC Systems - Supplier Installation and Erection Manual |  | E07 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-26 | 2027-06-16 |  | 2027-06-30 | 2027-07-28 | PO MR-EL-007 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFR
10 | ALP-E03-00BBA-ME-PRC-0001 | MV Switchgear 10.5 kV - Supplier Installation and Erection Manual |  | E03 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-01 |  | 2027-07-15 | 2027-08-12 | PO MR-EL-003 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFR
10 | ALP-E06-00XJA-ME-PRC-0001 | Emergency Diesel Generator - Supplier Installation and Erection Manual |  | E06 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-10 | 2027-07-01 |  | 2027-07-15 | 2027-08-12 | PO MR-EL-006 | G-CON-CWP CWP-03-EL-01 | 2027-10-25 | G-CON-CWP CWP-03-EL-01 IFR
10 | ALP-E04-00BFT-ME-TRP-0001 | LV Transformers - Factory Acceptance Test Report |  | E04 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-27 | 2027-08-03 |  | 2027-08-17 | 2027-08-17 | PO MR-EL-004 | G-PRC-SHP MR-EL-004 | 2027-08-31 | G-PRC-SHP MR-EL-004 ACCEPTED
10 | ALP-E05-00BFA-ME-TRP-0001 | LV Switchboards and MCCs - Factory Acceptance Test Report |  | E05 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-29 | 2027-08-05 |  | 2027-08-19 | 2027-08-19 | PO MR-EL-005 | G-PRC-SHP MR-EL-005 | 2027-09-02 | G-PRC-SHP MR-EL-005 ACCEPTED
10 | ALP-E07-00BRA-ME-TRP-0001 | UPS, Batteries and DC Systems - Factory Acceptance Test Report |  | E07 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-04 | 2027-08-11 |  | 2027-08-25 | 2027-08-25 | PO MR-EL-007 | G-PRC-SHP MR-EL-007 | 2027-09-08 | G-PRC-SHP MR-EL-007 ACCEPTED
10 | ALP-E03-00BBA-ME-TRP-0001 | MV Switchgear 10.5 kV - Factory Acceptance Test Report |  | E03 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-08-26 |  | 2027-09-09 | 2027-09-09 | PO MR-EL-003 | G-PRC-SHP MR-EL-003 | 2027-09-23 | G-PRC-SHP MR-EL-003 ACCEPTED
10 | ALP-E06-00XJA-ME-TRP-0001 | Emergency Diesel Generator - Factory Acceptance Test Report |  | E06 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-08-26 |  | 2027-09-09 | 2027-09-09 | PO MR-EL-006 | G-PRC-SHP MR-EL-006 | 2027-09-23 | G-PRC-SHP MR-EL-006 ACCEPTED
10 | ALP-E02-10BBT-ME-TST-0001 | Unit Auxiliary Transformers - Factory Acceptance Test Procedure |  | E02 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-15 | 2027-08-05 |  | 2027-09-02 | 2027-09-16 | PO MR-EL-002 | G-PRC-FAT MR-EL-002 | 2027-10-28 | G-PRC-FAT MR-EL-002 ACCEPTED
10 | ALP-E04-00BFT-ME-MDB-0001 | LV Transformers - Manufacturing Record Book and Conformity Certificates |  | E04 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-03 | 2027-08-17 |  | 2027-08-17 | 2027-10-12 | PO MR-EL-004 | G-PRC-SHP MR-EL-004 | 2027-08-31 | G-PRC-SHP MR-EL-004 IFR
10 | ALP-E02-10BBT-ME-PRC-0001 | Unit Auxiliary Transformers - Supplier Installation and Erection Manual |  | E02 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-12 | 2027-09-02 |  | 2027-09-16 | 2027-10-14 | PO MR-EL-002 | G-CON-CWP CWP-01-EL-01 | 2028-01-10 | G-CON-CWP CWP-01-EL-01 IFR G-CON-CWP CWP-02-EL-01 IFR
10 | ALP-E05-00BFA-ME-MDB-0001 | LV Switchboards and MCCs - Manufacturing Record Book and Conformity Certificates |  | E05 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-05 | 2027-08-19 |  | 2027-08-19 | 2027-10-14 | PO MR-EL-005 | G-PRC-SHP MR-EL-005 | 2027-09-02 | G-PRC-SHP MR-EL-005 IFR
10 | ALP-E07-00BRA-ME-MDB-0001 | UPS, Batteries and DC Systems - Manufacturing Record Book and Conformity Certificates |  | E07 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-11 | 2027-08-25 |  | 2027-08-25 | 2027-10-20 | PO MR-EL-007 | G-PRC-SHP MR-EL-007 | 2027-09-08 | G-PRC-SHP MR-EL-007 IFR
10 | ALP-E03-00BBA-ME-MDB-0001 | MV Switchgear 10.5 kV - Manufacturing Record Book and Conformity Certificates |  | E03 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-26 | 2027-09-09 |  | 2027-09-09 | 2027-11-04 | PO MR-EL-003 | G-PRC-SHP MR-EL-003 | 2027-09-23 | G-PRC-SHP MR-EL-003 IFR
10 | ALP-E06-00XJA-ME-MDB-0001 | Emergency Diesel Generator - Manufacturing Record Book and Conformity Certificates |  | E06 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-26 | 2027-09-09 |  | 2027-09-09 | 2027-11-04 | PO MR-EL-006 | G-PRC-SHP MR-EL-006 | 2027-09-23 | G-PRC-SHP MR-EL-006 IFR
10 | ALP-E02-10BBT-ME-TRP-0001 | Unit Auxiliary Transformers - Factory Acceptance Test Report |  | E02 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-21 | 2027-10-28 |  | 2027-11-11 | 2027-11-11 | PO MR-EL-002 | G-PRC-SHP MR-EL-002 | 2027-11-25 | G-PRC-SHP MR-EL-002 ACCEPTED
10 | ALP-E04-00BFT-ME-OMM-0001 | LV Transformers - Supplier Operation and Maintenance Manual |  | E04 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-25 | 2027-07-06 |  | 2027-07-20 | 2027-11-23 | PO MR-EL-004 | G-COM-SC-EL 00BFT | 2028-05-09 | G-COM-SC-EL 00BFT IFR G-OPS-HO-EL 00BFT IFC
10 | ALP-E05-00BFA-ME-OMM-0001 | LV Switchboards and MCCs - Supplier Operation and Maintenance Manual |  | E05 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BFA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-05-27 | 2027-07-08 |  | 2027-07-22 | 2027-11-25 | PO MR-EL-005 | G-COM-SC-EL 00BFA | 2028-05-09 | G-COM-SC-EL 00BFA IFR G-COM-SC-EL 00BMA IFR G-OPS-HO-EL 00BFA IFC G-OPS-HO-EL 00BMA IFC
10 | ALP-E07-00BRA-ME-OMM-0001 | UPS, Batteries and DC Systems - Supplier Operation and Maintenance Manual |  | E07 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BRA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-02 | 2027-07-14 |  | 2027-07-28 | 2027-12-01 | PO MR-EL-007 | G-COM-SC-EL 00BRA | 2028-05-09 | G-COM-SC-EL 00BRA IFR G-COM-SC-EL 00BTA IFR G-OPS-HO-EL 00BRA IFC G-OPS-HO-EL 00BTA IFC
10 | ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List |  | EPC | commissioning | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PR-LST-0001 is NONE, IFR needs it at IFR input ALP-EPC-00ACA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BBA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BFA-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BFT-EL-DSH-0001 is NONE, IFR needs it at IFR input ALP-EPC-00BMA-EL-DSH-0001 is NONE, IFR needs it at IFR |  | 2026-11-18 | 2027-11-03 |  | 2027-11-17 | 2027-12-01 | capacity commissioning | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFC G-OWN-TO 00000 IFR
10 | ALP-E03-00BBA-ME-OMM-0001 | MV Switchgear 10.5 kV - Supplier Operation and Maintenance Manual |  | E03 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00BBA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-17 | 2027-07-29 |  | 2027-08-12 | 2027-12-16 | PO MR-EL-003 | G-COM-SC-EL 00BBA | 2028-05-09 | G-COM-SC-EL 00BBA IFR G-OPS-HO-EL 00BBA IFC
10 | ALP-E06-00XJA-ME-OMM-0001 | Emergency Diesel Generator - Supplier Operation and Maintenance Manual |  | E06 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00XJA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-17 | 2027-07-29 |  | 2027-08-12 | 2027-12-16 | PO MR-EL-006 | G-COM-SC-EL 00XJA | 2028-05-09 | G-COM-SC-EL 00XJA IFR G-OPS-HO-EL 00XJA IFC
10 | ALP-E02-10BBT-ME-MDB-0001 | Unit Auxiliary Transformers - Manufacturing Record Book and Conformity Certificates |  | E02 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-10-28 | 2027-11-11 |  | 2027-11-11 | 2028-01-06 | PO MR-EL-002 | G-PRC-SHP MR-EL-002 | 2027-11-25 | G-PRC-SHP MR-EL-002 IFR
10 | ALP-E02-10BBT-ME-OMM-0001 | Unit Auxiliary Transformers - Supplier Operation and Maintenance Manual |  | E02 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-10BBT-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-19 | 2027-09-30 |  | 2027-10-14 | 2028-02-17 | PO MR-EL-002 | G-COM-SC-EL 10BBT | 2028-05-09 | G-COM-SC-EL 10BBT IFR G-COM-SC-EL 20BBT IFR G-OPS-HO-EL 10BBT IFC G-OPS-HO-EL 20BBT IFC
10 | ALP-EPC-00000-PI-M3D-0004 | Plant 3D Model and IFC4 Export - As-Built | native model format | EPC | piping | M3D | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-PI-M3D-0003 is NONE, IFR needs it at IFR |  | 2028-03-23 | 2028-06-15 |  | 2028-06-29 | 2028-07-06 | ALP-EPC-00000-PI-M3D-0003 | G-OPS-AB 00000 | 2029-07-18 | G-OPS-AB 00000 AB
11 | ALP-EPC-00ACA-GE-RPT-0001 | 380 kV GIS - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-11-05 | 2026-11-26 |  | 2026-11-26 | 2026-12-03 | bids MR-EL-001 | G-PRC-PO MR-EL-001 | 2026-12-15 | G-PRC-PO MR-EL-001 IFR
11 | ALP-EPC-00CJA-GE-RPT-0001 | Plant DCS - Technical Bid Evaluation |  | EPC | general | RPT | internal | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-22 | 2027-01-12 |  | 2027-01-12 | 2027-01-19 | capacity general | G-PRC-PO MR-IC-001 | 2027-02-15 | G-PRC-PO MR-IC-001 IFR
11 | ALP-E01-00ACA-ME-ITP-0001 | 380 kV GIS - Supplier Inspection and Test Plan |  | E01 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-29 | 2027-01-12 |  | 2027-02-02 | 2027-02-09 | PO MR-EL-001 | G-PRC-FAB MR-EL-001 | 2027-05-10 | G-PRC-FAB MR-EL-001 ACCEPTED
11 | ALP-E01-00ACA-CV-CAL-0001 | 380 kV GIS - Supplier Foundation Loads and Anchor Bolt Drawings |  | E01 | civil | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-05 | 2027-01-26 |  | 2027-02-09 | 2027-02-23 | PO MR-EL-001 | G-PRC-FAB MR-EL-001 | 2027-05-10 | G-PRC-FAB MR-EL-001 ACCEPTED
11 | ALP-E01-00ACA-ME-DSH-0001 | 380 kV GIS - Supplier Certified Datasheets and Performance Curves |  | E01 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-29 | 2027-01-12 |  | 2027-01-26 | 2027-02-23 | PO MR-EL-001 | G-PRC-FAB MR-EL-001 | 2027-05-10 | G-PRC-FAB MR-EL-001 ACCEPTED
11 | ALP-E01-00ACA-ME-GAD-0001 | 380 kV GIS - Supplier GA Drawings |  | E01 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2026-12-29 | 2027-01-26 |  | 2027-02-09 | 2027-03-09 | PO MR-EL-001 | G-PRC-FAB MR-EL-001 | 2027-05-10 | G-COM-MC-EL 00ACA IFC G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC G-PRC-FAB MR-EL-001 ACCEPTED
11 | ALP-I01-00CJA-ME-ITP-0001 | Plant DCS - Supplier Inspection and Test Plan |  | I01 | mechanical | ITP | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-18 |  | 2027-03-11 | 2027-03-18 | PO MR-IC-001 | G-PRC-FAB MR-IC-001 | 2027-06-07 | G-PRC-FAB MR-IC-001 ACCEPTED
11 | ALP-E01-00ACA-IC-IOL-0001 | 380 kV GIS - Supplier I/O List, Control Philosophy and Interface Signals |  | E01 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-19 | 2027-02-09 |  | 2027-02-23 | 2027-03-23 | PO MR-EL-001
11 | ALP-E01-00ACA-ME-CAL-0001 | 380 kV GIS - Supplier Design Calculations |  | E01 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-01-19 | 2027-02-09 |  | 2027-02-23 | 2027-03-23 | PO MR-EL-001 | G-PRC-FAB MR-EL-001 | 2027-05-10 | G-PRC-FAB MR-EL-001 ACCEPTED
11 | ALP-I01-00CJA-ME-DSH-0001 | Plant DCS - Supplier Certified Datasheets and Performance Curves |  | I01 | mechanical | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-02-18 |  | 2027-03-04 | 2027-04-01 | PO MR-IC-001 | G-PRC-FAB MR-IC-001 | 2027-06-07 | G-PRC-FAB MR-IC-001 ACCEPTED
11 | ALP-I01-00CJA-ME-GAD-0001 | Plant DCS - Supplier GA Drawings |  | I01 | mechanical | GAD | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-04 | 2027-03-04 |  | 2027-03-18 | 2027-04-15 | PO MR-IC-001 | G-PRC-FAB MR-IC-001 | 2027-06-07 | G-COM-MC-FF 00CJA IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC G-PRC-FAB MR-IC-001 ACCEPTED
11 | ALP-E01-00ACA-EL-WIR-0001 | 380 kV GIS - Supplier Electrical Schematics and Wiring Diagrams |  | E01 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-02-02 | 2027-02-23 |  | 2027-03-09 | 2027-04-20 | PO MR-EL-001 | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-COM-MC-EL 00ACA IFC G-CON-CWP CWP-04-EL-01 IFC G-CON-IWP CWP-04-EL-01 IFC
11 | ALP-E01-00ACA-IC-DSH-0001 | 380 kV GIS - Supplier Instrument List and Datasheets |  | E01 | i_and_c | DSH | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-09 | 2027-02-23 |  | 2027-03-09 | 2027-04-20 | PO MR-EL-001
11 | ALP-EPC-00UBA-CV-EFD-0001 | Electrical Building - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBA-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-E06-00XJA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-02-22 | 2027-03-16 | 2027-04-13 | 2027-04-13 | 2027-04-20 | ALP-E06-00XJA-CV-CAL-0001 | G-CON-CWP CWP-03-CV-01 | 2027-03-29 | G-CON-CWP CWP-03-CV-01 IFC G-CON-IWP CWP-03-CV-01 IFC
11 | ALP-I01-00CJA-IC-IOL-0001 | Plant DCS - Supplier I/O List, Control Philosophy and Interface Signals |  | I01 | i_and_c | IOL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-18 |  | 2027-04-01 | 2027-04-29 | PO MR-IC-001
11 | ALP-I01-00CJA-ME-CAL-0001 | Plant DCS - Supplier Design Calculations |  | I01 | mechanical | CAL | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-25 | 2027-03-18 |  | 2027-04-01 | 2027-04-29 | PO MR-IC-001 | G-PRC-FAB MR-IC-001 | 2027-06-07 | G-PRC-FAB MR-IC-001 ACCEPTED
11 | ALP-E01-00ACA-ME-LST-0001 | 380 kV GIS - Spare Parts and Special Tools Lists |  | E01 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-02-16 | 2027-03-09 |  | 2027-03-23 | 2027-05-04 | PO MR-EL-001
11 | ALP-I01-00CJA-EL-WIR-0001 | Plant DCS - Supplier Electrical Schematics and Wiring Diagrams |  | I01 | electrical | WIR | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFC |  | 2027-03-11 | 2027-04-01 |  | 2027-04-15 | 2027-05-27 | PO MR-IC-001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-COM-MC-FF 00CJA IFC G-CON-CWP CWP-11-IC-01 IFC G-CON-IWP CWP-11-IC-01 IFC
11 | ALP-I01-00CJA-ME-LST-0001 | Plant DCS - Spare Parts and Special Tools Lists |  | I01 | mechanical | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-03-25 | 2027-04-15 |  | 2027-04-29 | 2027-06-10 | PO MR-IC-001
11 | ALP-EPC-00UBF-CV-EFD-0001 | Transformer Bays - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UBF-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-E02-10BBT-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10BAT-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10MBA-CV-CAL-0001 is NONE, IFR needs it at IFR input ALP-IEC-10HAA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-04-19 | 2027-05-17 | 2027-06-14 | 2027-06-14 | 2027-06-21 | capacity civil | G-CON-CWP CWP-01-CV-02 | 2027-04-19 | G-CON-CWP CWP-01-CV-02 IFC G-CON-IWP CWP-01-CV-02 IFC
11 | ALP-I01-00CJA-ME-TST-0001 | Plant DCS - Factory Acceptance Test Procedure |  | I01 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-06-17 | 2027-07-08 |  | 2027-08-05 | 2027-08-19 | PO MR-IC-001 | G-PRC-FAT MR-IC-001 | 2027-09-30 | G-PRC-FAT MR-IC-001 ACCEPTED
11 | ALP-I01-00CJA-ME-PRC-0001 | Plant DCS - Supplier Installation and Erection Manual |  | I01 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-15 | 2027-08-05 |  | 2027-08-19 | 2027-09-16 | PO MR-IC-001 | G-CON-CWP CWP-11-IC-01 | 2027-11-22 | G-CON-CWP CWP-11-IC-01 IFR
11 | ALP-E01-00ACA-ME-TST-0001 | 380 kV GIS - Factory Acceptance Test Procedure |  | E01 | mechanical | TST | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-03 | 2027-08-24 |  | 2027-09-21 | 2027-10-05 | PO MR-EL-001 | G-PRC-FAT MR-EL-001 | 2027-11-16 | G-PRC-FAT MR-EL-001 ACCEPTED
11 | ALP-I01-00CJA-ME-TRP-0001 | Plant DCS - Factory Acceptance Test Report |  | I01 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-23 | 2027-09-30 |  | 2027-10-14 | 2027-10-14 | PO MR-IC-001 | G-PRC-SHP MR-IC-001 | 2027-10-28 | G-PRC-SHP MR-IC-001 ACCEPTED
11 | ALP-E01-00ACA-ME-PRC-0001 | 380 kV GIS - Supplier Installation and Erection Manual |  | E01 | mechanical | PRC | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-08-31 | 2027-09-21 |  | 2027-10-05 | 2027-11-02 | PO MR-EL-001 | G-CON-CWP CWP-04-EL-01 | 2028-01-04 | G-CON-CWP CWP-04-EL-01 IFR
11 | ALP-E01-00ACA-ME-TRP-0001 | 380 kV GIS - Factory Acceptance Test Report |  | E01 | mechanical | TRP | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-11-09 | 2027-11-16 |  | 2027-11-30 | 2027-11-30 | PO MR-EL-001 | G-PRC-SHP MR-EL-001 | 2027-12-14 | G-PRC-SHP MR-EL-001 ACCEPTED
11 | ALP-I01-00CJA-ME-MDB-0001 | Plant DCS - Manufacturing Record Book and Conformity Certificates |  | I01 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-30 | 2027-10-14 |  | 2027-10-14 | 2027-12-09 | PO MR-IC-001 | G-PRC-SHP MR-IC-001 | 2027-10-28 | G-PRC-SHP MR-IC-001 IFR
11 | ALP-EPC-00000-CM-LST-0004 | Special Tools List |  | EPC | commissioning | LST | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00000-CM-LST-0002 is NONE, IFR needs it at IFR |  | 2027-11-03 | 2027-11-24 |  | 2027-12-08 | 2027-12-22 | ALP-EPC-00000-CM-LST-0002 | G-OWN-TO 00000 | 2029-04-18 | G-OWN-TO 00000 IFR
11 | ALP-I01-00CJA-ME-OMM-0001 | Plant DCS - Supplier Operation and Maintenance Manual |  | I01 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00CJA-IC-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-07-22 | 2027-09-02 |  | 2027-09-16 | 2028-01-20 | PO MR-IC-001 | G-COM-SC-FF 00CJA | 2028-07-24 | G-COM-SC-FF 00CJA IFR G-OPS-HO-FF 00CJA IFC
11 | ALP-E01-00ACA-ME-MDB-0001 | 380 kV GIS - Manufacturing Record Book and Conformity Certificates |  | E01 | mechanical | MDB | information | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-11-16 | 2027-11-30 |  | 2027-11-30 | 2028-01-25 | PO MR-EL-001 | G-PRC-SHP MR-EL-001 | 2027-12-14 | G-PRC-SHP MR-EL-001 IFR
11 | ALP-E01-00ACA-ME-OMM-0001 | 380 kV GIS - Supplier Operation and Maintenance Manual |  | E01 | mechanical | OMM | review | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00ACA-EL-MRQ-0001 is NONE, IFR needs it at IFR |  | 2027-09-07 | 2027-10-19 |  | 2027-11-02 | 2028-03-07 | PO MR-EL-001 | G-COM-SC-EL 00ACA | 2028-05-09 | G-COM-SC-EL 00ACA IFR G-OPS-HO-EL 00ACA IFC
12 | ALP-EPC-00UAC-CV-EFD-0001 | GIS Building - Equipment Foundation Drawings |  | EPC | civil | EFD | approval | NONE |  |  | issue IFR | IFR | A | no | input ALP-EPC-00UAC-CV-FND-0001 is NONE, IFR needs it at IFR input ALP-E01-00ACA-CV-CAL-0001 is NONE, IFR needs it at IFR |  | 2027-02-18 | 2027-03-12 | 2027-04-09 | 2027-04-09 | 2027-04-16 | ALP-EPC-00UAC-CV-FND-0001 | G-CON-CWP CWP-04-CV-01 | 2027-04-05 | G-CON-CWP CWP-04-CV-01 IFC G-CON-IWP CWP-04-CV-01 IFC

## Release sequence
Alpilla 600 MW Combined Cycle Power Plant - Release sequence (print version of the release plan)
engine release_control v1.2.0 ¦ generated 2026-09-29T02:52:27Z by SETUP ¦ data 6d73bc5813f68e2b ¦ planned dates from the levelled workflow network and the CPM (working days)
Wave | Document | Title | Status now | Next | Rev | Can issue | Planned IFR | Planned IFC | First gate | Gate need
1 | ALP-IEC-00000-GE-LST-0001 | Power Island - Terminal Points and Interface Data | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-11-02 | G-OWN-TO 00000 | 2029-04-18
1 | ALP-IEC-00000-GE-RPT-0001 | Power Island and Balance of Plant - Division of Responsibility | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-11-02
1 | ALP-IEC-00000-GE-SPC-0001 | Power Island Interface Requirements to the EPC | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-11-02
1 | ALP-IEC-10MBA-PR-HMB-0001 | Power Island Thermal Performance Data | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-11-02
1 | ALP-IEC-10MBA-PR-HMB-0002 | Power Island Off-Design Heat Balances | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-11-02
1 | ALP-EPC-00GQA-CM-MDB-0001 | Storm Water Drainage - System Turnover Dossier | NONE | IFR | A | yes | 2026-11-25 | 2026-12-02
1 | ALP-EPC-00000-CV-RPT-0003 | Topographic Survey and Site Setting-Out Report | IFR |  |  | - | 2026-11-20 | 2026-12-11
1 | ALP-EPC-00000-GE-PRC-0002 | Document Numbering and Document Control Procedure | IFR |  |  | - | 2026-11-13 | 2026-12-18
1 | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | IFR |  |  | - | 2026-11-16 | 2026-12-28 | G-OWN-BDP 00000 | 2027-04-02
1 | ALP-IEC-10BAT-EL-DSH-0001 | Generator Step-Up Transformers - Supplier Certified Datasheets and Performance Curves | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-12-28 | G-PRC-FAB MR-EL-102 | 2027-03-22
1 | ALP-IEC-10BAT-ME-ITP-0001 | Generator Step-Up Transformers - Supplier Inspection and Test Plan | NONE | IFR | A | yes | 2026-11-30 | 2026-12-28 | G-PRC-FAB MR-EL-102 | 2027-03-22
1 | ALP-IEC-10HAA-ME-DSH-0001 | HRSG incl. SCR - Supplier Certified Datasheets and Performance Curves | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-12-28 | G-PRC-FAB MR-ME-102 | 2027-03-16
1 | ALP-IEC-10HAA-ME-ITP-0001 | HRSG incl. SCR - Supplier Inspection and Test Plan | NONE | IFR | A | yes | 2026-11-30 | 2026-12-28 | G-PRC-FAB MR-ME-102 | 2027-03-16
1 | ALP-IEC-10MBA-ME-DSH-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Certified Datasheets and Performance Curves | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-12-28 | G-PRC-FAB MR-ME-101 | 2027-03-22
1 | ALP-IEC-10MBY-ME-ITP-0001 | Turbine Control System - Supplier Inspection and Test Plan | NONE | IFR | A | yes | 2026-11-30 | 2026-12-28 | G-PRC-FAB MR-IC-101 | 2027-02-22
1 | ALP-IEC-10MKA-EL-DSH-0001 | Generators, Excitation, GCB and Busducts - Supplier Certified Datasheets and Performance Curves | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-12-28 | G-PRC-FAB MR-EL-101 | 2027-03-18
1 | ALP-IEC-10MKA-ME-ITP-0001 | Generators, Excitation, GCB and Busducts - Supplier Inspection and Test Plan | NONE | IFR | A | yes | 2026-11-30 | 2026-12-28 | G-PRC-FAB MR-EL-101 | 2027-03-18
1 | ALP-IEC-20MAA-ME-DSH-0001 | Steam Turbine and Condenser - Supplier Certified Datasheets and Performance Curves | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-12-28 | G-PRC-FAB MR-ME-103 | 2027-04-07
1 | ALP-IEC-20MAA-ME-ITP-0001 | Steam Turbine and Condenser - Supplier Inspection and Test Plan | NONE | IFR | A | yes | 2026-11-30 | 2026-12-28 | G-PRC-FAB MR-ME-103 | 2027-04-07
1 | ALP-IEC-20MAG-ME-DSH-0001 | Seawater-Cooled Surface Condenser - Datasheet | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2026-12-28
1 | ALP-EPC-00000-GE-PRC-0001 | KKS Identification Manual | IFR |  |  | - | 2026-11-20 | 2027-01-01 | G-OWN-BDP 00000 | 2027-04-02
1 | ALP-IEC-10BAT-CV-CAL-0001 | Generator Step-Up Transformers - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | yes | 2026-12-14 | 2027-01-11 | G-PRC-FAB MR-EL-102 | 2027-03-22
1 | ALP-IEC-10BAT-EL-GAD-0001 | Generator Step-Up Transformers - Supplier GA Drawings | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2027-01-11 | G-PRC-FAB MR-EL-102 | 2027-03-22
1 | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | yes | 2026-12-14 | 2027-01-11 | G-PRC-FAB MR-ME-102 | 2027-03-16
1 | ALP-IEC-10HAA-ME-GAD-0001 | HRSG incl. SCR - Supplier GA Drawings | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2027-01-11 | G-PRC-FAB MR-ME-102 | 2027-03-16
1 | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | yes | 2026-12-14 | 2027-01-11 | G-PRC-FAB MR-ME-101 | 2027-03-22
1 | ALP-IEC-10MBA-ME-GAD-0001 | Gas Turbine Package incl. Auxiliaries - Supplier GA Drawings | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2027-01-11 | G-PRC-FAB MR-ME-101 | 2027-03-22
1 | ALP-IEC-10MBA-ME-LAY-0001 | Power Island Arrangement - Installation and Maintenance Spaces | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2027-01-11 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
1 | ALP-IEC-10MBY-ME-DSH-0001 | Turbine Control System - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | yes | 2026-11-30 | 2027-01-11 | G-PRC-FAB MR-IC-101 | 2027-02-22
1 | ALP-IEC-10MKA-CV-CAL-0001 | Generators, Excitation, GCB and Busducts - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | yes | 2026-12-14 | 2027-01-11 | G-PRC-FAB MR-EL-101 | 2027-03-18
1 | ALP-IEC-20MAA-ME-GAD-0001 | Steam Turbine and Condenser - Supplier GA Drawings | ACCEPTED | IFC | 0 | yes | 2026-09-28 | 2027-01-11 | G-PRC-FAB MR-ME-103 | 2027-04-07
1 | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | NONE | IFR | A | yes | 2026-12-28 | 2027-01-25 | G-OWN-TO 00000 | 2029-04-18
1 | ALP-IEC-10MBY-ME-GAD-0001 | Turbine Control System - Supplier GA Drawings | NONE | IFR | A | yes | 2026-12-14 | 2027-01-25 | G-PRC-FAB MR-IC-101 | 2027-02-22
1 | ALP-IEC-10MKA-ME-GAD-0001 | Generators, Excitation, GCB and Busducts - Supplier GA Drawings | NONE | IFR | A | yes | 2026-12-14 | 2027-01-25 | G-PRC-FAB MR-EL-101 | 2027-03-18
1 | ALP-IEC-20MAA-CV-CAL-0001 | Steam Turbine and Condenser - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | yes | 2026-12-28 | 2027-01-25 | G-PRC-FAB MR-ME-103 | 2027-04-07
1 | ALP-IEC-10BAA-EL-SLD-0001 | Power Island Single Line Diagram | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08 | G-OPS-AB 00000 | 2029-07-18
1 | ALP-IEC-10BAT-IC-IOL-0001 | Generator Step-Up Transformers - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08
1 | ALP-IEC-10BAT-ME-CAL-0001 | Generator Step-Up Transformers - Supplier Design Calculations | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08 | G-PRC-FAB MR-EL-102 | 2027-03-22
1 | ALP-IEC-10HAA-IC-IOL-0001 | HRSG incl. SCR - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08
1 | ALP-IEC-10HAA-ME-CAL-0001 | HRSG incl. SCR - Supplier Design Calculations | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08 | G-PRC-FAB MR-ME-102 | 2027-03-16
1 | ALP-IEC-10MBA-EL-LST-0001 | Power Island Electrical Load List | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08
1 | ALP-IEC-10MBA-IC-IOL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08
1 | ALP-IEC-10MBA-ME-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Design Calculations | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08 | G-PRC-FAB MR-ME-101 | 2027-03-22
1 | ALP-IEC-10MBY-ME-CAL-0001 | Turbine Control System - Supplier Design Calculations | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08 | G-PRC-FAB MR-IC-101 | 2027-02-22
1 | ALP-IEC-10MKA-IC-IOL-0001 | Generators, Excitation, GCB and Busducts - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08
1 | ALP-IEC-10MKA-ME-CAL-0001 | Generators, Excitation, GCB and Busducts - Supplier Design Calculations | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08 | G-PRC-FAB MR-EL-101 | 2027-03-18
1 | ALP-IEC-20MAA-IC-IOL-0001 | Steam Turbine and Condenser - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08
1 | ALP-IEC-20MAA-ME-CAL-0001 | Steam Turbine and Condenser - Supplier Design Calculations | NONE | IFR | A | yes | 2026-12-28 | 2027-02-08 | G-PRC-FAB MR-ME-103 | 2027-04-07
1 | ALP-IEC-10MBA-HS-RPT-0001 | Power Island Noise Data | NONE | IFR | A | yes | 2027-01-11 | 2027-02-22
1 | ALP-IEC-10MBA-ME-ITP-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Inspection and Test Plan | NONE | IFR | A | yes | 2027-01-25 | 2027-02-22 | G-PRC-FAB MR-ME-101 | 2027-03-22
1 | ALP-IEC-10MBY-IC-BLK-0001 | TCS Architecture and DCS Integration | NONE | IFR | A | yes | 2027-01-11 | 2027-02-22
1 | ALP-IEC-10BAT-EL-WIR-0001 | Generator Step-Up Transformers - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
1 | ALP-IEC-10BAT-IC-DSH-0001 | Generator Step-Up Transformers - Supplier Instrument List and Datasheets | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-10HAA-EL-WIR-0001 | HRSG incl. SCR - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
1 | ALP-IEC-10HAA-IC-DSH-0001 | HRSG incl. SCR - Supplier Instrument List and Datasheets, Part 1 of 2 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-10HAA-IC-DSH-0002 | HRSG incl. SCR - Supplier Instrument List and Datasheets, Part 2 of 2 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-10HAA-PR-PID-0001 | HRSG incl. SCR - Supplier P&IDs | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-PRC-FAB MR-ME-102 | 2027-03-16
1 | ALP-IEC-10MBA-EL-WIR-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Electrical Schematics and Wiring Diagrams, Part 1 of 2 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
1 | ALP-IEC-10MBA-EL-WIR-0002 | Gas Turbine Package incl. Auxiliaries - Supplier Electrical Schematics and Wiring Diagrams, Part 2 of 2 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
1 | ALP-IEC-10MBA-IC-DSH-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Instrument List and Datasheets, Part 1 of 3 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-10MBA-IC-DSH-0002 | Gas Turbine Package incl. Auxiliaries - Supplier Instrument List and Datasheets, Part 2 of 3 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-10MBA-IC-DSH-0003 | Gas Turbine Package incl. Auxiliaries - Supplier Instrument List and Datasheets, Part 3 of 3 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-10MBA-PR-PID-0001 | Gas Turbine Package incl. Auxiliaries - Supplier P&IDs | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-PRC-FAB MR-ME-101 | 2027-03-22
1 | ALP-IEC-10MBY-EL-WIR-0001 | Turbine Control System - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
1 | ALP-IEC-10MKA-EL-WIR-0001 | Generators, Excitation, GCB and Busducts - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
1 | ALP-IEC-10MKA-IC-DSH-0001 | Generators, Excitation, GCB and Busducts - Supplier Instrument List and Datasheets | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-20MAA-EL-WIR-0001 | Steam Turbine and Condenser - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08 | G-CON-CWP CWP-02-ME-01 | 2027-12-20
1 | ALP-IEC-20MAA-IC-DSH-0001 | Steam Turbine and Condenser - Supplier Instrument List and Datasheets, Part 1 of 2 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-20MAA-IC-DSH-0002 | Steam Turbine and Condenser - Supplier Instrument List and Datasheets, Part 2 of 2 | NONE | IFR | A | yes | 2027-01-11 | 2027-03-08
1 | ALP-IEC-10BAT-ME-LST-0001 | Generator Step-Up Transformers - Spare Parts and Special Tools Lists | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22
1 | ALP-IEC-10HAA-ME-LST-0001 | HRSG incl. SCR - Spare Parts and Special Tools Lists | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22
1 | ALP-IEC-10MBA-ME-LST-0001 | Gas Turbine Package incl. Auxiliaries - Spare Parts and Special Tools Lists | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22
1 | ALP-IEC-10MBY-ME-LST-0001 | Turbine Control System - Spare Parts and Special Tools Lists | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22
1 | ALP-IEC-10MKA-EL-RPT-0001 | Generator Capability Curves and Dynamic Models | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22
1 | ALP-IEC-10MKA-ME-LST-0001 | Generators, Excitation, GCB and Busducts - Spare Parts and Special Tools Lists | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22
1 | ALP-IEC-10MKA-PR-PID-0001 | Generators, Excitation, GCB and Busducts - Supplier P&IDs | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22 | G-PRC-FAB MR-EL-101 | 2027-03-18
1 | ALP-IEC-20MAA-ME-LST-0001 | Steam Turbine and Condenser - Spare Parts and Special Tools Lists | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22
1 | ALP-IEC-20MAA-PR-PID-0001 | Steam Turbine and Condenser - Supplier P&IDs | NONE | IFR | A | yes | 2027-01-25 | 2027-03-22 | G-PRC-FAB MR-ME-103 | 2027-04-07
1 | ALP-IEC-10MBY-IC-CNR-0001 | Power Island Operating and Control Description | NONE | IFR | A | yes | 2027-02-08 | 2027-04-05
1 | ALP-IEC-10MBA-PI-M3D-0001 | Power Island 3D Model Export | NONE | IFR | A | yes | 2027-02-22 | 2027-04-19
1 | ALP-IEC-10MBY-IC-IOL-0001 | Turbine Control System - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | yes | 2027-02-22 | 2027-04-19
1 | ALP-IEC-10MBY-ME-TST-0001 | Turbine Control System - Factory Acceptance Test Procedure | NONE | IFR | A | yes | 2027-04-19 | 2027-05-31 | G-PRC-FAT MR-IC-101 | 2027-07-12
1 | ALP-IEC-10MBY-CM-CMP-0001 | Turbine Control System - Supplier Commissioning Procedures | NONE | IFR | A | yes | 2027-03-22 | 2027-06-14 | G-COM-SC-FF 10MBY | 2028-07-24
1 | ALP-IEC-10MBY-IC-LOG-0001 | Turbine Control System - Supplier Logic Diagrams, Part 1 of 6 | NONE | IFR | A | yes | 2027-03-22 | 2027-06-14
1 | ALP-IEC-10MBY-IC-LOG-0002 | Turbine Control System - Supplier Logic Diagrams, Part 2 of 6 | NONE | IFR | A | yes | 2027-03-22 | 2027-06-14
1 | ALP-IEC-10MBY-IC-LOG-0003 | Turbine Control System - Supplier Logic Diagrams, Part 3 of 6 | NONE | IFR | A | yes | 2027-03-22 | 2027-06-14
1 | ALP-IEC-10MBY-IC-LOG-0004 | Turbine Control System - Supplier Logic Diagrams, Part 4 of 6 | NONE | IFR | A | yes | 2027-03-22 | 2027-06-14
1 | ALP-IEC-10MBY-IC-LOG-0005 | Turbine Control System - Supplier Logic Diagrams, Part 5 of 6 | NONE | IFR | A | yes | 2027-03-22 | 2027-06-14
1 | ALP-IEC-10MBY-IC-LOG-0006 | Turbine Control System - Supplier Logic Diagrams, Part 6 of 6 | NONE | IFR | A | yes | 2027-03-22 | 2027-06-14
1 | ALP-IEC-10MBY-ME-PRC-0001 | Turbine Control System - Supplier Installation and Erection Manual | NONE | IFR | A | yes | 2027-05-17 | 2027-06-28 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
1 | ALP-IEC-10HAA-ME-TST-0001 | HRSG incl. SCR - Factory Acceptance Test Procedure | NONE | IFR | A | yes | 2027-06-14 | 2027-07-26 | G-PRC-FAT MR-ME-102 | 2027-09-06
1 | ALP-IEC-10MBY-IC-CBL-0001 | Power Island Cable List | NONE | IFR | A | yes | 2027-05-31 | 2027-07-26 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
1 | ALP-IEC-10MBY-ME-TRP-0001 | Turbine Control System - Factory Acceptance Test Report | NONE | IFR | A | yes | 2027-07-12 | 2027-07-26 | G-PRC-SHP MR-IC-101 | 2027-08-09
1 | ALP-IEC-10MKA-ME-TST-0001 | Generators, Excitation, GCB and Busducts - Factory Acceptance Test Procedure | NONE | IFR | A | yes | 2027-06-21 | 2027-08-02 | G-PRC-FAT MR-EL-101 | 2027-09-13
1 | ALP-IEC-10BAT-ME-TST-0001 | Generator Step-Up Transformers - Factory Acceptance Test Procedure | NONE | IFR | A | yes | 2027-06-28 | 2027-08-09 | G-PRC-FAT MR-EL-102 | 2027-09-20
1 | ALP-IEC-10HAA-CM-CMP-0001 | HRSG incl. SCR - Supplier Commissioning Procedures | NONE | IFR | A | yes | 2027-05-17 | 2027-08-09 | G-COM-SC-FF 10HAA | 2028-07-24
1 | ALP-IEC-10MBA-ME-TST-0001 | Gas Turbine Package incl. Auxiliaries - Factory Acceptance Test Procedure | NONE | IFR | A | yes | 2027-06-28 | 2027-08-09 | G-PRC-FAT MR-ME-101 | 2027-09-20
1 | ALP-IEC-10MKA-CM-CMP-0001 | Generators, Excitation, GCB and Busducts - Supplier Commissioning Procedures | NONE | IFR | A | yes | 2027-05-24 | 2027-08-16 | G-COM-SC-EL 10BAA | 2028-05-09
1 | ALP-IEC-10BAT-CM-CMP-0001 | Generator Step-Up Transformers - Supplier Commissioning Procedures | NONE | IFR | A | yes | 2027-05-31 | 2027-08-23 | G-COM-SC-EL 10BAT | 2028-05-09
1 | ALP-IEC-10HAA-ME-PRC-0001 | HRSG incl. SCR - Supplier Installation and Erection Manual | NONE | IFR | A | yes | 2027-07-12 | 2027-08-23 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
1 | ALP-IEC-10MBA-CM-CMP-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Commissioning Procedures | NONE | IFR | A | yes | 2027-05-31 | 2027-08-23 | G-COM-SC-FF 10MBA | 2028-07-24
1 | ALP-IEC-10MKA-ME-PRC-0001 | Generators, Excitation, GCB and Busducts - Supplier Installation and Erection Manual | NONE | IFR | A | yes | 2027-07-19 | 2027-08-30 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
1 | ALP-IEC-10BAT-ME-PRC-0001 | Generator Step-Up Transformers - Supplier Installation and Erection Manual | NONE | IFR | A | yes | 2027-07-26 | 2027-09-06 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
1 | ALP-IEC-10MBA-ME-PRC-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Installation and Erection Manual | NONE | IFR | A | yes | 2027-07-12 | 2027-09-06 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
1 | ALP-IEC-10HAA-ME-TRP-0001 | HRSG incl. SCR - Factory Acceptance Test Report | NONE | IFR | A | yes | 2027-09-06 | 2027-09-20 | G-PRC-SHP MR-ME-102 | 2027-10-04
1 | ALP-IEC-10MBY-ME-MDB-0001 | Turbine Control System - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | yes | 2027-07-26 | 2027-09-20 | G-PRC-SHP MR-IC-101 | 2027-08-09
1 | ALP-IEC-20MAA-ME-TST-0001 | Steam Turbine and Condenser - Factory Acceptance Test Procedure | NONE | IFR | A | yes | 2027-08-09 | 2027-09-20 | G-PRC-FAT MR-ME-103 | 2027-11-01
1 | ALP-IEC-10MKA-ME-TRP-0001 | Generators, Excitation, GCB and Busducts - Factory Acceptance Test Report | NONE | IFR | A | yes | 2027-09-13 | 2027-09-27 | G-PRC-SHP MR-EL-101 | 2027-10-11
1 | ALP-IEC-10BAT-ME-TRP-0001 | Generator Step-Up Transformers - Factory Acceptance Test Report | NONE | IFR | A | yes | 2027-09-20 | 2027-10-04 | G-PRC-SHP MR-EL-102 | 2027-10-18
1 | ALP-IEC-10MBA-ME-RPT-0001 | Maintenance Concept and Long-Term Service Offer | NONE | IFR | A | yes | 2027-08-09 | 2027-10-04
1 | ALP-IEC-10MBA-ME-TRP-0001 | Gas Turbine Package incl. Auxiliaries - Factory Acceptance Test Report | NONE | IFR | A | yes | 2027-09-20 | 2027-10-04 | G-PRC-SHP MR-ME-101 | 2027-10-18
1 | ALP-IEC-20MAA-CM-CMP-0001 | Steam Turbine and Condenser - Supplier Commissioning Procedures | NONE | IFR | A | yes | 2027-07-12 | 2027-10-04 | G-COM-SC-WS 20MAA | 2028-09-25
1 | ALP-IEC-20MAA-ME-PRC-0001 | Steam Turbine and Condenser - Supplier Installation and Erection Manual | NONE | IFR | A | yes | 2027-09-06 | 2027-10-18 | G-CON-CWP CWP-02-ME-01 | 2027-12-20
1 | ALP-IEC-10MBY-ME-OMM-0001 | Turbine Control System - Supplier Operation and Maintenance Manual | NONE | IFR | A | yes | 2027-06-14 | 2027-11-01 | G-COM-SC-FF 10MBY | 2028-07-24
1 | ALP-IEC-10HAA-ME-MDB-0001 | HRSG incl. SCR - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | yes | 2027-09-20 | 2027-11-15 | G-PRC-SHP MR-ME-102 | 2027-10-04
1 | ALP-IEC-20MAA-ME-TRP-0001 | Steam Turbine and Condenser - Factory Acceptance Test Report | NONE | IFR | A | yes | 2027-11-01 | 2027-11-15 | G-PRC-SHP MR-ME-103 | 2027-11-29
1 | ALP-IEC-10MKA-ME-MDB-0001 | Generators, Excitation, GCB and Busducts - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | yes | 2027-09-27 | 2027-11-22 | G-PRC-SHP MR-EL-101 | 2027-10-11
1 | ALP-IEC-10BAT-ME-MDB-0001 | Generator Step-Up Transformers - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | yes | 2027-10-04 | 2027-11-29 | G-PRC-SHP MR-EL-102 | 2027-10-18
1 | ALP-IEC-10MBA-ME-MDB-0001 | Gas Turbine Package incl. Auxiliaries - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | yes | 2027-10-04 | 2027-11-29 | G-PRC-SHP MR-ME-101 | 2027-10-18
1 | ALP-IEC-10HAA-ME-OMM-0001 | HRSG incl. SCR - Supplier Operation and Maintenance Manual | NONE | IFR | A | yes | 2027-08-09 | 2027-12-27 | G-COM-SC-FF 10HAA | 2028-07-24
1 | ALP-IEC-10MKA-ME-OMM-0001 | Generators, Excitation, GCB and Busducts - Supplier Operation and Maintenance Manual | NONE | IFR | A | yes | 2027-08-16 | 2028-01-03 | G-COM-SC-EL 10BAA | 2028-05-09
1 | ALP-IEC-10BAT-ME-OMM-0001 | Generator Step-Up Transformers - Supplier Operation and Maintenance Manual | NONE | IFR | A | yes | 2027-08-23 | 2028-01-10 | G-COM-SC-EL 10BAT | 2028-05-09
1 | ALP-IEC-20MAA-ME-MDB-0001 | Steam Turbine and Condenser - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | yes | 2027-11-15 | 2028-01-10 | G-PRC-SHP MR-ME-103 | 2027-11-29
1 | ALP-EPC-10BAA-CM-MDB-0001 | GT Generator Busduct - System Turnover Dossier | NONE | IFR | A | yes | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 10BAA | 2028-04-11
1 | ALP-EPC-10BAC-CM-MDB-0001 | GT Generator Circuit Breaker - System Turnover Dossier | NONE | IFR | A | yes | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 10BAC | 2028-04-11
1 | ALP-EPC-10BAT-CM-MDB-0001 | GT Generator Step-Up Transformer - System Turnover Dossier | NONE | IFR | A | yes | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 10BAT | 2028-04-11
1 | ALP-EPC-20BAA-CM-MDB-0001 | ST Generator Busduct - System Turnover Dossier | NONE | IFR | A | yes | 2028-02-01 | 2028-02-08 | G-COM-MC-EL 20BAA | 2028-04-11
1 | ALP-EPC-20BAC-CM-MDB-0001 | ST Generator Circuit Breaker - System Turnover Dossier | NONE | IFR | A | yes | 2028-02-01 | 2028-02-08 | G-COM-MC-EL 20BAC | 2028-04-11
1 | ALP-EPC-20BAT-CM-MDB-0001 | ST Generator Step-Up Transformer - System Turnover Dossier | NONE | IFR | A | yes | 2028-02-01 | 2028-02-08 | G-COM-MC-EL 20BAT | 2028-04-11
1 | ALP-IEC-20MAA-ME-OMM-0001 | Steam Turbine and Condenser - Supplier Operation and Maintenance Manual | NONE | IFR | A | yes | 2027-10-04 | 2028-02-21 | G-COM-SC-WS 20MAA | 2028-09-25
1 | ALP-EPC-10HAA-CM-MDB-0001 | HRSG Pressure System - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 10HAA | 2028-06-26
1 | ALP-EPC-10HNA-CM-MDB-0001 | HRSG Flue Gas Ducting - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 10HNA | 2028-06-26
1 | ALP-EPC-10HSA-CM-MDB-0001 | SCR Catalyst and Ammonia Injection - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 10HSA | 2028-06-26
1 | ALP-EPC-10MBA-CM-MDB-0001 | Gas Turbine - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 10MBA | 2028-06-26
1 | ALP-EPC-10MBL-CM-MDB-0001 | GT Inlet Air System - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 10MBL | 2028-06-26
1 | ALP-EPC-10MBN-CM-MDB-0001 | GT Liquid Fuel and Water Injection - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 10MBN | 2028-06-26
1 | ALP-EPC-10MBP-CM-MDB-0001 | GT Fuel Gas System incl. Performance Heater - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 10MBP | 2028-06-26
1 | ALP-EPC-10MBU-CM-MDB-0001 | GT Compressor Washing - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 10MBU | 2028-06-26
1 | ALP-EPC-10MBV-CM-MDB-0001 | GT Lube Oil System - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 10MBV | 2028-06-26
1 | ALP-EPC-10MBY-CM-MDB-0001 | GT Control and Protection - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 10MBY | 2028-06-26
1 | ALP-EPC-10MKA-CM-MDB-0001 | GT Generator - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 10MKA | 2028-06-26
1 | ALP-EPC-10MKC-CM-MDB-0001 | GT Excitation and Static Frequency Converter - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 10MKC | 2028-06-26
1 | ALP-EPC-10MKG-CM-MDB-0001 | GT Generator Gas System - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 10MKG | 2028-06-26
1 | ALP-EPC-20MAY-CM-MDB-0001 | ST Control and Protection - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 20MAY | 2028-06-26
1 | ALP-EPC-20MKA-CM-MDB-0001 | ST Generator - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 20MKA | 2028-06-26
1 | ALP-EPC-20MKC-CM-MDB-0001 | ST Excitation - System Turnover Dossier | NONE | IFR | A | yes | 2028-05-15 | 2028-05-22 | G-COM-MC-FF 20MKC | 2028-06-26
1 | ALP-EPC-20MAA-CM-MDB-0001 | HP Turbine - System Turnover Dossier | NONE | IFR | A | yes | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 20MAA | 2028-08-28
1 | ALP-EPC-20MAB-CM-MDB-0001 | IP/LP Turbine - System Turnover Dossier | NONE | IFR | A | yes | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 20MAB | 2028-08-28
1 | ALP-EPC-20MAG-CM-MDB-0001 | Condensing System - System Turnover Dossier | NONE | IFR | A | yes | 2028-06-19 | 2028-06-26 | G-COM-MC-WS 20MAG | 2028-08-28
1 | ALP-EPC-20MAJ-CM-MDB-0001 | Condenser Vacuum System - System Turnover Dossier | NONE | IFR | A | yes | 2028-06-19 | 2028-06-26 | G-COM-MC-WS 20MAJ | 2028-08-28
1 | ALP-EPC-20MAV-CM-MDB-0001 | ST Lube Oil System - System Turnover Dossier | NONE | IFR | A | yes | 2028-06-19 | 2028-06-26 | G-COM-MC-WS 20MAV | 2028-08-28
1 | ALP-EPC-20MAW-CM-MDB-0001 | Gland Steam System - System Turnover Dossier | NONE | IFR | A | yes | 2028-06-19 | 2028-06-26 | G-COM-MC-WS 20MAW | 2028-08-28
1 | ALP-EPC-20MAX-CM-MDB-0001 | ST Control Fluid System - System Turnover Dossier | NONE | IFR | A | yes | 2028-06-19 | 2028-06-26 | G-COM-MC-WS 20MAX | 2028-08-28
1 | ALP-IEC-10MBA-ME-OMM-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Operation and Maintenance Manual | NONE | IFR | A | yes | 2028-03-06 | 2028-07-24 | G-COM-SC-FF 10MBA | 2028-07-24
2 | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | NONE | IFR | A | yes | 2026-11-02 | 2026-12-07
2 | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | NONE | IFR | A | yes | 2026-11-02 | 2026-12-07
2 | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | NONE | IFR | A | yes | 2026-11-02 | 2026-12-14 | G-OWN-BDP 00000 | 2027-04-02
2 | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | NONE | IFR | A | yes | 2026-11-02 | 2026-12-14 | G-OWN-BDP 00000 | 2027-04-02
2 | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | NONE | IFR | A | yes | 2026-11-02 | 2026-12-14 | G-OWN-BDP 00000 | 2027-04-02
2 | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | NONE | IFR | A | yes | 2026-11-02 | 2026-12-14 | G-OWN-BDP 00000 | 2027-04-02
2 | ALP-EPC-00000-ME-RPT-0002 | Materials Selection and Corrosion Control Report | NONE | IFR | A | yes | 2026-12-07 | 2026-12-28
2 | ALP-EPC-00000-ME-SPC-0002 | Painting and Coating Specification | NONE | IFR | A | yes | 2026-12-14 | 2027-01-18
2 | ALP-EPC-00000-HS-RPT-0001 | EIA Conditions Compliance Matrix | NONE | IFR | A | yes | 2026-12-31 | 2027-01-21
2 | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | NONE | IFR | A | yes | 2026-12-18 | 2027-01-22
2 | ALP-EPC-00000-PC-PRC-0001 | Progress Measurement and Reporting Procedure | NONE | IFR | A | yes | 2026-12-22 | 2027-01-26
2 | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | NONE | IFR | A | yes | 2026-12-25 | 2027-02-05 | G-OWN-BDP 00000 | 2027-04-02
2 | ALP-EPC-00000-ME-SPC-0003 | Insulation Specification | NONE | IFR | A | yes | 2027-02-11 | 2027-03-18
2 | ALP-EPC-00000-HS-PLN-0001 | HSE in Design Plan and Safety-in-Design Register | NONE | IFR | A | yes | 2027-03-09 | 2027-04-13
2 | ALP-EPC-00000-GE-LST-0004 | Variation and Change Register | NONE | IFR | A | yes | 2027-04-07 | 2027-05-05 | G-OWN-TO 00000 | 2029-04-18
2 | ALP-EPC-00000-GE-PRC-0003 | As-Built Documentation and Engineering Database Handover Procedure | NONE | IFR | A | yes | 2027-04-05 | 2027-05-10
2 | ALP-EPC-00000-GE-LST-0001 | Codes, Standards and Regulations Register | NONE | IFR | A | yes | 2027-04-14 | 2027-05-12 | G-OWN-TO 00000 | 2029-04-18
2 | ALP-EPC-00000-GE-LST-0002 | Permits and Authorities Register | NONE | IFR | A | yes | 2027-04-14 | 2027-05-12 | G-OWN-TO 00000 | 2029-04-18
2 | ALP-EPC-00000-GE-LST-0003 | Tie-in and Terminal Point Register | NONE | IFR | A | yes | 2027-04-19 | 2027-05-17 | G-OWN-TO 00000 | 2029-04-18
2 | ALP-EPC-00000-GE-PLN-0001 | Engineering Execution Plan | NONE | IFR | A | yes | 2027-05-03 | 2027-06-07
2 | ALP-EPC-00000-GE-PLN-0003 | Project Quality Plan | NONE | IFR | A | yes | 2027-05-07 | 2027-06-11
3 | ALP-EPC-00000-CV-SPC-0001 | Concrete and Civil Works Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07
3 | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | NONE | IFR | A | no | 2026-11-02 | 2026-12-07
3 | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07
3 | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | NONE | IFR | A | no | 2026-11-23 | 2026-12-14
3 | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | NONE | IFR | A | no | 2026-11-23 | 2026-12-14
3 | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | NONE | IFR | A | no | 2026-11-23 | 2026-12-14
3 | ALP-EPC-00000-PR-CAL-0001 | Performance Guarantee Calculation and Correction Curves | NONE | IFR | A | no | 2026-11-23 | 2026-12-14
3 | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | NONE | IFR | A | no | 2026-11-02 | 2026-12-14 | G-OWN-BDP 00000 | 2027-04-02
3 | ALP-EPC-00000-EL-SPC-0005 | Cable Trays, Earthing and Lighting Materials - Technical Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04 | G-PRC-ENQ MR-EL-009 | 2026-12-21
3 | ALP-EPC-00000-HS-STU-0002 | Stack Dispersion Confirmation | NONE | IFR | A | no | 2026-12-07 | 2027-01-04
3 | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04
3 | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04
3 | ALP-EPC-00000-IC-SPC-0003 | Field Instruments - Technical Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04 | G-PRC-ENQ MR-IC-004 | 2027-05-24
3 | ALP-EPC-00000-IC-SPC-0004 | Control Valves - Technical Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04 | G-PRC-ENQ MR-IC-005 | 2027-03-15
3 | ALP-EPC-00000-PR-PFD-0002 | Utility Flow Diagrams | NONE | IFR | A | no | 2026-11-30 | 2027-01-04
3 | ALP-EPC-00000-PR-STU-0001 | Plant Water Balance | NONE | IFR | A | no | 2026-12-07 | 2027-01-04
3 | ALP-EPC-00000-PR-STU-0003 | CW Thermal Plume and Outfall Dispersion Study | NONE | IFR | A | no | 2026-12-07 | 2027-01-04
3 | ALP-EPC-00000-IC-SPC-0005 | DCS Functional Design Specification | NONE | IFR | A | no | 2026-12-03 | 2027-01-07
3 | ALP-EPC-00000-EL-SPC-0001 | Power and Control Cable Specification | NONE | IFR | A | no | 2026-12-04 | 2027-01-08
3 | ALP-EPC-00000-IC-TST-0001 | DCS Site Acceptance Test Procedure | NONE | IFR | A | no | 2026-12-11 | 2027-01-15
3 | ALP-EPC-00000-EL-CAL-0005 | Cathodic Protection Design | NONE | IFR | A | no | 2026-12-28 | 2027-01-18
3 | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | NONE | IFR | A | no | 2026-12-14 | 2027-01-25 | G-OWN-BDP 00000 | 2027-04-02
3 | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | NONE | IFR | A | no | 2027-01-08 | 2027-01-29
3 | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | NONE | IFR | A | no | 2027-01-18 | 2027-02-08
3 | ALP-EPC-00CJA-IC-BLK-0001 | Plant DCS - System Architecture | NONE | IFR | A | no | 2027-02-01 | 2027-03-15 | G-OWN-BDP 00000 | 2027-04-02
3 | ALP-EPC-00000-IC-CNR-0001 | Unit Coordination, Load Control, Export Limiter and Fuel Transfer | NONE | IFR | A | no | 2027-03-01 | 2027-03-29
3 | ALP-EPC-00000-HS-PLN-0003 | Construction Environmental and Social Management Plan | NONE | IFR | A | no | 2027-03-23 | 2027-04-27
3 | ALP-EPC-00000-HS-PLN-0004 | Waste Management Plan | NONE | IFR | A | no | 2027-04-02 | 2027-05-07
3 | ALP-EPC-00000-HS-PLN-0002 | Construction HSE Plan and Site Safety Plan | NONE | IFR | A | no | 2027-04-06 | 2027-05-11
3 | ALP-EPC-00000-GE-LST-0005 | As-Built Documentation Index | NONE | IFR | A | no | 2027-04-26 | 2027-05-24 | G-OWN-TO 00000 | 2029-04-18
3 | ALP-EPC-00000-GE-MDL-0001 | Master Document List | NONE | IFR | A | no | 2027-05-17 | 2027-05-24
3 | ALP-EPC-00000-GE-PLN-0004 | Interface Management Plan | NONE | IFR | A | no | 2027-05-17 | 2027-06-21
3 | ALP-EPC-00000-GE-PLN-0002 | Advanced Work Packaging Execution Plan | NONE | IFR | A | no | 2027-05-31 | 2027-07-05
3 | ALP-EPC-00000-GE-PLN-0005 | Project Execution Plan | NONE | IFR | A | no | 2027-06-11 | 2027-07-16
3 | ALP-EPC-00000-EL-CAL-0004 | Lighting Calculation | NONE | IFR | A | no | 2027-10-20 | 2027-11-10
3 | ALP-EPC-00000-EL-RPT-0001 | Electrical Control and Interlock Philosophy | NONE | IFR | A | no | 2027-10-20 | 2027-11-10
3 | ALP-EPC-00000-EL-SPC-0002 | LV and MV Motor Specification | NONE | IFR | A | no | 2027-10-27 | 2027-12-01
4 | ALP-EPC-00000-PR-LST-0001 | Equipment List | NONE | IFR | A | no | 2026-11-02 | 2026-11-30 | G-OWN-TO 00000 | 2029-04-18
4 | ALP-EPC-00EGA-PR-SDS-0001 | LDO Unloading - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00EGB-PR-SDS-0001 | LDO Storage - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00EGC-PR-SDS-0001 | LDO Forwarding and Treatment - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00EKA-PR-SDS-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00EKC-PR-SDS-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00GBA-PR-SDS-0001 | Seawater Reverse Osmosis - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00GCA-PR-SDS-0001 | Demineralisation - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00GHA-PR-SDS-0001 | Demineralised Water Storage and Distribution - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00GNA-PR-SDS-0001 | Waste Water Treatment - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00GUA-PR-SDS-0001 | Sanitary Waste Water Treatment - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00LBG-PR-SDS-0001 | Auxiliary Steam - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00LDA-PR-SDS-0001 | Condensate Polishing - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00PAB-PR-SDS-0001 | CW Piping - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00PAC-PR-SDS-0001 | CW Pumps - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00PAH-PR-SDS-0001 | Condenser Tube Cleaning - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00PBA-PR-SDS-0001 | Electro-Chlorination - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00PGA-PR-SDS-0001 | Closed Cooling Water - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00QCA-PR-SDS-0001 | Chemical Dosing - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00QEA-PR-SDS-0001 | Compressed Air - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00QHA-PR-SDS-0001 | Auxiliary Boiler - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00QJA-PR-SDS-0001 | Nitrogen Supply - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00QJB-PR-SDS-0001 | Hydrogen and CO2 Supply - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00QUA-PR-SDS-0001 | Sampling and SWAS - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00SAA-HV-SDS-0001 | HVAC - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00SGC-PR-SDS-0001 | Deluge, Spray and Foam Systems - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10HAN-PR-SDS-0001 | HRSG Blowdown and Drains - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10HSB-PR-SDS-0001 | Ammonia Storage and Supply - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10LAB-PR-SDS-0001 | Feedwater Piping - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10LAC-PR-SDS-0001 | Boiler Feed Pumps - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10LAE-PR-SDS-0001 | HP Attemperation Spray Water - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10LAF-PR-SDS-0001 | Reheat Attemperation Spray Water - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10LBA-PR-SDS-0001 | Main Steam Piping - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10LBB-PR-SDS-0001 | Hot Reheat Piping - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10LBC-PR-SDS-0001 | Cold Reheat Piping - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-10LBD-PR-SDS-0001 | LP Steam Piping - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-20LCA-PR-SDS-0001 | Main Condensate Piping - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-20LCB-PR-SDS-0001 | Condensate Extraction Pumps - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-20MAN-PR-SDS-0001 | Turbine Bypass Stations and Piping - System Design Description | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
4 | ALP-EPC-00000-CV-SPC-0004 | Civil and Building Works - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-CV-002 | 2026-11-23
4 | ALP-EPC-00000-CV-SPC-0005 | Marine Works - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-CV-003 | 2027-03-05
4 | ALP-EPC-00000-SS-SPC-0002 | Structural Steel Supply and Fabrication - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-SS-001 | 2027-01-19
4 | ALP-EPC-10HNE-SS-SPC-0001 | Stack 65 m with Silencer - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-SS-002 | 2027-01-11
4 | ALP-EPC-00000-EL-MRQ-0002 | Cable Trays, Earthing and Lighting Materials - Material Requisition | NONE | IFR | A | no | 2026-12-07 | 2026-12-10 | G-PRC-ENQ MR-EL-009 | 2026-12-21
4 | ALP-EPC-00000-IC-MRQ-0001 | Field Instruments - Material Requisition | NONE | IFR | A | no | 2026-12-07 | 2026-12-10 | G-PRC-ENQ MR-IC-004 | 2027-05-24
4 | ALP-EPC-00000-IC-MRQ-0002 | Control Valves - Material Requisition | NONE | IFR | A | no | 2026-12-07 | 2026-12-10 | G-PRC-ENQ MR-IC-005 | 2027-03-15
4 | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | NONE | IFR | A | no | 2026-11-02 | 2026-12-14 | G-OWN-BDP 00000 | 2027-04-02
4 | ALP-EPC-00000-PR-RPT-0001 | Cycle Chemistry Concept | NONE | IFR | A | no | 2026-11-23 | 2026-12-14
4 | ALP-EPC-00000-PR-RPT-0002 | Operating Philosophy | NONE | IFR | A | no | 2026-11-23 | 2026-12-14
4 | ALP-EPC-00000-PR-RPT-0003 | Isolation, Drainage and Venting Philosophy | NONE | IFR | A | no | 2026-11-30 | 2026-12-21
4 | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | NONE | IFR | A | no | 2026-11-30 | 2027-01-04
4 | ALP-EPC-00000-GE-SPC-0007 | Piping Specialty Items - Technical Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04 | G-PRC-ENQ MR-PI-006 | 2027-07-12
4 | ALP-EPC-00000-GE-SPC-0008 | Safety and Relief Valves - Technical Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04 | G-PRC-ENQ MR-PI-007 | 2027-06-14
4 | ALP-EPC-00000-PI-SPC-0004 | Piping Bulk Materials - Technical Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04 | G-PRC-ENQ MR-PI-001 | 2027-01-04
4 | ALP-EPC-00000-PR-CAL-0002 | Degradation Curves | NONE | IFR | A | no | 2026-12-14 | 2027-01-04
4 | ALP-EPC-00000-IC-LST-0002 | Alarm List | NONE | IFR | A | no | 2026-12-14 | 2027-01-11 | G-OWN-TO 00000 | 2029-04-18
4 | ALP-EPC-00000-IC-TST-0002 | OT Cybersecurity Acceptance Test Procedure | NONE | IFR | A | no | 2026-12-14 | 2027-01-18
4 | ALP-EPC-00CJG-IC-BLK-0001 | Safety Instrumented Systems - System Architecture | NONE | IFR | A | no | 2026-12-14 | 2027-01-18
4 | ALP-EPC-00CKA-IC-BLK-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Architecture | NONE | IFR | A | no | 2026-12-14 | 2027-01-18
4 | ALP-EPC-00CQA-IC-BLK-0001 | Continuous Emission Monitoring - System Architecture | NONE | IFR | A | no | 2026-12-14 | 2027-01-18
4 | ALP-EPC-00CYA-IC-BLK-0001 | Telecom, CCTV, Access Control, Security - System Architecture | NONE | IFR | A | no | 2026-12-14 | 2027-01-18
4 | ALP-EPC-00SGY-IC-BLK-0001 | Fire Detection and Alarm - System Architecture | NONE | IFR | A | no | 2026-12-14 | 2027-01-18
4 | ALP-EPC-00000-PI-SPC-0006 | Valves - Technical Specification | NONE | IFR | A | no | 2026-12-17 | 2027-01-21 | G-PRC-ENQ MR-PI-003 | 2027-04-12
4 | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | NONE | IFR | A | no | 2026-12-21 | 2027-01-25
4 | ALP-EPC-00ACA-IC-DSH-0001 | 380 kV GIS Switchyard - Instrument Datasheets | NONE | IFR | A | no | 2026-12-28 | 2027-01-25
4 | ALP-EPC-10BBT-IC-DSH-0001 | GT Unit Auxiliary Transformer - Instrument Datasheets | NONE | IFR | A | no | 2026-12-30 | 2027-01-27
4 | ALP-EPC-00000-EL-SPC-0004 | Power and Control Cables - Technical Specification | NONE | IFR | A | no | 2027-01-01 | 2027-02-05 | G-PRC-ENQ MR-EL-008 | 2027-05-03
4 | ALP-EPC-00CKA-IC-LOG-0001 | Historian, Performance Monitoring and Operator Training Simulator - Logic Diagrams | NONE | IFR | A | no | 2027-01-04 | 2027-02-08
4 | ALP-EPC-00CQA-IC-DSH-0002 | Continuous Emission Monitoring - Instrument Datasheets | NONE | IFR | A | no | 2027-01-11 | 2027-02-08
4 | ALP-EPC-00XJA-IC-DSH-0001 | Emergency Diesel Generator - Instrument Datasheets | NONE | IFR | A | no | 2027-01-11 | 2027-02-08
4 | ALP-EPC-20BBT-IC-DSH-0001 | ST Unit Auxiliary Transformer - Instrument Datasheets | NONE | IFR | A | no | 2027-01-13 | 2027-02-10
4 | ALP-EPC-10HNE-IC-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Instrument Datasheets | NONE | IFR | A | no | 2027-01-19 | 2027-02-16
4 | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | NONE | IFR | A | no | 2027-01-11 | 2027-02-22 | G-OWN-BDP 00000 | 2027-04-02
4 | ALP-EPC-00ACA-IC-LOG-0001 | 380 kV GIS Switchyard - Logic Diagrams | NONE | IFR | A | no | 2027-01-21 | 2027-02-25
4 | ALP-EPC-00CYA-IC-LOG-0001 | Telecom, CCTV, Access Control, Security - Logic Diagrams | NONE | IFR | A | no | 2027-01-21 | 2027-02-25
4 | ALP-EPC-00BMA-IC-LOG-0001 | Emergency LV Switchgear - Logic Diagrams | NONE | IFR | A | no | 2027-01-22 | 2027-02-26
4 | ALP-EPC-00BTA-IC-LOG-0001 | Batteries and DC 220 V - Logic Diagrams | NONE | IFR | A | no | 2027-01-25 | 2027-03-01
4 | ALP-EPC-00UAC-CV-CAL-0001 | GIS Building - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-02-08 | 2027-03-01
4 | ALP-EPC-00SMA-IC-LOG-0001 | Cranes and Hoists - Logic Diagrams | NONE | IFR | A | no | 2027-01-26 | 2027-03-02
4 | ALP-EPC-00UPC-CV-CAL-0001 | CW Pump House - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-02-09 | 2027-03-02
4 | ALP-EPC-00UZD-CV-CAL-0001 | Pipe Racks and Pipe Sleepers - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-02-10 | 2027-03-03
4 | ALP-EPC-00XJA-IC-LOG-0001 | Emergency Diesel Generator - Logic Diagrams | NONE | IFR | A | no | 2027-01-27 | 2027-03-03
4 | ALP-EPC-00BLA-IC-LOG-0001 | Lighting and Small Power - Logic Diagrams | NONE | IFR | A | no | 2027-01-28 | 2027-03-04
4 | ALP-EPC-00CQA-IC-LOG-0001 | Continuous Emission Monitoring - Logic Diagrams | NONE | IFR | A | no | 2027-01-28 | 2027-03-04
4 | ALP-EPC-10BBT-IC-LOG-0001 | GT Unit Auxiliary Transformer - Logic Diagrams | NONE | IFR | A | no | 2027-01-29 | 2027-03-05
4 | ALP-EPC-00BRA-IC-LOG-0001 | UPS - Logic Diagrams | NONE | IFR | A | no | 2027-02-01 | 2027-03-08
4 | ALP-EPC-00CJA-IC-LOG-0001 | Plant DCS - Logic Diagrams | NONE | IFR | A | no | 2027-02-04 | 2027-03-11
4 | ALP-EPC-00UEG-CV-CAL-0001 | LDO Tank Farm Structures - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-02-25 | 2027-03-18
4 | ALP-EPC-00UBA-CV-CAL-0001 | Electrical Building - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-03-02 | 2027-03-23
4 | ALP-EPC-00UGA-CV-CAL-0001 | Water Treatment Building and Basins - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-03-03 | 2027-03-24
4 | ALP-EPC-20BBT-IC-LOG-0001 | ST Unit Auxiliary Transformer - Logic Diagrams | NONE | IFR | A | no | 2027-02-23 | 2027-03-30
4 | ALP-EPC-00BXA-GE-SPC-0001 | Cathodic Protection - Technical Specification | NONE | IFR | A | no | 2027-02-25 | 2027-04-01 | G-PRC-ENQ MR-EL-010 | 2027-04-26
4 | ALP-EPC-00UQA-CV-CAL-0001 | Utility Building - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-03-29 | 2027-04-19
4 | ALP-EPC-00UCA-CV-CAL-0001 | Control Building - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-03-31 | 2027-04-21
4 | ALP-EPC-00USA-CV-CAL-0001 | Workshop and Warehouse - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-03-31 | 2027-04-21
4 | ALP-EPC-00UYA-CV-CAL-0001 | Administration Building - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-04-02 | 2027-04-23
4 | ALP-EPC-00000-GE-SPC-0006 | Pipe Supports, Spring Hangers and Snubbers - Technical Specification | NONE | IFR | A | no | 2027-03-22 | 2027-04-26 | G-PRC-ENQ MR-PI-005 | 2027-07-12
4 | ALP-EPC-10UMA-CV-CAL-0001 | Gas Turbine Hall - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-04-05 | 2027-04-26
4 | ALP-EPC-20UMB-CV-CAL-0001 | Steam Turbine Hall - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-04-05 | 2027-04-26
4 | ALP-EPC-00000-HS-RPT-0003 | Soil and Groundwater Baseline Survey Report | NONE | IFR | A | no | 2027-04-13 | 2027-05-04
4 | ALP-EPC-00000-GE-SPC-0003 | Instrument Installation Materials - Technical Specification | NONE | IFR | A | no | 2027-04-02 | 2027-05-07 | G-PRC-ENQ MR-IC-010 | 2027-10-25
4 | ALP-EPC-00UEK-CV-CAL-0001 | Gas Station Structures - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-04-27 | 2027-05-18
4 | ALP-EPC-00UBF-CV-CAL-0001 | Transformer Bays - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-05-03 | 2027-05-24
4 | ALP-EPC-00000-CV-RPT-0002 | Dewatering Design and Discharge Plan | NONE | IFR | A | no | 2027-05-06 | 2027-05-27
4 | ALP-EPC-00UPA-CV-RPT-0001 | Marine Route Survey for Intake and Outfall Pipelines | NONE | IFR | A | no | 2027-05-11 | 2027-06-01
4 | ALP-EPC-00UZF-CV-CAL-0001 | Temporary Barge Landing - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-05-21 | 2027-06-11
4 | ALP-EPC-00UPA-CV-CAL-0001 | CW Intake and Outfall Marine Structures - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-05-27 | 2027-06-17
4 | ALP-EPC-00000-CV-STU-0001 | Site-Specific Seismic Hazard Study | NONE | IFR | A | no | 2027-05-21 | 2027-06-18
4 | ALP-EPC-00000-PR-STU-0002 | Reliability, Availability and Maintainability Study | NONE | IFR | A | no | 2027-05-24 | 2027-06-21
4 | ALP-EPC-00UZB-CV-CAL-0001 | Fencing and Gates - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-06-01 | 2027-06-22
4 | ALP-EPC-00000-PR-LST-0003 | Chemical Consumption, Effluent and Emission Inventory | NONE | IFR | A | no | 2027-05-27 | 2027-06-24 | G-OWN-TO 00000 | 2029-04-18
4 | ALP-EPC-00UZA-CV-CAL-0001 | Roads and Paving - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-06-03 | 2027-06-24
4 | ALP-EPC-00000-PI-SPC-0003 | Welding, Heat Treatment and NDE Specification | NONE | IFR | A | no | 2027-05-21 | 2027-06-25
4 | ALP-EPC-00000-PR-STU-0004 | Carbon Capture Readiness Study | NONE | IFR | A | no | 2027-06-01 | 2027-06-29
4 | ALP-EPC-00UZC-CV-CAL-0001 | Site Drainage and Culverts - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-06-09 | 2027-06-30
4 | ALP-EPC-00UZE-CV-CAL-0001 | Cable Trenches and Duct Banks - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-06-09 | 2027-06-30
4 | ALP-EPC-10UHN-CV-CAL-0001 | Stack Foundation - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-06-09 | 2027-06-30
4 | ALP-EPC-10UHA-CV-CAL-0001 | HRSG Foundations and Structures - Structural and Foundation Calculation | NONE | IFR | A | no | 2027-06-10 | 2027-07-01
4 | ALP-EPC-00000-PC-SCH-0001 | Level 3 Project Schedule | NONE | IFR | A | no | 2027-06-21 | 2027-07-12
4 | ALP-EPC-00000-CM-CMP-0002 | Performance Test Procedure | NONE | IFR | A | no | 2027-07-14 | 2027-08-18 | G-OWN-TOC 00000 | 2028-08-21
4 | ALP-EPC-00SGY-IC-LOG-0001 | Fire Detection and Alarm - Logic Diagrams | NONE | IFR | A | no | 2027-09-29 | 2027-11-03
4 | ALP-EPC-10HNE-IC-LOG-0001 | Stack 65 m with CEMS Platform and Silencer - Logic Diagrams | NONE | IFR | A | no | 2027-09-29 | 2027-11-03
5 | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-CV-002 | 2026-11-23
5 | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-CV-003 | 2027-03-05
5 | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | NONE | IFR | A | no | 2026-11-09 | 2026-11-12 | G-PRC-ENQ MR-SS-001 | 2027-01-19
5 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | NONE | IFR | A | no | 2026-11-02 | 2026-11-30 | G-OWN-TO 00000 | 2029-04-18
5 | ALP-EPC-10HNE-ME-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
5 | ALP-EPC-00000-CV-SPC-0003 | Piling Works - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-CV-001 | 2027-02-01
5 | ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-IC-002 | 2027-05-03
5 | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-016 | 2026-11-16
5 | ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-017 | 2027-05-17
5 | ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-015 | 2026-11-16
5 | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-013 | 2027-03-29
5 | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-014 | 2027-03-22
5 | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-012 | 2026-11-16
5 | ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-004 | 2027-02-01
5 | ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-003 | 2026-11-23
5 | ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-006 | 2027-04-26
5 | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-005 | 2027-02-01
5 | ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-007 | 2027-01-25
5 | ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-011 | 2027-04-05
5 | ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-008 | 2027-01-25
5 | ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-009 | 2026-11-16
5 | ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-010 | 2027-05-10
5 | ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-IC-003 | 2027-05-03
5 | ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-HV-001 | 2027-01-04
5 | ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-020 | 2027-01-11
5 | ALP-EPC-00SMA-ME-SPC-0001 | EOT Cranes - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-021 | 2026-11-30
5 | ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-019 | 2027-03-15
5 | ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-018 | 2027-01-25
5 | ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-001 | 2026-11-16
5 | ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-ME-002 | 2027-02-01
5 | ALP-EPC-00000-GE-MRQ-0007 | Piping Specialty Items - Material Requisition | NONE | IFR | A | no | 2026-12-07 | 2026-12-10 | G-PRC-ENQ MR-PI-006 | 2027-07-12
5 | ALP-EPC-00000-GE-MRQ-0008 | Safety and Relief Valves - Material Requisition | NONE | IFR | A | no | 2026-12-07 | 2026-12-10 | G-PRC-ENQ MR-PI-007 | 2027-06-14
5 | ALP-EPC-00000-PI-MRQ-0001 | Piping Bulk Materials - Material Requisition | NONE | IFR | A | no | 2026-12-07 | 2026-12-10 | G-PRC-ENQ MR-PI-001 | 2027-01-04
5 | ALP-EPC-00UZA-CV-CVL-0001 | Temporary Facilities and Construction Site Layout | NONE | IFR | A | no | 2026-12-01 | 2026-12-15 | G-CON-CWP CWP-12-CV-01 | 2027-01-18
5 | ALP-EPC-00000-PI-MRQ-0003 | Valves - Material Requisition | NONE | IFR | A | no | 2026-12-24 | 2026-12-29 | G-PRC-ENQ MR-PI-003 | 2027-04-12
5 | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | NONE | IFR | A | no | 2026-12-07 | 2027-01-04
5 | ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04 | G-PRC-ENQ MR-PI-002 | 2026-12-21
5 | ALP-EPC-00000-PI-SPC-0007 | GRP CW Pipes and Fittings - Technical Specification | NONE | IFR | A | no | 2026-11-30 | 2027-01-04 | G-PRC-ENQ MR-PI-004 | 2026-12-21
5 | ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout | NONE | IFR | A | no | 2026-12-01 | 2027-01-05 | G-CON-CWP CWP-04-CV-01 | 2027-04-05
5 | ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout | NONE | IFR | A | no | 2026-12-01 | 2027-01-05 | G-CON-CWP CWP-12-CV-01 | 2027-01-18
5 | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | NONE | IFR | A | no | 2026-12-16 | 2027-01-06 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | NONE | IFR | A | no | 2026-12-03 | 2027-01-07 | G-CON-CWP CWP-05-ME-01 | 2027-12-20
5 | ALP-EPC-00UZB-CV-CVL-0001 | Fencing and Gates - Civil Drawings | NONE | IFR | A | no | 2026-12-28 | 2027-01-11 | G-CON-CWP CWP-12-CV-01 | 2027-01-18
5 | ALP-EPC-00000-EL-MRQ-0001 | Power and Control Cables - Material Requisition | NONE | IFR | A | no | 2027-01-08 | 2027-01-13 | G-PRC-ENQ MR-EL-008 | 2027-05-03
5 | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | NONE | IFR | A | no | 2026-12-09 | 2027-01-13 | G-CON-CWP CWP-03-CV-01 | 2027-03-29
5 | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | NONE | IFR | A | no | 2026-12-15 | 2027-01-19 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
5 | ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | NONE | IFR | A | no | 2026-12-15 | 2027-01-19 | G-CON-CWP CWP-07-ME-01 | 2027-12-27
5 | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | NONE | IFR | A | no | 2026-12-11 | 2027-01-22 | G-OWN-BDP 00000 | 2027-04-02
5 | ALP-EPC-00000-EL-STU-0003 | Earthing Study | NONE | IFR | A | no | 2026-12-28 | 2027-01-25
5 | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | NONE | IFR | A | no | 2026-12-29 | 2027-01-26
5 | ALP-EPC-00PAB-ME-CAL-0001 | CW Piping - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-05 | 2027-01-26
5 | ALP-EPC-00PAC-ME-CAL-0001 | CW Pumps - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-05 | 2027-01-26
5 | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | NONE | IFR | A | no | 2026-12-22 | 2027-01-26 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
5 | ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | NONE | IFR | A | no | 2026-12-23 | 2027-01-27 | G-CON-CWP CWP-10-ME-01 | 2027-10-04
5 | ALP-EPC-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-06 | 2027-01-27
5 | ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-07 | 2027-01-28
5 | ALP-EPC-00GCA-ME-CAL-0001 | Demineralisation - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-07 | 2027-01-28
5 | ALP-EPC-00LDA-ME-CAL-0001 | Condensate Polishing - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-07 | 2027-01-28
5 | ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-08 | 2027-01-29
5 | ALP-EPC-00ACA-CM-CMP-0001 | 380 kV GIS Switchyard - System Commissioning Procedure | NONE | IFR | A | no | 2026-12-28 | 2027-02-01 | G-COM-SC-EL 00ACA | 2028-05-09
5 | ALP-EPC-00BBA-CM-CMP-0001 | MV Switchgear 10.5 kV - System Commissioning Procedure | NONE | IFR | A | no | 2026-12-28 | 2027-02-01 | G-COM-SC-EL 00BBA | 2028-05-09
5 | ALP-EPC-00BFA-CM-CMP-0001 | LV Switchgear 0.4 kV - System Commissioning Procedure | NONE | IFR | A | no | 2026-12-28 | 2027-02-01 | G-COM-SC-EL 00BFA | 2028-05-09
5 | ALP-EPC-00BFT-CM-CMP-0001 | LV Transformers - System Commissioning Procedure | NONE | IFR | A | no | 2026-12-28 | 2027-02-01 | G-COM-SC-EL 00BFT | 2028-05-09
5 | ALP-EPC-00BLA-CM-CMP-0001 | Lighting and Small Power - System Commissioning Procedure | NONE | IFR | A | no | 2026-12-28 | 2027-02-01 | G-COM-SC-EL 00BLA | 2028-05-09
5 | ALP-EPC-00BMA-CM-CMP-0001 | Emergency LV Switchgear - System Commissioning Procedure | NONE | IFR | A | no | 2026-12-28 | 2027-02-01 | G-COM-SC-EL 00BMA | 2028-05-09
5 | ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-11 | 2027-02-01
5 | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-11 | 2027-02-01
5 | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | NONE | IFR | A | no | 2026-12-28 | 2027-02-01 | G-CON-CWP CWP-09-ME-01 | 2027-11-01
5 | ALP-EPC-00EGC-ME-CAL-0001 | LDO Forwarding and Treatment - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-12 | 2027-02-02
5 | ALP-EPC-00UPA-PI-LAY-0001 | Marine Works - Equipment Layout | NONE | IFR | A | no | 2026-12-29 | 2027-02-02 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
5 | ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-13 | 2027-02-03
5 | ALP-EPC-00SGC-ME-CAL-0001 | Deluge, Spray and Foam Systems - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-13 | 2027-02-03
5 | ALP-EPC-00BLA-GE-RPT-0001 | Cable Trays, Earthing and Lighting Materials - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-28 | 2027-02-04 | G-PRC-PO MR-EL-009 | 2027-02-08
5 | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | NONE | IFR | A | no | 2026-12-24 | 2027-02-04 | G-OWN-BDP 00000 | 2027-04-02
5 | ALP-EPC-00SGA-ME-CAL-0001 | Fire Water System - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-15 | 2027-02-05
5 | ALP-EPC-00GMA-ME-CAL-0001 | Process Drains and Waste Water Collection - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-18 | 2027-02-08
5 | ALP-EPC-00GUA-ME-CAL-0001 | Sanitary Waste Water Treatment - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-19 | 2027-02-09
5 | ALP-EPC-00BRA-CM-CMP-0001 | UPS - System Commissioning Procedure | NONE | IFR | A | no | 2027-01-07 | 2027-02-11 | G-COM-SC-EL 00BRA | 2028-05-09
5 | ALP-EPC-00GNA-ME-CAL-0001 | Waste Water Treatment - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-22 | 2027-02-12
5 | ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-01-29 | 2027-02-19
5 | ALP-EPC-00PAA-ME-CAL-0001 | CW Intake, Screens and Outfall - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-01 | 2027-02-22
5 | ALP-EPC-00BTA-CM-CMP-0001 | Batteries and DC 220 V - System Commissioning Procedure | NONE | IFR | A | no | 2027-01-19 | 2027-02-23 | G-COM-SC-EL 00BTA | 2028-05-09
5 | ALP-E09-00BLA-ME-DSH-0001 | Cable Trays, Earthing and Lighting Materials - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-02-11 | 2027-02-25
5 | ALP-E09-00BLA-ME-ITP-0001 | Cable Trays, Earthing and Lighting Materials - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-11 | 2027-02-25
5 | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | NONE | IFR | A | no | 2027-01-22 | 2027-02-26
5 | ALP-EPC-00BXA-CM-CMP-0001 | Earthing and Lightning Protection - System Commissioning Procedure | NONE | IFR | A | no | 2027-01-25 | 2027-03-01 | G-COM-SC-EL 00BXA | 2028-05-09
5 | ALP-EPC-00XJA-CM-CMP-0001 | Emergency Diesel Generator - System Commissioning Procedure | NONE | IFR | A | no | 2027-01-25 | 2027-03-01 | G-COM-SC-EL 00XJA | 2028-05-09
5 | ALP-EPC-10BBT-CM-CMP-0001 | GT Unit Auxiliary Transformer - System Commissioning Procedure | NONE | IFR | A | no | 2027-01-25 | 2027-03-01 | G-COM-SC-EL 10BBT | 2028-05-09
5 | ALP-EPC-20BBT-CM-CMP-0001 | ST Unit Auxiliary Transformer - System Commissioning Procedure | NONE | IFR | A | no | 2027-01-25 | 2027-03-01 | G-COM-SC-EL 20BBT | 2028-05-09
5 | ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-09 | 2027-03-02
5 | ALP-EPC-00000-HS-HAZ-0001 | HAZID Report | NONE | IFR | A | no | 2027-01-27 | 2027-03-03
5 | ALP-EPC-00QEA-ME-CAL-0001 | Compressed Air - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-12 | 2027-03-05
5 | ALP-EPC-10HSB-ME-CAL-0001 | Ammonia Storage and Supply - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-12 | 2027-03-05
5 | ALP-EPC-00CJG-GE-SPC-0001 | BOP Safety Instrumented System - Technical Specification | NONE | IFR | A | no | 2027-02-01 | 2027-03-08 | G-PRC-ENQ MR-IC-008 | 2027-04-12
5 | ALP-EPC-00CKA-GE-SPC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Specification | NONE | IFR | A | no | 2027-02-01 | 2027-03-08 | G-PRC-ENQ MR-IC-009 | 2027-04-12
5 | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | NONE | IFR | A | no | 2027-03-04 | 2027-03-09 | G-PRC-ENQ MR-EL-010 | 2027-04-26
5 | ALP-EPC-00GKA-ME-CAL-0001 | Potable Water - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-16 | 2027-03-09
5 | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | NONE | IFR | A | no | 2027-01-26 | 2027-03-09 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | NONE | IFR | A | no | 2027-01-26 | 2027-03-09 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-16 | 2027-03-09
5 | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | NONE | IFR | A | no | 2027-01-27 | 2027-03-10 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00GHA-ME-CAL-0001 | Demineralised Water Storage and Distribution - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-18 | 2027-03-11
5 | ALP-EPC-00CJA-CM-CMP-0001 | Plant DCS - System Commissioning Procedure | NONE | IFR | A | no | 2027-02-05 | 2027-03-12 | G-COM-SC-FF 00CJA | 2028-07-24
5 | ALP-EPC-00000-HS-STU-0001 | Noise Study | NONE | IFR | A | no | 2027-02-15 | 2027-03-15
5 | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | NONE | IFR | A | no | 2027-01-25 | 2027-03-15 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | NONE | IFR | A | no | 2027-02-02 | 2027-03-16 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00PAH-ME-CAL-0001 | Condenser Tube Cleaning - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-26 | 2027-03-19
5 | ALP-EPC-10HAN-ME-CAL-0001 | HRSG Blowdown and Drains - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-02-26 | 2027-03-19
5 | ALP-EPC-00000-GE-RPT-0007 | Control Valves - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-15 | 2027-03-22 | G-PRC-PO MR-IC-005 | 2027-05-17
5 | ALP-EPC-00000-ME-STU-0002 | Mechanical Handling and Maintenance Access Study | NONE | IFR | A | no | 2027-02-23 | 2027-03-23
5 | ALP-EPC-00CJG-CM-CMP-0001 | Safety Instrumented Systems - System Commissioning Procedure | NONE | IFR | A | no | 2027-02-16 | 2027-03-23 | G-COM-SC-FF 00CJG | 2028-07-24
5 | ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | NONE | IFR | A | no | 2027-02-16 | 2027-03-23 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
5 | ALP-EPC-00QCA-ME-CAL-0001 | Chemical Dosing - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-03 | 2027-03-24
5 | ALP-EPC-00QJB-ME-CAL-0001 | Hydrogen and CO2 Supply - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-03 | 2027-03-24
5 | ALP-EPC-00QJA-ME-CAL-0001 | Nitrogen Supply - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-04 | 2027-03-25
5 | ALP-EPC-00EGB-ME-CAL-0001 | LDO Storage - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-05 | 2027-03-26
5 | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | NONE | IFR | A | no | 2027-02-12 | 2027-03-26 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-10LAE-ME-CAL-0001 | HP Attemperation Spray Water - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-05 | 2027-03-26
5 | ALP-EPC-00CKA-CM-CMP-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Commissioning Procedure | NONE | IFR | A | no | 2027-02-22 | 2027-03-29 | G-COM-SC-FF 00CKA | 2028-07-24
5 | ALP-EPC-00CQA-CM-CMP-0001 | Continuous Emission Monitoring - System Commissioning Procedure | NONE | IFR | A | no | 2027-02-22 | 2027-03-29 | G-COM-SC-FF 00CQA | 2028-07-24
5 | ALP-EPC-00CYA-CM-CMP-0001 | Telecom, CCTV, Access Control, Security - System Commissioning Procedure | NONE | IFR | A | no | 2027-02-22 | 2027-03-29 | G-COM-SC-FF 00CYA | 2028-07-24
5 | ALP-EPC-00EKC-ME-CAL-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-08 | 2027-03-29
5 | ALP-EPC-00QUA-ME-CAL-0001 | Sampling and SWAS - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-08 | 2027-03-29
5 | ALP-EPC-10LAB-ME-CAL-0001 | Feedwater Piping - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-08 | 2027-03-29
5 | ALP-EPC-10LAF-ME-CAL-0001 | Reheat Attemperation Spray Water - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-08 | 2027-03-29
5 | ALP-EPC-10LBA-ME-CAL-0001 | Main Steam Piping - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-08 | 2027-03-29
5 | ALP-EPC-10LBB-ME-CAL-0001 | Hot Reheat Piping - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-08 | 2027-03-29
5 | ALP-EPC-10LBC-ME-CAL-0001 | Cold Reheat Piping - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-08 | 2027-03-29
5 | ALP-EPC-10LBD-ME-CAL-0001 | LP Steam Piping - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-08 | 2027-03-29
5 | ALP-EPC-00LBG-ME-CAL-0001 | Auxiliary Steam - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-09 | 2027-03-30
5 | ALP-EPC-20MAN-ME-CAL-0001 | Turbine Bypass Stations and Piping - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-09 | 2027-03-30
5 | ALP-EPC-00000-GE-RPT-0006 | Field Instruments - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-24 | 2027-03-31 | G-PRC-PO MR-IC-004 | 2027-07-26
5 | ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification | NONE | IFR | A | no | 2027-02-24 | 2027-03-31 | G-PRC-ENQ MR-IC-007 | 2027-05-24
5 | ALP-EPC-20LCA-ME-CAL-0001 | Main Condensate Piping - Sizing and Hydraulic Calculation | NONE | IFR | A | no | 2027-03-10 | 2027-03-31
5 | ALP-EPC-00000-GE-MRQ-0006 | Pipe Supports, Spring Hangers and Snubbers - Material Requisition | NONE | IFR | A | no | 2027-03-29 | 2027-04-01 | G-PRC-ENQ MR-PI-005 | 2027-07-12
5 | ALP-EPC-00BXA-GE-ITP-0001 | Cathodic Protection - Inspection and Test Plan | NONE | IFR | A | no | 2027-03-11 | 2027-04-08 | G-PRC-PO MR-EL-010 | 2027-06-21
5 | ALP-EPC-00SGY-CM-CMP-0001 | Fire Detection and Alarm - System Commissioning Procedure | NONE | IFR | A | no | 2027-03-05 | 2027-04-09 | G-COM-SC-FF 00SGY | 2028-07-24
5 | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | NONE | IFR | A | no | 2027-03-01 | 2027-04-12 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00SMA-CM-CMP-0001 | Cranes and Hoists - System Commissioning Procedure | NONE | IFR | A | no | 2027-03-08 | 2027-04-12 | G-COM-SC-FF 00SMA | 2028-07-24
5 | ALP-EPC-00000-GE-MRQ-0003 | Instrument Installation Materials - Material Requisition | NONE | IFR | A | no | 2027-04-09 | 2027-04-14 | G-PRC-ENQ MR-IC-010 | 2027-10-25
5 | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | NONE | IFR | A | no | 2027-03-04 | 2027-04-15 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings | NONE | IFR | A | no | 2027-03-11 | 2027-04-15 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
5 | ALP-EPC-10HNE-CM-CMP-0001 | Stack 65 m with CEMS Platform and Silencer - System Commissioning Procedure | NONE | IFR | A | no | 2027-03-11 | 2027-04-15 | G-COM-SC-FF 10HNE | 2028-07-24
5 | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | NONE | IFR | A | no | 2027-03-05 | 2027-04-16 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | NONE | IFR | A | no | 2027-03-05 | 2027-04-16 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | NONE | IFR | A | no | 2027-03-05 | 2027-04-16 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | NONE | IFR | A | no | 2027-03-05 | 2027-04-16 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | NONE | IFR | A | no | 2027-03-08 | 2027-04-19 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-I05-00000-ME-DSH-0001 | Control Valves - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-04-05 | 2027-04-26
5 | ALP-I05-00000-ME-ITP-0001 | Control Valves - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-04-05 | 2027-04-26
5 | ALP-I04-00000-ME-DSH-0001 | Field Instruments - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-04-12 | 2027-04-29
5 | ALP-I04-00000-ME-ITP-0001 | Field Instruments - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-04-12 | 2027-04-29
5 | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | NONE | IFR | A | no | 2027-03-24 | 2027-05-05 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | NONE | IFR | A | no | 2027-03-25 | 2027-05-06 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | NONE | IFR | A | no | 2027-04-06 | 2027-05-18 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00000-GE-SPC-0004 | Painting and Insulation - Technical Specification | NONE | IFR | A | no | 2027-04-16 | 2027-05-21 | G-PRC-ENQ MR-ME-022 | 2027-11-15
5 | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | NONE | IFR | A | no | 2027-04-09 | 2027-05-21 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | NONE | IFR | A | no | 2027-04-09 | 2027-05-21 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | NONE | IFR | A | no | 2027-04-12 | 2027-05-24 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | NONE | IFR | A | no | 2027-04-12 | 2027-05-24 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | NONE | IFR | A | no | 2027-04-12 | 2027-05-24 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | NONE | IFR | A | no | 2027-04-12 | 2027-05-24 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | NONE | IFR | A | no | 2027-04-13 | 2027-05-25 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | NONE | IFR | A | no | 2027-04-12 | 2027-05-31 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-00UPA-CV-CAL-0002 | Marine Structures Design: Hydrodynamics, Scour and Rock Protection | NONE | IFR | A | no | 2027-05-10 | 2027-05-31
5 | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | NONE | IFR | A | no | 2027-04-28 | 2027-06-09 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | NONE | IFR | A | no | 2027-04-30 | 2027-06-11 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00000-CV-TST-0001 | Pile Load Test Procedure | NONE | IFR | A | no | 2027-05-13 | 2027-06-17
5 | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | NONE | IFR | A | no | 2027-05-06 | 2027-06-17 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | NONE | IFR | A | no | 2027-05-14 | 2027-06-25 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | NONE | IFR | A | no | 2027-05-17 | 2027-06-28 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | NONE | IFR | A | no | 2027-05-17 | 2027-06-28 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | NONE | IFR | A | no | 2027-05-17 | 2027-06-28 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | NONE | IFR | A | no | 2027-05-17 | 2027-06-28 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | NONE | IFR | A | no | 2027-05-18 | 2027-06-29 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | NONE | IFR | A | no | 2027-05-18 | 2027-06-29 | G-OPS-AB 00000 | 2029-07-18
5 | ALP-E09-00BLA-ME-MDB-0001 | Cable Trays, Earthing and Lighting Materials - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-05-06 | 2027-07-01 | G-PRC-SHP MR-EL-009 | 2027-05-20
5 | ALP-EPC-00000-PR-RPT-0004 | Equipment Sparing and Redundancy Philosophy | NONE | IFR | A | no | 2027-06-14 | 2027-07-05
5 | ALP-EPC-00PAA-PR-STU-0001 | CW Intake Hydraulic Model Study and Pump Sump Model Test | NONE | IFR | A | no | 2027-06-07 | 2027-07-05
5 | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | NONE | IFR | A | no | 2027-05-18 | 2027-07-06 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | NONE | IFR | A | no | 2027-05-18 | 2027-07-06 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | NONE | IFR | A | no | 2027-05-18 | 2027-07-06 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | NONE | IFR | A | no | 2027-06-02 | 2027-07-21 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | NONE | IFR | A | no | 2027-06-02 | 2027-07-21 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | NONE | IFR | A | no | 2027-06-03 | 2027-07-22 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-00000-GE-SPC-0005 | Mechanical and Piping Erection - Technical Specification | NONE | IFR | A | no | 2027-06-18 | 2027-07-23 | G-PRC-ENQ MR-ME-023 | 2027-08-30
5 | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | NONE | IFR | A | no | 2027-06-07 | 2027-07-26 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | NONE | IFR | A | no | 2027-06-09 | 2027-07-28 | G-OWN-BDP2 00000 | 2027-08-02
5 | ALP-EPC-00000-CM-CMP-0004 | Operational Demonstration and Reliability Run Procedure | NONE | IFR | A | no | 2027-08-04 | 2027-09-08 | G-OWN-TOC 00000 | 2028-08-21
5 | ALP-EPC-00000-HS-PLN-0006 | Radiation Protection Plan | NONE | IFR | A | no | 2027-08-10 | 2027-09-14
5 | ALP-I04-00000-ME-MDB-0001 | Field Instruments - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-08 | 2027-11-03 | G-PRC-SHP MR-IC-004 | 2027-09-22
5 | ALP-I05-00000-ME-MDB-0001 | Control Valves - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-27 | 2027-11-22 | G-PRC-SHP MR-IC-005 | 2027-10-11
5 | ALP-EPC-00000-CM-PRC-0001 | Punch List and Completion Procedure | NONE | IFR | A | no | 2027-11-11 | 2027-12-16
5 | ALP-EPC-00000-CM-PRC-0002 | System Completion, Mechanical Completion and Turnover Procedure | NONE | IFR | A | no | 2027-11-24 | 2027-12-29
5 | ALP-EPC-00000-CM-PLN-0002 | Training Plan | NONE | IFR | A | no | 2027-11-25 | 2027-12-30
5 | ALP-EPC-00000-IC-TRP-0001 | OT Cybersecurity Acceptance Test Report | NONE | IFR | A | no | 2028-09-25 | 2028-10-16 | G-OWN-TO 00000 | 2029-04-18
5 | ALP-EPC-00000-CM-TRP-0002 | Performance Test Report incl. Uncertainty Analysis | NONE | IFR | A | no | 2029-03-27 | 2029-04-17 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-CV-001 | 2027-02-01
6 | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | NONE | IFR | A | no | 2026-11-09 | 2026-11-12 | G-PRC-ENQ MR-SS-002 | 2027-01-11
6 | ALP-EPC-00000-EL-LST-0002 | Construction Power Load List | NONE | IFR | A | no | 2026-11-02 | 2026-11-16 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-00CQA-IC-DSH-0001 | Continuous Emission Monitoring: Analyser - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00EGA-ME-DSH-0001 | LDO Unloading: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00EGB-ME-DSH-0001 | LDO Storage: Tanks - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00EGC-ME-DSH-0001 | LDO Forwarding and Treatment: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00EKA-ME-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00GBA-ME-DSH-0001 | Seawater Reverse Osmosis: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00GCA-ME-DSH-0001 | Demineralisation: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00GHA-ME-DSH-0001 | Demineralised Water Storage and Distribution: Tanks - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00GHA-ME-DSH-0002 | Demineralised Water Storage and Distribution: Pumps - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00GKA-ME-DSH-0001 | Potable Water: Tank - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00GNA-ME-DSH-0001 | Waste Water Treatment: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00GUA-ME-DSH-0001 | Sanitary Waste Water Treatment: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00LDA-ME-DSH-0001 | Condensate Polishing: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00PAA-ME-DSH-0001 | CW Intake, Screens and Outfall: Filters - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00PAC-ME-DSH-0001 | CW Pumps - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00PAH-ME-DSH-0001 | Condenser Tube Cleaning: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00PBA-ME-DSH-0001 | Electro-Chlorination: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00PGA-ME-DSH-0001 | Closed Cooling Water: Heat Exchangers - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00PGA-ME-DSH-0002 | Closed Cooling Water: Pumps - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00PGA-ME-DSH-0003 | Closed Cooling Water: Tanks - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00QCA-ME-DSH-0001 | Chemical Dosing: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00QEA-ME-DSH-0001 | Compressed Air: Compressors - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00QEA-ME-DSH-0002 | Compressed Air: Filters - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00QEA-ME-DSH-0003 | Compressed Air: Tanks - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00QHA-ME-DSH-0001 | Auxiliary Boiler - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00QJA-ME-DSH-0001 | Nitrogen Supply: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00QJB-ME-DSH-0001 | Hydrogen and CO2 Supply: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00QUA-ME-DSH-0001 | Sampling and SWAS: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00SAA-HV-DSH-0001 | HVAC: Package - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00SMA-ME-DSH-0001 | Cranes and Hoists - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-10HAN-ME-DSH-0001 | HRSG Blowdown and Drains - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-10HSB-ME-DSH-0001 | Ammonia Storage and Supply: Tanks - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-10HSB-ME-DSH-0002 | Ammonia Storage and Supply: Pumps - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
6 | ALP-EPC-00000-PI-MRQ-0002 | Alloy Piping P91 / P22 - Material Requisition | NONE | IFR | A | no | 2026-12-07 | 2026-12-10 | G-PRC-ENQ MR-PI-002 | 2026-12-21
6 | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | NONE | IFR | A | no | 2026-11-02 | 2026-12-14 | G-OWN-BDP 00000 | 2027-04-02
6 | ALP-EPC-00CQA-IC-ITP-0001 | Continuous Emission Monitoring System - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-IC-002 | 2027-07-12
6 | ALP-EPC-00EGA-ME-ITP-0001 | LDO Unloading and Forwarding / Treatment Skids - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-016 | 2027-01-25
6 | ALP-EPC-00EKA-ME-ITP-0001 | Gas Receiving and Metering Station - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-015 | 2027-01-25
6 | ALP-EPC-00GHA-ME-ITP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-013 | 2027-05-17
6 | ALP-EPC-00GNA-ME-ITP-0001 | Waste Water and Sanitary Treatment Packages - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-014 | 2027-05-31
6 | ALP-EPC-00LDA-ME-ITP-0001 | Water Treatment Package - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-012 | 2027-02-08
6 | ALP-EPC-00PAA-ME-ITP-0001 | Travelling Band Screens and Trash Rakes - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-004 | 2027-04-12
6 | ALP-EPC-00PAC-ME-ITP-0001 | CW Pumps - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-003 | 2027-02-01
6 | ALP-EPC-00PBA-ME-ITP-0001 | Electro-Chlorination Package - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-005 | 2027-04-12
6 | ALP-EPC-00QHA-ME-ITP-0001 | Auxiliary Boiler - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-009 | 2027-01-25
6 | ALP-EPC-00QUA-IC-ITP-0001 | Steam/Water Analysis System - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-IC-003 | 2027-07-12
6 | ALP-EPC-00SAA-HV-ITP-0001 | HVAC Plant and Equipment - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-HV-001 | 2027-03-15
6 | ALP-EPC-00SGA-ME-ITP-0001 | Fire Pumps and Fire Protection Systems - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-020 | 2027-03-22
6 | ALP-EPC-00SMA-ME-ITP-0001 | EOT Cranes - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-021 | 2027-02-08
6 | ALP-EPC-10LAC-ME-ITP-0001 | Boiler Feed Pumps - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-ME-001 | 2027-01-25
6 | ALP-EPC-00PGA-ME-ITP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-17 | 2026-12-15 | G-PRC-PO MR-ME-007 | 2027-04-05
6 | ALP-EPC-00QEA-ME-ITP-0001 | Air Compressors and Dryers - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-18 | 2026-12-16 | G-PRC-PO MR-ME-008 | 2027-04-05
6 | ALP-EPC-10HSB-ME-ITP-0001 | Aqueous Ammonia Storage and Forwarding - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-20 | 2026-12-18 | G-PRC-PO MR-ME-018 | 2027-04-05
6 | ALP-EPC-20LCB-ME-ITP-0001 | Condensate Extraction Pumps - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-23 | 2026-12-21 | G-PRC-PO MR-ME-002 | 2027-04-12
6 | ALP-EPC-10HAN-ME-ITP-0001 | HRSG Blowdown and Drain Tanks - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-25 | 2026-12-23 | G-PRC-PO MR-ME-019 | 2027-05-03
6 | ALP-EPC-00QCA-ME-ITP-0001 | Chemical Dosing Skid - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-26 | 2026-12-24 | G-PRC-PO MR-ME-011 | 2027-05-17
6 | ALP-EPC-00PAH-ME-ITP-0001 | Condenser Tube Cleaning System - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-30 | 2026-12-28 | G-PRC-PO MR-ME-006 | 2027-07-05
6 | ALP-EPC-00QJA-ME-ITP-0001 | Nitrogen, Hydrogen and CO2 Supply - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-30 | 2026-12-28 | G-PRC-PO MR-ME-010 | 2027-06-28
6 | ALP-EPC-00000-GE-RPT-0002 | Civil and Building Works - Technical Bid Evaluation | NONE | IFR | A | no | 2026-12-24 | 2026-12-31 | G-PRC-PO MR-CV-002 | 2027-01-11
6 | ALP-C02-00000-GE-ITP-0001 | Civil and Building Works - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-01-07 | 2027-01-21
6 | ALP-C02-00000-GE-MOS-0001 | Civil and Building Works - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-01-07 | 2027-01-21
6 | ALP-C02-00000-GE-MOS-0002 | Civil and Building Works - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-01-07 | 2027-01-21
6 | ALP-C02-00000-GE-MOS-0003 | Civil and Building Works - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-01-07 | 2027-01-21
6 | ALP-C02-00000-GE-MOS-0004 | Civil and Building Works - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-01-07 | 2027-01-21
6 | ALP-C02-00000-GE-MOS-0005 | Civil and Building Works - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-01-07 | 2027-01-21
6 | ALP-C02-00000-GE-MOS-0006 | Civil and Building Works - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-01-07 | 2027-01-21
6 | ALP-EPC-00000-GE-RPT-0011 | Piping Bulk Materials - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-28 | 2027-02-04 | G-PRC-PO MR-PI-001 | 2027-02-22
6 | ALP-EPC-00UPC-CV-ARC-0001 | CW Pump House - Architectural Drawings | NONE | IFR | A | no | 2027-01-05 | 2027-02-09 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
6 | ALP-EPC-00000-GE-RPT-0016 | Structural Steel Supply and Fabrication - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-03 | 2027-02-10 | G-PRC-PO MR-SS-001 | 2027-03-23
6 | ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings | NONE | IFR | A | no | 2027-01-07 | 2027-02-11 | G-CON-CWP CWP-04-SS-01 | 2027-05-31
6 | ALP-EPC-00EGA-ME-DSH-0002 | LDO Unloading: Filters - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00EGA-ME-DSH-0004 | LDO Unloading: Tank - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00GBA-ME-DSH-0004 | Seawater Reverse Osmosis: Tank - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00GCA-ME-DSH-0003 | Demineralisation: Pumps - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00LDA-ME-DSH-0002 | Condensate Polishing: Filters - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00PAB-ME-DSH-0001 | CW Piping: Valves - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00QHA-ME-DSH-0002 | Auxiliary Boiler: Fan - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00QHA-ME-DSH-0003 | Auxiliary Boiler: Pumps - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00QHA-ME-DSH-0004 | Auxiliary Boiler: Tanks - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
6 | ALP-EPC-00UPC-CV-FND-0002 | CW Pump House - Piling Layout and Pile Schedule | NONE | IFR | A | no | 2027-01-19 | 2027-02-23 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
6 | ALP-EPC-20UMB-CV-ARC-0001 | Steam Turbine Hall - Architectural Drawings | NONE | IFR | A | no | 2027-01-19 | 2027-02-23 | G-CON-CWP CWP-02-SS-01 | 2027-07-12
6 | ALP-EPC-00EGA-ME-DSH-0003 | LDO Unloading: Pumps - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00EGC-ME-DSH-0002 | LDO Forwarding and Treatment: Filters - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00EGC-ME-DSH-0003 | LDO Forwarding and Treatment: Pumps - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00EKA-ME-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station: Filters - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00EKA-ME-DSH-0003 | Gas Receiving, Filtration and Fiscal Metering Station: Heat Exchangers - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00EKA-ME-DSH-0004 | Gas Receiving, Filtration and Fiscal Metering Station: Tank - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00GBA-ME-DSH-0002 | Seawater Reverse Osmosis: Filters - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00GBA-ME-DSH-0003 | Seawater Reverse Osmosis: Pumps - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00GCA-ME-DSH-0002 | Demineralisation: Filters - Datasheet | NONE | IFR | A | no | 2027-01-27 | 2027-02-24
6 | ALP-EPC-00UZB-EL-ELY-0001 | Fencing and Gates - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-01-27 | 2027-02-24 | G-CON-CWP CWP-12-EL-01 | 2027-05-17
6 | ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings | NONE | IFR | A | no | 2027-01-21 | 2027-02-25 | G-CON-CWP CWP-03-SS-01 | 2027-05-24
6 | ALP-P01-00000-ME-DSH-0001 | Piping Bulk Materials - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-02-11 | 2027-02-25
6 | ALP-P01-00000-ME-ITP-0001 | Piping Bulk Materials - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-11 | 2027-02-25
6 | ALP-EPC-00UBF-CV-FND-0002 | Transformer Bays - Piling Layout and Pile Schedule | NONE | IFR | A | no | 2027-01-22 | 2027-02-26 | G-CON-CWP CWP-01-CV-01 | 2027-03-22
6 | ALP-EPC-10UHN-CV-FND-0002 | Stack Foundation - Piling Layout and Pile Schedule | NONE | IFR | A | no | 2027-01-22 | 2027-02-26 | G-CON-CWP CWP-01-CV-01 | 2027-03-22
6 | ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings | NONE | IFR | A | no | 2027-01-25 | 2027-03-01 | G-CON-CWP CWP-07-SS-01 | 2027-06-14
6 | ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings | NONE | IFR | A | no | 2027-01-25 | 2027-03-01 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
6 | ALP-EPC-10UHA-CV-FND-0002 | HRSG Foundations and Structures - Piling Layout and Pile Schedule | NONE | IFR | A | no | 2027-01-26 | 2027-03-02 | G-CON-CWP CWP-01-CV-01 | 2027-03-22
6 | ALP-EPC-00000-ME-LST-0001 | Heavy and Oversized Piece List | NONE | IFR | A | no | 2027-02-03 | 2027-03-03 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-00UQA-CV-ARC-0001 | Utility Building - Architectural Drawings | NONE | IFR | A | no | 2027-01-27 | 2027-03-03 | G-CON-CWP CWP-08-SS-01 | 2027-06-29
6 | ALP-S01-00000-GE-ITP-0001 | Structural Steel Supply and Fabrication - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-02-17 | 2027-03-03
6 | ALP-S01-00000-GE-MOS-0001 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-02-17 | 2027-03-03
6 | ALP-S01-00000-GE-MOS-0002 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-02-17 | 2027-03-03
6 | ALP-S01-00000-GE-MOS-0003 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-02-17 | 2027-03-03
6 | ALP-S01-00000-GE-MOS-0004 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-02-17 | 2027-03-03
6 | ALP-S01-00000-GE-MOS-0005 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-02-17 | 2027-03-03
6 | ALP-S01-00000-GE-MOS-0006 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-02-17 | 2027-03-03
6 | ALP-EPC-00GMA-ME-DSH-0004 | Process Drains and Waste Water Collection: Filter - Datasheet | NONE | IFR | A | no | 2027-02-04 | 2027-03-04
6 | ALP-EPC-10UMA-CV-FND-0001 | Gas Turbine Hall - Piling Layout and Pile Schedule | NONE | IFR | A | no | 2027-01-28 | 2027-03-04 | G-CON-CWP CWP-01-CV-01 | 2027-03-22
6 | ALP-EPC-00SAA-ME-DSH-0001 | HVAC: Compressors - Datasheet | NONE | IFR | A | no | 2027-02-05 | 2027-03-05
6 | ALP-EPC-00ACA-CM-OMM-0001 | 380 kV GIS Switchyard - Operating Procedures | NONE | IFR | A | no | 2027-02-08 | 2027-03-08 | G-COM-SC-EL 00ACA | 2028-05-09
6 | ALP-EPC-00BBA-CM-OMM-0001 | MV Switchgear 10.5 kV - Operating Procedures | NONE | IFR | A | no | 2027-02-08 | 2027-03-08 | G-COM-SC-EL 00BBA | 2028-05-09
6 | ALP-EPC-00BFA-CM-OMM-0001 | LV Switchgear 0.4 kV - Operating Procedures | NONE | IFR | A | no | 2027-02-08 | 2027-03-08 | G-COM-SC-EL 00BFA | 2028-05-09
6 | ALP-EPC-00BFT-CM-OMM-0001 | LV Transformers - Operating Procedures | NONE | IFR | A | no | 2027-02-08 | 2027-03-08 | G-COM-SC-EL 00BFT | 2028-05-09
6 | ALP-EPC-00GMA-ME-DSH-0006 | Process Drains and Waste Water Collection: Tank - Datasheet | NONE | IFR | A | no | 2027-02-08 | 2027-03-08
6 | ALP-EPC-00SAA-ME-DSH-0003 | HVAC: Pumps - Datasheet | NONE | IFR | A | no | 2027-02-08 | 2027-03-08
6 | ALP-EPC-10UMA-CV-ARC-0001 | Gas Turbine Hall - Architectural Drawings | NONE | IFR | A | no | 2027-02-01 | 2027-03-08 | G-CON-CWP CWP-01-SS-01 | 2027-07-12
6 | ALP-EPC-20UMB-CV-FND-0001 | Steam Turbine Hall - Piling Layout and Pile Schedule | NONE | IFR | A | no | 2027-02-01 | 2027-03-08 | G-CON-CWP CWP-02-CV-01 | 2027-03-22
6 | ALP-EPC-00BLA-CM-OMM-0001 | Lighting and Small Power - Operating Procedures | NONE | IFR | A | no | 2027-02-09 | 2027-03-09 | G-COM-SC-EL 00BLA | 2028-05-09
6 | ALP-EPC-00SGC-ME-DSH-0001 | Deluge, Spray and Foam Systems: Tank - Datasheet | NONE | IFR | A | no | 2027-02-09 | 2027-03-09
6 | ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings | NONE | IFR | A | no | 2027-02-02 | 2027-03-09 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
6 | ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings | NONE | IFR | A | no | 2027-02-02 | 2027-03-09 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
6 | ALP-EPC-00GMA-ME-DSH-0005 | Process Drains and Waste Water Collection: Pumps - Datasheet | NONE | IFR | A | no | 2027-02-10 | 2027-03-10
6 | ALP-EPC-00GNA-ME-DSH-0002 | Waste Water Treatment: Pumps - Datasheet | NONE | IFR | A | no | 2027-02-10 | 2027-03-10
6 | ALP-EPC-00GUA-ME-DSH-0002 | Sanitary Waste Water Treatment: Pumps - Datasheet | NONE | IFR | A | no | 2027-02-10 | 2027-03-10
6 | ALP-EPC-00SAA-ME-DSH-0002 | HVAC: Fans - Datasheet | NONE | IFR | A | no | 2027-02-10 | 2027-03-10
6 | ALP-EPC-00EGC-IC-DSH-0002 | LDO Forwarding and Treatment - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-02-12 | 2027-03-12
6 | ALP-EPC-00EKA-IC-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-02-12 | 2027-03-12
6 | ALP-EPC-00GNA-ME-DSH-0003 | Waste Water Treatment: Tanks - Datasheet | NONE | IFR | A | no | 2027-02-12 | 2027-03-12
6 | ALP-EPC-00PBA-ME-DSH-0002 | Electro-Chlorination: Fans - Datasheet | NONE | IFR | A | no | 2027-02-12 | 2027-03-12
6 | ALP-EPC-00PBA-ME-DSH-0003 | Electro-Chlorination: Filters - Datasheet | NONE | IFR | A | no | 2027-02-12 | 2027-03-12
6 | ALP-EPC-00PBA-ME-DSH-0005 | Electro-Chlorination: Tanks - Datasheet | NONE | IFR | A | no | 2027-02-12 | 2027-03-12
6 | ALP-EPC-00SGC-ME-DSH-0002 | Deluge, Spray and Foam Systems: Valves - Datasheet | NONE | IFR | A | no | 2027-02-12 | 2027-03-12
6 | ALP-EPC-00BMA-CM-OMM-0001 | Emergency LV Switchgear - Operating Procedures | NONE | IFR | A | no | 2027-02-15 | 2027-03-15 | G-COM-SC-EL 00BMA | 2028-05-09
6 | ALP-EPC-00CJG-IC-DSH-0001 | Safety Instrumented Systems: Control System - Datasheet | NONE | IFR | A | no | 2027-02-15 | 2027-03-15
6 | ALP-EPC-00CKA-IC-DSH-0001 | Historian, Performance Monitoring and Operator Training Simulator: Control System - Datasheet | NONE | IFR | A | no | 2027-02-15 | 2027-03-15
6 | ALP-EPC-00PAA-ME-DSH-0002 | CW Intake, Screens and Outfall: Pumps - Datasheet | NONE | IFR | A | no | 2027-02-15 | 2027-03-15
6 | ALP-EPC-00PAA-ME-DSH-0003 | CW Intake, Screens and Outfall: Valves - Datasheet | NONE | IFR | A | no | 2027-02-15 | 2027-03-15
6 | ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | NONE | IFR | A | no | 2027-02-15 | 2027-03-15 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
6 | ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative | NONE | IFR | A | no | 2027-02-16 | 2027-03-16
6 | ALP-EPC-00PBA-ME-DSH-0004 | Electro-Chlorination: Pumps - Datasheet | NONE | IFR | A | no | 2027-02-16 | 2027-03-16
6 | ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings | NONE | IFR | A | no | 2027-02-09 | 2027-03-16 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
6 | ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative | NONE | IFR | A | no | 2027-02-17 | 2027-03-17
6 | ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative | NONE | IFR | A | no | 2027-02-17 | 2027-03-17
6 | ALP-EPC-00BRA-CM-OMM-0001 | UPS - Operating Procedures | NONE | IFR | A | no | 2027-02-18 | 2027-03-18 | G-COM-SC-EL 00BRA | 2028-05-09
6 | ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative | NONE | IFR | A | no | 2027-02-18 | 2027-03-18
6 | ALP-EPC-00UPA-GE-RPT-0001 | Marine Works - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-11 | 2027-03-18 | G-PRC-PO MR-CV-003 | 2027-05-14
6 | ALP-EPC-00000-GE-RPT-0003 | Power and Control Cables - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-15 | 2027-03-22 | G-PRC-PO MR-EL-008 | 2027-06-21
6 | ALP-EPC-00000-GE-RPT-0012 | Valves - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-15 | 2027-03-22 | G-PRC-PO MR-PI-003 | 2027-06-14
6 | ALP-EPC-00EKA-IC-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Instrument Datasheets | NONE | IFR | A | no | 2027-02-22 | 2027-03-22
6 | ALP-EPC-00PGA-ME-DSH-0004 | Closed Cooling Water: Filter - Datasheet | NONE | IFR | A | no | 2027-02-23 | 2027-03-23
6 | ALP-EPC-00EGC-IC-DSH-0001 | LDO Forwarding and Treatment - Instrument Datasheets | NONE | IFR | A | no | 2027-02-24 | 2027-03-24
6 | ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative | NONE | IFR | A | no | 2027-02-24 | 2027-03-24
6 | ALP-EPC-00UCA-CV-FND-0001 | Control Building - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-02-17 | 2027-03-24 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
6 | ALP-EPC-00USA-CV-FND-0001 | Workshop and Warehouse - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-02-17 | 2027-03-24 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
6 | ALP-EPC-00UYA-CV-FND-0001 | Administration Building - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-02-17 | 2027-03-24 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
6 | ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-02-18 | 2027-03-25 | G-CON-CWP CWP-04-CV-01 | 2027-04-05
6 | ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-02-18 | 2027-03-25 | G-CON-CWP CWP-03-CV-01 | 2027-03-29
6 | ALP-EPC-00000-ME-RPT-0001 | Abnormal Load Route Survey and Transport Drawings | NONE | IFR | A | no | 2027-03-05 | 2027-03-26
6 | ALP-EPC-00SAA-IC-DSH-0002 | HVAC - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-02-26 | 2027-03-26
6 | ALP-EPC-00CJG-GE-ITP-0001 | BOP Safety Instrumented System - Inspection and Test Plan | NONE | IFR | A | no | 2027-03-01 | 2027-03-29 | G-PRC-PO MR-IC-008 | 2027-06-07
6 | ALP-EPC-00BTA-CM-OMM-0001 | Batteries and DC 220 V - Operating Procedures | NONE | IFR | A | no | 2027-03-02 | 2027-03-30 | G-COM-SC-EL 00BTA | 2028-05-09
6 | ALP-EPC-00GKA-ME-DSH-0002 | Potable Water: Filters - Datasheet | NONE | IFR | A | no | 2027-03-02 | 2027-03-30
6 | ALP-EPC-00PGA-IC-DSH-0002 | Closed Cooling Water - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-03-02 | 2027-03-30
6 | ALP-EPC-00GKA-ME-DSH-0003 | Potable Water: Pumps - Datasheet | NONE | IFR | A | no | 2027-03-03 | 2027-03-31
6 | ALP-EPC-00SAA-IC-DSH-0001 | HVAC - Instrument Datasheets | NONE | IFR | A | no | 2027-03-03 | 2027-03-31
6 | ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | NONE | IFR | A | no | 2027-03-03 | 2027-03-31 | G-CON-CWP CWP-10-PI-01 | 2027-12-27
6 | ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-02-24 | 2027-03-31 | G-CON-CWP CWP-07-CV-01 | 2027-04-05
6 | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | NONE | IFR | A | no | 2027-03-03 | 2027-03-31 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
6 | ALP-EPC-00CKA-GE-ITP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Inspection and Test Plan | NONE | IFR | A | no | 2027-03-08 | 2027-04-05 | G-PRC-PO MR-IC-009 | 2027-06-21
6 | ALP-EPC-00PGA-IC-CNR-0001 | Closed Cooling Water - Control Narrative | NONE | IFR | A | no | 2027-03-08 | 2027-04-05
6 | ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | NONE | IFR | A | no | 2027-03-08 | 2027-04-05 | G-CON-CWP CWP-09-PI-01 | 2027-11-29
6 | ALP-EPC-00XJA-CM-OMM-0001 | Emergency Diesel Generator - Operating Procedures | NONE | IFR | A | no | 2027-03-08 | 2027-04-05 | G-COM-SC-EL 00XJA | 2028-05-09
6 | ALP-EPC-10BBT-CM-OMM-0001 | GT Unit Auxiliary Transformer - Operating Procedures | NONE | IFR | A | no | 2027-03-08 | 2027-04-05 | G-COM-SC-EL 10BBT | 2028-05-09
6 | ALP-EPC-20BBT-CM-OMM-0001 | ST Unit Auxiliary Transformer - Operating Procedures | NONE | IFR | A | no | 2027-03-08 | 2027-04-05 | G-COM-SC-EL 20BBT | 2028-05-09
6 | ALP-EPC-00000-ME-PLN-0001 | Marine Operations Plan | NONE | IFR | A | no | 2027-03-03 | 2027-04-07
6 | ALP-EPC-00CYA-IC-DSH-0001 | Telecom, CCTV, Access Control, Security - Datasheet | NONE | IFR | A | no | 2027-03-10 | 2027-04-07
6 | ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification | NONE | IFR | A | no | 2027-03-03 | 2027-04-07 | G-PRC-ENQ MR-IC-006 | 2027-05-24
6 | ALP-C03-00UPA-GE-ITP-0001 | Marine Works - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-03-25 | 2027-04-08
6 | ALP-C03-00UPA-GE-MOS-0001 | Marine Works - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-03-25 | 2027-04-08
6 | ALP-C03-00UPA-GE-MOS-0002 | Marine Works - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-03-25 | 2027-04-08
6 | ALP-C03-00UPA-GE-MOS-0003 | Marine Works - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-03-25 | 2027-04-08
6 | ALP-C03-00UPA-GE-MOS-0004 | Marine Works - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-03-25 | 2027-04-08
6 | ALP-C03-00UPA-GE-MOS-0005 | Marine Works - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-03-25 | 2027-04-08
6 | ALP-C03-00UPA-GE-MOS-0006 | Marine Works - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-03-25 | 2027-04-08
6 | ALP-EPC-00000-GE-RPT-0015 | Safety and Relief Valves - Technical Bid Evaluation | NONE | IFR | A | no | 2027-04-01 | 2027-04-08 | G-PRC-PO MR-PI-007 | 2027-08-02
6 | ALP-EPC-00PAH-ME-DSH-0002 | Condenser Tube Cleaning: Filters - Datasheet | NONE | IFR | A | no | 2027-03-12 | 2027-04-09
6 | ALP-EPC-00PAH-ME-DSH-0003 | Condenser Tube Cleaning: Pumps - Datasheet | NONE | IFR | A | no | 2027-03-12 | 2027-04-09
6 | ALP-EPC-00PGA-IC-DSH-0001 | Closed Cooling Water - Instrument Datasheets | NONE | IFR | A | no | 2027-03-12 | 2027-04-09
6 | ALP-EPC-10HAN-ME-DSH-0002 | HRSG Blowdown and Drains: Pumps - Datasheet | NONE | IFR | A | no | 2027-03-12 | 2027-04-09
6 | ALP-E08-00000-ME-DSH-0001 | Power and Control Cables - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-03-29 | 2027-04-12
6 | ALP-E08-00000-ME-ITP-0001 | Power and Control Cables - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-29 | 2027-04-12
6 | ALP-EPC-00000-GE-RPT-0014 | Piping Specialty Items - Technical Bid Evaluation | NONE | IFR | A | no | 2027-04-05 | 2027-04-12 | G-PRC-PO MR-PI-006 | 2027-08-30
6 | ALP-EPC-00GBA-IC-DSH-0002 | Seawater Reverse Osmosis - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-03-17 | 2027-04-14
6 | ALP-EPC-00CYA-GE-ITP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Inspection and Test Plan | NONE | IFR | A | no | 2027-03-18 | 2027-04-15 | G-PRC-PO MR-IC-007 | 2027-07-19
6 | ALP-EPC-00QCA-ME-DSH-0003 | Chemical Dosing: Tanks - Datasheet | NONE | IFR | A | no | 2027-03-18 | 2027-04-15
6 | ALP-EPC-00QJA-ME-DSH-0002 | Nitrogen Supply: Tank - Datasheet | NONE | IFR | A | no | 2027-03-18 | 2027-04-15
6 | ALP-EPC-00PBA-IC-DSH-0002 | Electro-Chlorination - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-03-19 | 2027-04-16
6 | ALP-EPC-00QCA-ME-DSH-0002 | Chemical Dosing: Pumps - Datasheet | NONE | IFR | A | no | 2027-03-19 | 2027-04-16
6 | ALP-EPC-00GNA-IC-DSH-0002 | Waste Water Treatment - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-03-22 | 2027-04-19
6 | ALP-EPC-00QUA-ME-DSH-0002 | Sampling and SWAS: Heat Exchanger - Datasheet | NONE | IFR | A | no | 2027-03-22 | 2027-04-19
6 | ALP-EPC-00GBA-IC-CNR-0001 | Seawater Reverse Osmosis - Control Narrative | NONE | IFR | A | no | 2027-03-23 | 2027-04-20
6 | ALP-EPC-00UPC-SS-STL-0001 | CW Pump House - Steel Structure Drawings | NONE | IFR | A | no | 2027-03-16 | 2027-04-20 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
6 | ALP-P03-00000-ME-DSH-0001 | Valves - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-04-01 | 2027-04-20
6 | ALP-P03-00000-ME-ITP-0001 | Valves - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-04-01 | 2027-04-20
6 | ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-03-17 | 2027-04-21 | G-CON-CWP CWP-08-CV-01 | 2027-05-04
6 | ALP-EPC-00CJA-CM-OMM-0001 | Plant DCS - Operating Procedures | NONE | IFR | A | no | 2027-03-25 | 2027-04-22 | G-COM-SC-FF 00CJA | 2028-07-24
6 | ALP-EPC-00GMA-IC-CNR-0001 | Process Drains and Waste Water Collection - Control Narrative | NONE | IFR | A | no | 2027-03-25 | 2027-04-22
6 | ALP-EPC-00GNA-IC-CNR-0001 | Waste Water Treatment - Control Narrative | NONE | IFR | A | no | 2027-03-26 | 2027-04-23
6 | ALP-EPC-00PAA-IC-CNR-0001 | CW Intake, Screens and Outfall - Control Narrative | NONE | IFR | A | no | 2027-03-26 | 2027-04-23
6 | ALP-EPC-00PBA-IC-CNR-0001 | Electro-Chlorination - Control Narrative | NONE | IFR | A | no | 2027-03-26 | 2027-04-23
6 | ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative | NONE | IFR | A | no | 2027-03-26 | 2027-04-23
6 | ALP-EPC-00UAC-SS-STL-0002 | GIS Building - Steel Structure Drawings | NONE | IFR | A | no | 2027-03-19 | 2027-04-23 | G-CON-CWP CWP-04-SS-01 | 2027-05-31
6 | ALP-EPC-00GBA-IC-DSH-0001 | Seawater Reverse Osmosis - Instrument Datasheets | NONE | IFR | A | no | 2027-03-29 | 2027-04-26
6 | ALP-EPC-00QEA-IC-CNR-0001 | Compressed Air - Control Narrative | NONE | IFR | A | no | 2027-03-29 | 2027-04-26
6 | ALP-EPC-00UZC-EL-ELY-0001 | Site Drainage and Culverts - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-03-29 | 2027-04-26 | G-CON-CWP CWP-12-EL-01 | 2027-05-17
6 | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | NONE | IFR | A | no | 2027-04-23 | 2027-04-28 | G-PRC-ENQ MR-ME-022 | 2027-11-15
6 | ALP-EPC-00GMA-IC-DSH-0001 | Process Drains and Waste Water Collection - Instrument Datasheets | NONE | IFR | A | no | 2027-04-01 | 2027-04-29
6 | ALP-P07-00000-ME-DSH-0001 | Safety and Relief Valves - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-04-15 | 2027-04-29
6 | ALP-P07-00000-ME-ITP-0001 | Safety and Relief Valves - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-04-15 | 2027-04-29
6 | ALP-EPC-00CJG-CM-OMM-0001 | Safety Instrumented Systems - Operating Procedures | NONE | IFR | A | no | 2027-04-02 | 2027-04-30 | G-COM-SC-FF 00CJG | 2028-07-24
6 | ALP-EPC-00GNA-IC-DSH-0001 | Waste Water Treatment - Instrument Datasheets | NONE | IFR | A | no | 2027-04-02 | 2027-04-30
6 | ALP-EPC-00PAA-IC-DSH-0001 | CW Intake, Screens and Outfall - Instrument Datasheets | NONE | IFR | A | no | 2027-04-02 | 2027-04-30
6 | ALP-EPC-00PBA-IC-DSH-0001 | Electro-Chlorination - Instrument Datasheets | NONE | IFR | A | no | 2027-04-02 | 2027-04-30
6 | ALP-EPC-00QEA-IC-DSH-0002 | Compressed Air - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-04-02 | 2027-04-30
6 | ALP-EPC-00000-HS-RPT-0002 | Constructability and Maintainability Review | NONE | IFR | A | no | 2027-04-12 | 2027-05-03
6 | ALP-P06-00000-ME-DSH-0001 | Piping Specialty Items - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-04-19 | 2027-05-03
6 | ALP-P06-00000-ME-ITP-0001 | Piping Specialty Items - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-04-19 | 2027-05-03
6 | ALP-EPC-00QCA-IC-DSH-0001 | Chemical Dosing - Instrument Datasheets | NONE | IFR | A | no | 2027-04-06 | 2027-05-04
6 | ALP-EPC-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Structure Drawings | NONE | IFR | A | no | 2027-03-30 | 2027-05-04 | G-CON-CWP CWP-10-CV-01 | 2027-06-03
6 | ALP-EPC-00EGA-IC-DSH-0002 | LDO Unloading - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-04-08 | 2027-05-06
6 | ALP-EPC-00CKA-CM-OMM-0001 | Historian, Performance Monitoring and Operator Training Simulator - Operating Procedures | NONE | IFR | A | no | 2027-04-09 | 2027-05-07 | G-COM-SC-FF 00CKA | 2028-07-24
6 | ALP-EPC-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Structure Drawings | NONE | IFR | A | no | 2027-04-07 | 2027-05-12 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
6 | ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative | NONE | IFR | A | no | 2027-04-15 | 2027-05-13
6 | ALP-EPC-00QHA-IC-CNR-0001 | Auxiliary Boiler - Control Narrative | NONE | IFR | A | no | 2027-04-15 | 2027-05-13
6 | ALP-EPC-00UBA-SS-STL-0002 | Electrical Building - Steel Structure Drawings | NONE | IFR | A | no | 2027-04-08 | 2027-05-13 | G-CON-CWP CWP-03-SS-01 | 2027-05-24
6 | ALP-EPC-00000-HS-RPT-0006 | Occupational Health and Safety Risk Assessment | NONE | IFR | A | no | 2027-04-23 | 2027-05-14
6 | ALP-EPC-00CQA-CM-OMM-0001 | Continuous Emission Monitoring - Operating Procedures | NONE | IFR | A | no | 2027-04-16 | 2027-05-14 | G-COM-SC-FF 00CQA | 2028-07-24
6 | ALP-EPC-00UGA-SS-STL-0002 | Water Treatment Building and Basins - Steel Structure Drawings | NONE | IFR | A | no | 2027-04-09 | 2027-05-14 | G-CON-CWP CWP-07-SS-01 | 2027-06-14
6 | ALP-EPC-00UZD-CV-FND-0001 | Pipe Racks and Pipe Sleepers - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-04-09 | 2027-05-14 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
6 | ALP-EPC-00UZE-EL-ELY-0001 | Cable Trenches and Duct Banks - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-04-16 | 2027-05-14 | G-CON-CWP CWP-12-EL-01 | 2027-05-17
6 | ALP-EPC-00CYA-CM-OMM-0001 | Telecom, CCTV, Access Control, Security - Operating Procedures | NONE | IFR | A | no | 2027-04-19 | 2027-05-17 | G-COM-SC-FF 00CYA | 2028-07-24
6 | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | NONE | IFR | A | no | 2027-04-19 | 2027-05-17 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
6 | ALP-EPC-00BXA-GE-RPT-0001 | Cathodic Protection - Technical Bid Evaluation | NONE | IFR | A | no | 2027-05-11 | 2027-05-18 | G-PRC-PO MR-EL-010 | 2027-06-21
6 | ALP-EPC-00UBA-HV-GAD-0001 | Electrical Building and Emergency Power - HVAC Layouts | NONE | IFR | A | no | 2027-04-21 | 2027-05-19 | G-CON-CWP CWP-03-HV-01 | 2027-10-11
6 | ALP-EPC-00EGA-IC-DSH-0001 | LDO Unloading - Instrument Datasheets | NONE | IFR | A | no | 2027-04-22 | 2027-05-20
6 | ALP-EPC-00EKC-IC-DSH-0002 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-04-23 | 2027-05-21
6 | ALP-EPC-00EGA-PR-DSH-0001 | LDO Unloading - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-04-26 | 2027-05-24
6 | ALP-EPC-00GHA-IC-DSH-0002 | Demineralised Water Storage and Distribution - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-04-26 | 2027-05-24
6 | ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative | NONE | IFR | A | no | 2027-04-27 | 2027-05-25
6 | ALP-EPC-00GCA-IC-DSH-0002 | Demineralisation - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-04-27 | 2027-05-25
6 | ALP-EPC-00LBG-IC-DSH-0002 | Auxiliary Steam - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-04-28 | 2027-05-26
6 | ALP-EPC-00LDA-IC-DSH-0002 | Condensate Polishing - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-04-29 | 2027-05-27
6 | ALP-EPC-00UCA-HV-GAD-0001 | Control, Administration and Workshop Buildings - HVAC Layouts | NONE | IFR | A | no | 2027-04-29 | 2027-05-27 | G-CON-CWP CWP-11-HV-01 | 2027-11-08
6 | ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-04-22 | 2027-05-27 | G-CON-CWP CWP-10-CV-01 | 2027-06-03
6 | ALP-EPC-10UMA-HV-GAD-0001 | Power Block - GT and HRSG - HVAC Layouts | NONE | IFR | A | no | 2027-04-29 | 2027-05-27 | G-CON-CWP CWP-01-HV-01 | 2027-11-01
6 | ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative | NONE | IFR | A | no | 2027-04-30 | 2027-05-28
6 | ALP-EPC-00GCA-IC-CNR-0001 | Demineralisation - Control Narrative | NONE | IFR | A | no | 2027-04-30 | 2027-05-28
6 | ALP-EPC-00GHA-IC-CNR-0001 | Demineralised Water Storage and Distribution - Control Narrative | NONE | IFR | A | no | 2027-05-03 | 2027-05-31
6 | ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative | NONE | IFR | A | no | 2027-05-03 | 2027-05-31
6 | ALP-EPC-00LDA-IC-CNR-0001 | Condensate Polishing - Control Narrative | NONE | IFR | A | no | 2027-05-03 | 2027-05-31
6 | ALP-EPC-00PAB-IC-CNR-0001 | CW Piping - Control Narrative | NONE | IFR | A | no | 2027-05-03 | 2027-05-31
6 | ALP-EPC-00PAC-IC-CNR-0001 | CW Pumps - Control Narrative | NONE | IFR | A | no | 2027-05-03 | 2027-05-31
6 | ALP-EPC-00EGB-IC-DSH-0001 | LDO Storage - Instrument Datasheets | NONE | IFR | A | no | 2027-05-04 | 2027-06-01
6 | ALP-EPC-00PAH-IC-CNR-0001 | Condenser Tube Cleaning - Control Narrative | NONE | IFR | A | no | 2027-05-04 | 2027-06-01
6 | ALP-EPC-00000-GE-RPT-0013 | Pipe Supports, Spring Hangers and Snubbers - Technical Bid Evaluation | NONE | IFR | A | no | 2027-05-27 | 2027-06-03 | G-PRC-PO MR-PI-005 | 2027-08-30
6 | ALP-EPC-00EKC-IC-DSH-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Instrument Datasheets | NONE | IFR | A | no | 2027-05-07 | 2027-06-04
6 | ALP-EPC-00GCA-IC-DSH-0001 | Demineralisation - Instrument Datasheets | NONE | IFR | A | no | 2027-05-07 | 2027-06-04
6 | ALP-EPC-00GHA-IC-DSH-0001 | Demineralised Water Storage and Distribution - Instrument Datasheets | NONE | IFR | A | no | 2027-05-10 | 2027-06-07
6 | ALP-EPC-00LBG-IC-DSH-0001 | Auxiliary Steam - Instrument Datasheets | NONE | IFR | A | no | 2027-05-10 | 2027-06-07
6 | ALP-E10-00BXA-ME-ITP-0001 | Cathodic Protection - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-05-25 | 2027-06-08 | G-PRC-FAB MR-EL-010 | 2027-08-04
6 | ALP-EPC-00LDA-IC-DSH-0001 | Condensate Polishing - Instrument Datasheets | NONE | IFR | A | no | 2027-05-11 | 2027-06-08
6 | ALP-EPC-00PAB-IC-DSH-0001 | CW Piping - Instrument Datasheets | NONE | IFR | A | no | 2027-05-11 | 2027-06-08
6 | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | NONE | IFR | A | no | 2027-05-11 | 2027-06-08 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
6 | ALP-EPC-00000-GE-RPT-0008 | Instrument Installation Materials - Technical Bid Evaluation | NONE | IFR | A | no | 2027-06-02 | 2027-06-09 | G-PRC-PO MR-IC-010 | 2027-11-29
6 | ALP-EPC-00UZF-CV-RPT-0001 | Temporary Barge Landing Design Report and Removal Plan | NONE | IFR | A | no | 2027-05-19 | 2027-06-09
6 | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | NONE | IFR | A | no | 2027-05-12 | 2027-06-09 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
6 | ALP-EPC-00000-CV-TRP-0001 | Pile Load Test Report and Pile Design Confirmation | NONE | IFR | A | no | 2027-05-20 | 2027-06-10 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-00PAC-IC-DSH-0001 | CW Pumps - Instrument Datasheets | NONE | IFR | A | no | 2027-05-13 | 2027-06-10
6 | ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | NONE | IFR | A | no | 2027-05-07 | 2027-06-11
6 | ALP-EPC-00PAH-IC-DSH-0001 | Condenser Tube Cleaning - Instrument Datasheets | NONE | IFR | A | no | 2027-05-14 | 2027-06-11
6 | ALP-EPC-00UCA-SS-STL-0002 | Control Building - Steel Structure Drawings | NONE | IFR | A | no | 2027-05-07 | 2027-06-11 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
6 | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | NONE | IFR | A | no | 2027-05-14 | 2027-06-11 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
6 | ALP-EPC-00UZC-CV-RBR-0001 | Site Drainage and Culverts - Reinforcement Drawings | NONE | IFR | A | no | 2027-05-24 | 2027-06-14 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
6 | ALP-EPC-00EGC-PR-DSH-0001 | LDO Forwarding and Treatment - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-05-18 | 2027-06-15
6 | ALP-EPC-00UQA-SS-STL-0001 | Utility Building - Steel Structure Drawings | NONE | IFR | A | no | 2027-05-11 | 2027-06-15 | G-CON-CWP CWP-08-SS-01 | 2027-06-29
6 | ALP-EPC-00USA-SS-STL-0002 | Workshop and Warehouse - Steel Structure Drawings | NONE | IFR | A | no | 2027-05-11 | 2027-06-15 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
6 | ALP-EPC-00UYA-SS-STL-0002 | Administration Building - Steel Structure Drawings | NONE | IFR | A | no | 2027-05-11 | 2027-06-15 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
6 | ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative | NONE | IFR | A | no | 2027-05-19 | 2027-06-16
6 | ALP-EPC-00UZE-CV-RBR-0001 | Cable Trenches and Duct Banks - Reinforcement Drawings | NONE | IFR | A | no | 2027-05-27 | 2027-06-17 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
6 | ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative | NONE | IFR | A | no | 2027-05-21 | 2027-06-18
6 | ALP-E10-00BXA-ME-TST-0001 | Cathodic Protection - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-11 | 2027-06-22 | G-PRC-FAT MR-EL-010 | 2027-08-03
6 | ALP-EPC-00EGB-PR-DSH-0001 | LDO Storage - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-05-26 | 2027-06-23
6 | ALP-EPC-00EKC-PR-DSH-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-05-26 | 2027-06-23
6 | ALP-P05-00000-ME-DSH-0001 | Pipe Supports, Spring Hangers and Snubbers - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-06-10 | 2027-06-24
6 | ALP-P05-00000-ME-ITP-0001 | Pipe Supports, Spring Hangers and Snubbers - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-06-10 | 2027-06-24
6 | ALP-EPC-00GCA-PR-DSH-0001 | Demineralisation - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-05-28 | 2027-06-25
6 | ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative | NONE | IFR | A | no | 2027-05-28 | 2027-06-25
6 | ALP-EPC-00GBA-PR-DSH-0001 | Seawater Reverse Osmosis - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-05-31 | 2027-06-28
6 | ALP-EPC-00GHA-PR-DSH-0001 | Demineralised Water Storage and Distribution - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-05-31 | 2027-06-28
6 | ALP-EPC-00LDA-PR-DSH-0001 | Condensate Polishing - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-05-31 | 2027-06-28
6 | ALP-EPC-00QEA-IC-DSH-0001 | Compressed Air - Instrument Datasheets | NONE | IFR | A | no | 2027-05-31 | 2027-06-28
6 | ALP-EPC-00UEK-CV-ARC-0001 | Gas Station Structures - Architectural Drawings | NONE | IFR | A | no | 2027-05-24 | 2027-06-28 | G-CON-CWP CWP-09-CV-01 | 2027-08-04
6 | ALP-E10-00BXA-IC-IOL-0001 | Cathodic Protection - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-06-08 | 2027-06-29
6 | ALP-EPC-00LBG-PR-DSH-0001 | Auxiliary Steam - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-01 | 2027-06-29
6 | ALP-EPC-00SAA-PR-DSH-0001 | HVAC - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-01 | 2027-06-29
6 | ALP-EPC-00SGA-PR-CAL-0001 | Fire Water Network Hydraulic Calculation | NONE | IFR | A | no | 2027-06-08 | 2027-06-29
6 | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | NONE | IFR | A | no | 2027-06-25 | 2027-06-30 | G-PRC-ENQ MR-ME-023 | 2027-08-30
6 | ALP-EPC-00PGA-PR-DSH-0001 | Closed Cooling Water - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-02 | 2027-06-30
6 | ALP-EPC-00QJA-PR-DSH-0001 | Nitrogen Supply - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-02 | 2027-06-30
6 | ALP-EPC-00QJB-PR-DSH-0001 | Hydrogen and CO2 Supply - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-02 | 2027-06-30
6 | ALP-EPC-00UZF-CV-FND-0002 | Temporary Barge Landing - Piling Layout and Pile Schedule | NONE | IFR | A | no | 2027-05-26 | 2027-06-30 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
6 | ALP-I10-00000-ME-DSH-0001 | Instrument Installation Materials - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-06-16 | 2027-06-30
6 | ALP-I10-00000-ME-ITP-0001 | Instrument Installation Materials - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-06-16 | 2027-06-30
6 | ALP-EPC-00QCA-PR-DSH-0001 | Chemical Dosing - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-03 | 2027-07-01
6 | ALP-EPC-00QEA-PR-DSH-0001 | Compressed Air - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-03 | 2027-07-01
6 | ALP-EPC-00QHA-PR-DSH-0001 | Auxiliary Boiler - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-03 | 2027-07-01
6 | ALP-EPC-00EKA-PR-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-04 | 2027-07-02
6 | ALP-EPC-00GKA-IC-DSH-0001 | Potable Water - Instrument Datasheets | NONE | IFR | A | no | 2027-06-04 | 2027-07-02
6 | ALP-EPC-00GUA-IC-DSH-0001 | Sanitary Waste Water Treatment - Instrument Datasheets | NONE | IFR | A | no | 2027-06-04 | 2027-07-02
6 | ALP-EPC-00UEK-SS-STL-0001 | Gas Station Structures - Steel Structure Drawings | NONE | IFR | A | no | 2027-05-28 | 2027-07-02 | G-CON-CWP CWP-09-CV-01 | 2027-08-04
6 | ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | NONE | IFR | A | no | 2027-06-04 | 2027-07-02
6 | ALP-EPC-00GKA-IC-CNR-0001 | Potable Water - Control Narrative | NONE | IFR | A | no | 2027-06-07 | 2027-07-05
6 | ALP-EPC-00GUA-IC-CNR-0001 | Sanitary Waste Water Treatment - Control Narrative | NONE | IFR | A | no | 2027-06-07 | 2027-07-05
6 | ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-05-31 | 2027-07-05 | G-CON-CWP CWP-09-CV-01 | 2027-08-04
6 | ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative | NONE | IFR | A | no | 2027-06-07 | 2027-07-05
6 | ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative | NONE | IFR | A | no | 2027-06-07 | 2027-07-05
6 | ALP-EPC-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Structure Drawings | NONE | IFR | A | no | 2027-05-31 | 2027-07-05 | G-CON-CWP CWP-01-SS-01 | 2027-07-12
6 | ALP-EPC-00UBF-SS-STL-0001 | Transformer Bays - Steel Structure Drawings | NONE | IFR | A | no | 2027-06-01 | 2027-07-06 | G-CON-CWP CWP-01-SS-01 | 2027-07-12
6 | ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative | NONE | IFR | A | no | 2027-06-08 | 2027-07-06
6 | ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative | NONE | IFR | A | no | 2027-06-08 | 2027-07-06
6 | ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative | NONE | IFR | A | no | 2027-06-08 | 2027-07-06
6 | ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative | NONE | IFR | A | no | 2027-06-08 | 2027-07-06
6 | ALP-EPC-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Structure Drawings | NONE | IFR | A | no | 2027-06-01 | 2027-07-06 | G-CON-CWP CWP-02-SS-01 | 2027-07-12
6 | ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | NONE | IFR | A | no | 2027-06-02 | 2027-07-07
6 | ALP-EPC-00SGA-PR-DSH-0001 | Fire Water System - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-09 | 2027-07-07
6 | ALP-EPC-10HAN-PR-DSH-0001 | HRSG Blowdown and Drains - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-09 | 2027-07-07
6 | ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative | NONE | IFR | A | no | 2027-06-09 | 2027-07-07
6 | ALP-EPC-10LAB-PR-DSH-0001 | Feedwater Piping - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-10 | 2027-07-08
6 | ALP-EPC-10LAC-PR-DSH-0001 | Boiler Feed Pumps - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-10 | 2027-07-08
6 | ALP-EPC-10HSB-PR-DSH-0001 | Ammonia Storage and Supply - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-11 | 2027-07-09
6 | ALP-EPC-20LCA-PR-DSH-0001 | Main Condensate Piping - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-11 | 2027-07-09
6 | ALP-EPC-00QHA-IC-DSH-0002 | Auxiliary Boiler - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-14 | 2027-07-12
6 | ALP-EPC-20MAN-PR-DSH-0001 | Turbine Bypass Stations and Piping - Safety / Relief Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-14 | 2027-07-12
6 | ALP-EPC-00QHA-IC-DSH-0001 | Auxiliary Boiler - Instrument Datasheets | NONE | IFR | A | no | 2027-06-18 | 2027-07-16
6 | ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | NONE | IFR | A | no | 2027-06-14 | 2027-07-19
6 | ALP-EPC-00QJA-IC-DSH-0002 | Nitrogen Supply - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-21 | 2027-07-19
6 | ALP-E10-00BXA-ME-LST-0001 | Cathodic Protection - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-06-22 | 2027-07-20
6 | ALP-E10-00BXA-ME-PRC-0001 | Cathodic Protection - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-08 | 2027-07-20
6 | ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | NONE | IFR | A | no | 2027-06-15 | 2027-07-20
6 | ALP-EPC-00PAB-PR-STU-0001 | CW System Hydraulic Transient Analysis | NONE | IFR | A | no | 2027-06-22 | 2027-07-20
6 | ALP-EPC-00QJB-IC-DSH-0002 | Hydrogen and CO2 Supply - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-06-22 | 2027-07-20
6 | ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative | NONE | IFR | A | no | 2027-06-23 | 2027-07-21
6 | ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative | NONE | IFR | A | no | 2027-06-23 | 2027-07-21
6 | ALP-EPC-00GKA-PI-PPL-0001 | Potable Water - Underground Piping Drawings | NONE | IFR | A | no | 2027-06-24 | 2027-07-22 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
6 | ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative | NONE | IFR | A | no | 2027-06-24 | 2027-07-22
6 | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | NONE | IFR | A | no | 2027-06-28 | 2027-07-26 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
6 | ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative | NONE | IFR | A | no | 2027-06-28 | 2027-07-26
6 | ALP-EPC-00GMA-PI-PPL-0001 | Process Drains and Waste Water Collection - Underground Piping Drawings | NONE | IFR | A | no | 2027-06-29 | 2027-07-27 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
6 | ALP-EPC-00PAB-PI-PPL-0001 | CW Piping - Underground Piping Drawings | NONE | IFR | A | no | 2027-06-29 | 2027-07-27 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
6 | ALP-EPC-00000-IC-LST-0001 | Instrument Index | NONE | IFR | A | no | 2027-06-30 | 2027-07-28 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-00000-PR-LST-0002 | Line List | NONE | IFR | A | no | 2027-06-30 | 2027-07-28 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-00SGA-IC-DSH-0001 | Fire Water System - Instrument Datasheets | NONE | IFR | A | no | 2027-06-30 | 2027-07-28
6 | ALP-EPC-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Structure Drawings | NONE | IFR | A | no | 2027-06-23 | 2027-07-28 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
6 | ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative | NONE | IFR | A | no | 2027-06-30 | 2027-07-28
6 | ALP-EPC-00QJA-IC-DSH-0001 | Nitrogen Supply - Instrument Datasheets | NONE | IFR | A | no | 2027-07-01 | 2027-07-29
6 | ALP-P01-00000-ME-MDB-0001 | Piping Bulk Materials - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-06-03 | 2027-07-29 | G-PRC-SHP MR-PI-001 | 2027-06-17
6 | ALP-EPC-00QJB-IC-DSH-0001 | Hydrogen and CO2 Supply - Instrument Datasheets | NONE | IFR | A | no | 2027-07-06 | 2027-08-03
6 | ALP-EPC-00UBA-PI-PPL-0001 | Electrical Building and Emergency Power - Piping General Arrangement | NONE | IFR | A | no | 2027-07-08 | 2027-08-05 | G-CON-CWP CWP-03-HV-01 | 2027-10-11
6 | ALP-EPC-00QUA-IC-DSH-0001 | Sampling and SWAS - Instrument Datasheets | NONE | IFR | A | no | 2027-07-09 | 2027-08-06
6 | ALP-EPC-00UCA-PI-PPL-0001 | Control, Administration and Workshop Buildings - Piping General Arrangement | NONE | IFR | A | no | 2027-07-09 | 2027-08-06 | G-CON-CWP CWP-11-HV-01 | 2027-11-08
6 | ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings | NONE | IFR | A | no | 2027-07-02 | 2027-08-06 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
6 | ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | NONE | IFR | A | no | 2027-07-07 | 2027-08-11
6 | ALP-E10-00BXA-ME-TRP-0001 | Cathodic Protection - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-03 | 2027-08-17 | G-PRC-SHP MR-EL-010 | 2027-08-31
6 | ALP-EPC-00SGY-CM-OMM-0001 | Fire Detection and Alarm - Operating Procedures | NONE | IFR | A | no | 2027-07-20 | 2027-08-17 | G-COM-SC-FF 00SGY | 2028-07-24
6 | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | NONE | IFR | A | no | 2027-07-21 | 2027-08-18 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
6 | ALP-P06-00000-ME-MDB-0001 | Piping Specialty Items - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-07-12 | 2027-09-06 | G-PRC-SHP MR-PI-006 | 2027-07-26
6 | ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | NONE | IFR | A | no | 2027-08-06 | 2027-09-10 | G-OWN-TOC 00000 | 2028-08-21
6 | ALP-E08-00000-ME-MDB-0001 | Power and Control Cables - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-07-19 | 2027-09-13 | G-PRC-SHP MR-EL-008 | 2027-08-02
6 | ALP-EPC-00000-CM-CMP-0005 | Tests on LDO Procedure | NONE | IFR | A | no | 2027-08-17 | 2027-09-21 | G-OWN-TOC 00000 | 2028-08-21
6 | ALP-EPC-00000-CM-CMP-0006 | Emission and Noise Test Procedure | NONE | IFR | A | no | 2027-08-19 | 2027-09-23 | G-OWN-TOC 00000 | 2028-08-21
6 | ALP-EPC-00SGA-PI-PPL-0001 | Fire Water System - Underground Piping Drawings | NONE | IFR | A | no | 2027-08-26 | 2027-09-23 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
6 | ALP-P07-00000-ME-MDB-0001 | Safety and Relief Valves - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-05 | 2027-09-30 | G-PRC-SHP MR-PI-007 | 2027-08-19
6 | ALP-I10-00000-ME-MDB-0001 | Instrument Installation Materials - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-11 | 2027-10-06 | G-PRC-SHP MR-IC-010 | 2027-08-25
6 | ALP-E10-00BXA-ME-MDB-0001 | Cathodic Protection - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-17 | 2027-10-12 | G-PRC-SHP MR-EL-010 | 2027-08-31
6 | ALP-P03-00000-ME-MDB-0001 | Valves - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-30 | 2027-10-25 | G-PRC-SHP MR-PI-003 | 2027-09-13
6 | ALP-P05-00000-ME-MDB-0001 | Pipe Supports, Spring Hangers and Snubbers - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-02 | 2027-10-28 | G-PRC-SHP MR-PI-005 | 2027-09-16
6 | ALP-EPC-00SGC-IC-DSH-0001 | Deluge, Spray and Foam Systems - Instrument Datasheets | NONE | IFR | A | no | 2027-10-06 | 2027-11-03
6 | ALP-EPC-10HAN-IC-DSH-0002 | HRSG Blowdown and Drains - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-10-06 | 2027-11-03
6 | ALP-EPC-10HSB-IC-DSH-0002 | Ammonia Storage and Supply - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-10-08 | 2027-11-05
6 | ALP-EPC-00000-EL-CAL-0002 | Battery, UPS and DC System Sizing Calculation | NONE | IFR | A | no | 2027-10-18 | 2027-11-08
6 | ALP-EPC-10HAN-IC-DSH-0001 | HRSG Blowdown and Drains - Instrument Datasheets | NONE | IFR | A | no | 2027-10-11 | 2027-11-08
6 | ALP-EPC-00000-EL-CAL-0003 | Emergency Diesel Generator and Transformer Sizing Calculation | NONE | IFR | A | no | 2027-10-19 | 2027-11-09
6 | ALP-EPC-10LAB-IC-DSH-0002 | Feedwater Piping - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-10-12 | 2027-11-09
6 | ALP-EPC-10LAC-IC-DSH-0002 | Boiler Feed Pumps - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-10-13 | 2027-11-10
6 | ALP-EPC-10LAE-IC-DSH-0002 | HP Attemperation Spray Water - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-10-19 | 2027-11-16
6 | ALP-EPC-10HSB-IC-DSH-0001 | Ammonia Storage and Supply - Instrument Datasheets | NONE | IFR | A | no | 2027-10-22 | 2027-11-19
6 | ALP-EPC-10LAB-IC-DSH-0001 | Feedwater Piping - Instrument Datasheets | NONE | IFR | A | no | 2027-10-22 | 2027-11-19
6 | ALP-EPC-10LAE-IC-DSH-0001 | HP Attemperation Spray Water - Instrument Datasheets | NONE | IFR | A | no | 2027-10-22 | 2027-11-19
6 | ALP-EPC-10LAF-IC-DSH-0002 | Reheat Attemperation Spray Water - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-10-22 | 2027-11-19
6 | ALP-E10-00BXA-ME-OMM-0001 | Cathodic Protection - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-06 | 2027-11-23 | G-COM-SC-EL 00BXA | 2028-05-09
6 | ALP-EPC-10LAC-IC-DSH-0001 | Boiler Feed Pumps - Instrument Datasheets | NONE | IFR | A | no | 2027-10-27 | 2027-11-24
6 | ALP-EPC-10LAF-IC-DSH-0001 | Reheat Attemperation Spray Water - Instrument Datasheets | NONE | IFR | A | no | 2027-10-28 | 2027-11-25
6 | ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | NONE | IFR | A | no | 2027-10-29 | 2027-11-26 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-10LBA-IC-DSH-0001 | Main Steam Piping - Instrument Datasheets | NONE | IFR | A | no | 2027-11-05 | 2027-12-03
6 | ALP-EPC-10LBB-IC-DSH-0001 | Hot Reheat Piping - Instrument Datasheets | NONE | IFR | A | no | 2027-11-08 | 2027-12-06
6 | ALP-EPC-20LCB-IC-DSH-0002 | Condensate Extraction Pumps - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-11-08 | 2027-12-06
6 | ALP-EPC-10LBD-IC-DSH-0001 | LP Steam Piping - Instrument Datasheets | NONE | IFR | A | no | 2027-11-09 | 2027-12-07
6 | ALP-EPC-20LCA-IC-DSH-0002 | Main Condensate Piping - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-11-09 | 2027-12-07
6 | ALP-EPC-10LBC-IC-DSH-0001 | Cold Reheat Piping - Instrument Datasheets | NONE | IFR | A | no | 2027-11-10 | 2027-12-08
6 | ALP-EPC-20MAN-IC-DSH-0002 | Turbine Bypass Stations and Piping - Control Valve Sizing and Datasheets | NONE | IFR | A | no | 2027-11-15 | 2027-12-13
6 | ALP-EPC-20LCA-IC-DSH-0001 | Main Condensate Piping - Instrument Datasheets | NONE | IFR | A | no | 2027-11-17 | 2027-12-15
6 | ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | NONE | IFR | A | no | 2027-11-18 | 2027-12-16 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-00000-CM-LST-0003 | Punch List at Taking-Over | NONE | IFR | A | no | 2027-12-02 | 2027-12-16 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-20LCB-IC-DSH-0001 | Condensate Extraction Pumps - Instrument Datasheets | NONE | IFR | A | no | 2027-11-23 | 2027-12-21
6 | ALP-EPC-20MAN-IC-DSH-0001 | Turbine Bypass Stations and Piping - Instrument Datasheets | NONE | IFR | A | no | 2027-11-26 | 2027-12-24
6 | ALP-EPC-00ACA-CM-MDB-0001 | 380 kV GIS Switchyard - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00ACA | 2028-04-11
6 | ALP-EPC-00BBA-CM-MDB-0001 | MV Switchgear 10.5 kV - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00BBA | 2028-04-11
6 | ALP-EPC-00BFA-CM-MDB-0001 | LV Switchgear 0.4 kV - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00BFA | 2028-04-11
6 | ALP-EPC-00BFT-CM-MDB-0001 | LV Transformers - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00BFT | 2028-04-11
6 | ALP-EPC-00BLA-CM-MDB-0001 | Lighting and Small Power - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00BLA | 2028-04-11
6 | ALP-EPC-00BMA-CM-MDB-0001 | Emergency LV Switchgear - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00BMA | 2028-04-11
6 | ALP-EPC-00BRA-CM-MDB-0001 | UPS - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00BRA | 2028-04-11
6 | ALP-EPC-00BTA-CM-MDB-0001 | Batteries and DC 220 V - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00BTA | 2028-04-11
6 | ALP-EPC-00BXA-CM-MDB-0001 | Earthing and Lightning Protection - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00BXA | 2028-04-11
6 | ALP-EPC-00XJA-CM-MDB-0001 | Emergency Diesel Generator - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 00XJA | 2028-04-11
6 | ALP-EPC-10BBT-CM-MDB-0001 | GT Unit Auxiliary Transformer - System Turnover Dossier | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-COM-MC-EL 10BBT | 2028-04-11
6 | ALP-EPC-20BBT-CM-MDB-0001 | ST Unit Auxiliary Transformer - System Turnover Dossier | NONE | IFR | A | no | 2028-02-01 | 2028-02-08 | G-COM-MC-EL 20BBT | 2028-04-11
6 | ALP-EPC-00000-PI-LST-0001 | Valve List | NONE | IFR | A | no | 2028-01-13 | 2028-02-10 | G-OWN-TO 00000 | 2029-04-18
6 | ALP-EPC-00000-CM-OMM-0002 | Training Manuals and Courseware | NONE | IFR | A | no | 2028-01-20 | 2028-02-17
6 | ALP-EPC-00CJA-CM-MDB-0001 | Plant DCS - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00CJA | 2028-06-26
6 | ALP-EPC-00CJG-CM-MDB-0001 | Safety Instrumented Systems - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00CJG | 2028-06-26
6 | ALP-EPC-00CKA-CM-MDB-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00CKA | 2028-06-26
6 | ALP-EPC-00CQA-CM-MDB-0001 | Continuous Emission Monitoring - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00CQA | 2028-06-26
6 | ALP-EPC-00CYA-CM-MDB-0001 | Telecom, CCTV, Access Control, Security - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00CYA | 2028-06-26
6 | ALP-EPC-00SGY-CM-MDB-0001 | Fire Detection and Alarm - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 00SGY | 2028-06-26
6 | ALP-EPC-00SMA-CM-MDB-0001 | Cranes and Hoists - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 00SMA | 2028-06-26
6 | ALP-EPC-10HNE-CM-MDB-0001 | Stack 65 m with CEMS Platform and Silencer - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 10HNE | 2028-06-26
6 | ALP-EPC-00CQA-IC-TRP-0001 | CEMS Certification, QAL1 / QAL2 and AST Reports | NONE | IFR | A | no | 2029-02-19 | 2029-03-12
6 | ALP-EPC-00000-CM-TRP-0004 | Operational Demonstration and Reliability Run Report | NONE | IFR | A | no | 2029-04-04 | 2029-04-25 | G-OWN-TO 00000 | 2029-04-18
7 | ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-PI-004 | 2026-12-21
7 | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-IC-002 | 2027-05-03
7 | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-016 | 2026-11-16
7 | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-015 | 2026-11-16
7 | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-013 | 2027-03-29
7 | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-014 | 2027-03-22
7 | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-012 | 2026-11-16
7 | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-004 | 2027-02-01
7 | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-003 | 2026-11-23
7 | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-006 | 2027-04-26
7 | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-005 | 2027-02-01
7 | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-007 | 2027-01-25
7 | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-008 | 2027-01-25
7 | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-009 | 2026-11-16
7 | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-IC-003 | 2027-05-03
7 | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-HV-001 | 2027-01-04
7 | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-020 | 2027-01-11
7 | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-021 | 2026-11-30
7 | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-019 | 2027-03-15
7 | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-018 | 2027-01-25
7 | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-001 | 2026-11-16
7 | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-ME-002 | 2027-02-01
7 | ALP-EPC-00000-EL-SLD-0002 | Construction Power Supply Single Line Diagram and RMU Design | NONE | IFR | A | no | 2026-11-02 | 2026-11-16 | G-OPS-AB 00000 | 2029-07-18
7 | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | NONE | IFR | A | no | 2026-11-23 | 2026-11-26 | G-PRC-ENQ MR-ME-017 | 2027-05-17
7 | ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-EL-003 | 2026-12-07
7 | ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-EL-005 | 2027-01-18
7 | ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-EL-004 | 2027-03-22
7 | ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-EL-007 | 2027-03-22
7 | ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-EL-006 | 2026-12-07
7 | ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-EL-002 | 2027-01-25
7 | ALP-EPC-00000-EL-STU-0005 | Insulation Coordination Study | NONE | IFR | A | no | 2026-12-07 | 2027-01-04
7 | ALP-EPC-00000-GE-SPC-0002 | Electrical and I&C Installation - Technical Specification | NONE | IFR | A | no | 2026-12-11 | 2027-01-15 | G-PRC-ENQ MR-EL-012 | 2027-09-06
7 | ALP-EPC-00000-GE-RPT-0001 | Piling Works - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-14 | 2027-01-21 | G-PRC-PO MR-CV-001 | 2027-03-22
7 | ALP-EPC-00BBA-EL-SLD-0001 | MV Switchgear 10.5 kV - Single Line Diagram | NONE | IFR | A | no | 2027-01-01 | 2027-02-05 | G-OPS-AB 00000 | 2029-07-18
7 | ALP-EPC-00000-EL-STU-0001 | Load Flow, Short-Circuit and Motor Starting Study | NONE | IFR | A | no | 2027-01-11 | 2027-02-08
7 | ALP-EPC-10HNE-GE-RPT-0001 | Stack 65 m with Silencer - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-02 | 2027-02-09 | G-PRC-PO MR-SS-002 | 2027-03-22
7 | ALP-C01-00000-GE-ITP-0001 | Piling Works - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-01-28 | 2027-02-11
7 | ALP-C01-00000-GE-MOS-0001 | Piling Works - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-01-28 | 2027-02-11
7 | ALP-C01-00000-GE-MOS-0002 | Piling Works - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-01-28 | 2027-02-11
7 | ALP-C01-00000-GE-MOS-0003 | Piling Works - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-01-28 | 2027-02-11
7 | ALP-C01-00000-GE-MOS-0004 | Piling Works - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-01-28 | 2027-02-11
7 | ALP-C01-00000-GE-MOS-0005 | Piling Works - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-01-28 | 2027-02-11
7 | ALP-C01-00000-GE-MOS-0006 | Piling Works - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-01-28 | 2027-02-11
7 | ALP-EPC-10LBA-GE-RPT-0001 | Alloy Piping P91 / P22 - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-04 | 2027-02-11 | G-PRC-PO MR-PI-002 | 2027-02-22
7 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | NONE | IFR | A | no | 2027-01-08 | 2027-02-12 | G-OPS-AB 00000 | 2029-07-18
7 | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | NONE | IFR | A | no | 2027-02-22 | 2027-02-25 | G-PRC-ENQ MR-IC-008 | 2027-04-12
7 | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | NONE | IFR | A | no | 2027-02-22 | 2027-02-25 | G-PRC-ENQ MR-IC-009 | 2027-04-12
7 | ALP-EPC-00UZA-EL-ELY-0001 | Site-Wide Infrastructure - Electrical Layouts | NONE | IFR | A | no | 2027-01-28 | 2027-02-25 | G-CON-CWP CWP-12-EL-01 | 2027-05-17
7 | ALP-EPC-00UPA-EL-ELY-0002 | Marine Works - Electrical Layouts | NONE | IFR | A | no | 2027-01-29 | 2027-02-26 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
7 | ALP-EPC-00UCA-EL-ELY-0001 | Control, Administration and Workshop Buildings - Electrical Layouts | NONE | IFR | A | no | 2027-02-01 | 2027-03-01 | G-CON-CWP CWP-11-EL-01 | 2027-11-08
7 | ALP-EPC-00UBA-EL-ELY-0001 | Electrical Building and Emergency Power - Electrical Layouts | NONE | IFR | A | no | 2027-02-02 | 2027-03-02 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
7 | ALP-S02-10HNE-GE-ITP-0001 | Stack 65 m with Silencer - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-02-23 | 2027-03-16
7 | ALP-S02-10HNE-GE-MOS-0001 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-02-23 | 2027-03-16
7 | ALP-S02-10HNE-GE-MOS-0002 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-02-23 | 2027-03-16
7 | ALP-S02-10HNE-GE-MOS-0003 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-02-23 | 2027-03-16
7 | ALP-S02-10HNE-GE-MOS-0004 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-02-23 | 2027-03-16
7 | ALP-S02-10HNE-GE-MOS-0005 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-02-23 | 2027-03-16
7 | ALP-S02-10HNE-GE-MOS-0006 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-02-23 | 2027-03-16
7 | ALP-EPC-00UAC-HV-GAD-0001 | GIS Building - Building Services | NONE | IFR | A | no | 2027-02-19 | 2027-03-19 | G-CON-CWP CWP-04-CV-01 | 2027-04-05
7 | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | NONE | IFR | A | no | 2027-03-17 | 2027-03-22 | G-PRC-ENQ MR-IC-007 | 2027-05-24
7 | ALP-EPC-00UPC-IC-ELY-0002 | CW Pump House - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-02-22 | 2027-03-22 | G-CON-CWP CWP-05-IC-01 | 2028-02-28
7 | ALP-EPC-00UAC-IC-ELY-0001 | GIS Building - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-02-23 | 2027-03-23 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
7 | ALP-EPC-20UMB-IC-ELY-0002 | Steam Turbine Hall - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-02-23 | 2027-03-23 | G-CON-CWP CWP-02-IC-01 | 2028-03-27
7 | ALP-EPC-00UBA-IC-ELY-0001 | Electrical Building - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-02-24 | 2027-03-24 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
7 | ALP-EPC-00UGA-IC-ELY-0002 | Water Treatment Building and Basins - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-02-25 | 2027-03-25 | G-CON-CWP CWP-07-IC-01 | 2028-03-20
7 | ALP-EPC-00UQA-IC-ELY-0002 | Utility Building - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-02-25 | 2027-03-25 | G-CON-CWP CWP-08-IC-01 | 2028-02-21
7 | ALP-EPC-00USA-IC-ELY-0001 | Workshop and Warehouse - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-02-25 | 2027-03-25 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
7 | ALP-EPC-00UPC-HS-GAD-0001 | CW Pump House - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-02-19 | 2027-03-26 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
7 | ALP-S02-10HNE-CV-CAL-0001 | Stack 65 m with Silencer - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-04 | 2027-03-26
7 | ALP-EPC-00UAC-HS-GAD-0001 | GIS Building - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-02-22 | 2027-03-29 | G-CON-CWP CWP-04-CV-01 | 2027-04-05
7 | ALP-EPC-20UMB-HS-GAD-0001 | Steam Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-02-22 | 2027-03-29 | G-CON-CWP CWP-02-CV-02 | 2027-04-19
7 | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | NONE | IFR | A | no | 2027-03-25 | 2027-03-30 | G-PRC-ENQ MR-ME-010 | 2027-05-10
7 | ALP-EPC-00UBA-HS-GAD-0001 | Electrical Building - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-02-23 | 2027-03-30 | G-CON-CWP CWP-03-CV-01 | 2027-03-29
7 | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | NONE | IFR | A | no | 2027-03-26 | 2027-03-31 | G-PRC-ENQ MR-ME-011 | 2027-04-05
7 | ALP-EPC-00UEK-EL-ELY-0001 | Fuel Gas Station - Electrical Layouts | NONE | IFR | A | no | 2027-03-03 | 2027-03-31 | G-CON-CWP CWP-09-EL-01 | 2027-12-27
7 | ALP-EPC-00UGA-HS-GAD-0001 | Water Treatment Building and Basins - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-02-24 | 2027-03-31 | G-CON-CWP CWP-07-CV-01 | 2027-04-05
7 | ALP-EPC-00USA-HS-GAD-0001 | Workshop and Warehouse - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-02-24 | 2027-03-31 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-10UMA-IC-ELY-0002 | Gas Turbine Hall - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-03-03 | 2027-03-31 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
7 | ALP-S01-00UAC-SS-STL-0001 | GIS Building - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-04-SS-01 | 2027-05-31
7 | ALP-S01-00UBA-SS-STL-0001 | Electrical Building - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-03-SS-01 | 2027-05-24
7 | ALP-S01-00UBF-SS-STL-0001 | Transformer Bays - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-01-SS-01 | 2027-07-12
7 | ALP-S01-00UCA-SS-STL-0001 | Control Building - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
7 | ALP-S01-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-10-CV-01 | 2027-06-03
7 | ALP-S01-00UEK-SS-STL-0001 | Gas Station Structures - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-09-CV-01 | 2027-08-04
7 | ALP-S01-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-07-SS-01 | 2027-06-14
7 | ALP-S01-00UPC-SS-STL-0001 | CW Pump House - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
7 | ALP-S01-00UQA-SS-STL-0001 | Utility Building - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-08-SS-01 | 2027-06-29
7 | ALP-S01-00USA-SS-STL-0001 | Workshop and Warehouse - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
7 | ALP-S01-00UYA-SS-STL-0001 | Administration Building - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
7 | ALP-S01-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Fabrication and Erection Drawings, Part 1 of 2 | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
7 | ALP-S01-00UZD-SS-STL-0002 | Pipe Racks and Pipe Sleepers - Steel Fabrication and Erection Drawings, Part 2 of 2 | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
7 | ALP-S01-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
7 | ALP-S01-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-01-SS-01 | 2027-07-12
7 | ALP-S01-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Fabrication and Erection Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-03-31 | G-CON-CWP CWP-02-SS-01 | 2027-07-12
7 | ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-04-01 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
7 | ALP-EPC-00UQA-HS-GAD-0001 | Utility Building - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-02-25 | 2027-04-01 | G-CON-CWP CWP-08-CV-01 | 2027-05-04
7 | ALP-EPC-00EKA-IC-HMI-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Operator Displays | NONE | IFR | A | no | 2027-03-12 | 2027-04-02
7 | ALP-EPC-00USA-HV-GAD-0001 | Workshop and Warehouse - Building Services | NONE | IFR | A | no | 2027-03-05 | 2027-04-02 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-00EGC-IC-HMI-0001 | LDO Forwarding and Treatment - Operator Displays | NONE | IFR | A | no | 2027-03-15 | 2027-04-05
7 | ALP-EPC-00UCA-IC-ELY-0002 | Control Building - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-03-09 | 2027-04-06 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
7 | ALP-EPC-00USA-CV-RBR-0001 | Workshop and Warehouse - Reinforcement Drawings | NONE | IFR | A | no | 2027-03-16 | 2027-04-06 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-00UYA-CV-RBR-0001 | Administration Building - Reinforcement Drawings | NONE | IFR | A | no | 2027-03-16 | 2027-04-06 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-00UYA-IC-ELY-0001 | Administration Building - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-03-09 | 2027-04-06 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
7 | ALP-EPC-10UMA-EL-ELY-0001 | Power Block - GT and HRSG - Electrical Layouts | NONE | IFR | A | no | 2027-03-09 | 2027-04-06 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
7 | ALP-EPC-10UMA-HS-GAD-0001 | Gas Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-03-02 | 2027-04-06 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
7 | ALP-EPC-00UCA-CV-RBR-0001 | Control Building - Reinforcement Drawings | NONE | IFR | A | no | 2027-03-17 | 2027-04-07 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-00UAC-CV-RBR-0001 | GIS Building - Reinforcement Drawings | NONE | IFR | A | no | 2027-03-18 | 2027-04-08 | G-CON-CWP CWP-04-CV-01 | 2027-04-05
7 | ALP-EPC-00UBA-HV-GAD-0002 | Electrical Building - Building Services | NONE | IFR | A | no | 2027-03-11 | 2027-04-08 | G-CON-CWP CWP-03-CV-01 | 2027-03-29
7 | ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-03-04 | 2027-04-08 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
7 | ALP-P02-10LBA-ME-DSH-0001 | Alloy Piping P91 / P22 - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-03-11 | 2027-04-08
7 | ALP-P02-10LBA-ME-ITP-0001 | Alloy Piping P91 / P22 - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-11 | 2027-04-08
7 | ALP-EPC-00UCA-HS-GAD-0001 | Control Building - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-03-05 | 2027-04-09 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-00UYA-HS-GAD-0001 | Administration Building - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-03-05 | 2027-04-09 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-00UBA-CV-RBR-0001 | Electrical Building - Reinforcement Drawings | NONE | IFR | A | no | 2027-03-22 | 2027-04-12 | G-CON-CWP CWP-03-CV-01 | 2027-03-29
7 | ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-03-09 | 2027-04-13 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
7 | ALP-EPC-00SGY-IC-DSH-0001 | Fire Detection and Alarm: Control System - Datasheet | NONE | IFR | A | no | 2027-03-17 | 2027-04-14
7 | ALP-EPC-00UCA-EL-ELY-0003 | Control Building - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-03-17 | 2027-04-14 | G-CON-CWP CWP-11-EL-01 | 2027-11-08
7 | ALP-EPC-00USA-EL-ELY-0001 | Workshop and Warehouse - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-03-17 | 2027-04-14 | G-CON-CWP CWP-11-EL-01 | 2027-11-08
7 | ALP-EPC-00UYA-EL-ELY-0001 | Administration Building - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-03-17 | 2027-04-14 | G-CON-CWP CWP-11-EL-01 | 2027-11-08
7 | ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-03-10 | 2027-04-14 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
7 | ALP-EPC-00UAC-SS-STL-0001 | GIS Building - Structural Drawings | NONE | IFR | A | no | 2027-03-11 | 2027-04-15 | G-CON-CWP CWP-04-SS-01 | 2027-05-31
7 | ALP-EPC-00UQA-EL-ELY-0001 | BOP Utilities - Electrical Layouts | NONE | IFR | A | no | 2027-03-18 | 2027-04-15 | G-CON-CWP CWP-08-EL-01 | 2028-01-10
7 | ALP-EPC-00SGY-GE-ITP-0001 | Fire Detection and Alarm System - Inspection and Test Plan | NONE | IFR | A | no | 2027-03-19 | 2027-04-16 | G-PRC-PO MR-IC-006 | 2027-07-19
7 | ALP-EPC-00UBA-EL-ELY-0003 | Electrical Building - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-03-19 | 2027-04-16 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
7 | ALP-EPC-00UPC-HV-GAD-0001 | CW Pump House - Building Services | NONE | IFR | A | no | 2027-03-19 | 2027-04-16 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
7 | ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-03-12 | 2027-04-16 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
7 | ALP-EPC-00UZA-EL-ELY-0003 | Roads and Paving - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-03-22 | 2027-04-19 | G-CON-CWP CWP-12-EL-01 | 2027-05-17
7 | ALP-EPC-00EKA-CM-CMP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Commissioning Procedure | NONE | IFR | A | no | 2027-03-16 | 2027-04-20 | G-COM-SC-FF 00EKA | 2028-07-24
7 | ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-03-16 | 2027-04-20 | G-CON-CWP CWP-02-CV-02 | 2027-04-19
7 | ALP-EPC-00PGA-IC-HMI-0001 | Closed Cooling Water - Operator Displays | NONE | IFR | A | no | 2027-03-31 | 2027-04-21
7 | ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure | NONE | IFR | A | no | 2027-03-17 | 2027-04-21 | G-COM-SC-FF 00SGA | 2028-07-24
7 | ALP-EPC-00SGC-CM-CMP-0001 | Deluge, Spray and Foam Systems - System Commissioning Procedure | NONE | IFR | A | no | 2027-03-17 | 2027-04-21 | G-COM-SC-FF 00SGC | 2028-07-24
7 | ALP-EPC-00EGC-CM-CMP-0001 | LDO Forwarding and Treatment - System Commissioning Procedure | NONE | IFR | A | no | 2027-03-18 | 2027-04-22 | G-COM-SC-FF 00EGC | 2028-07-24
7 | ALP-EPC-00UCA-HV-GAD-0002 | Control Building - Building Services | NONE | IFR | A | no | 2027-03-29 | 2027-04-26 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-00UYA-HV-GAD-0001 | Administration Building - Building Services | NONE | IFR | A | no | 2027-03-29 | 2027-04-26 | G-CON-CWP CWP-11-CV-01 | 2027-03-29
7 | ALP-EPC-00UGA-CV-RBR-0001 | Water Treatment Building and Basins - Reinforcement Drawings | NONE | IFR | A | no | 2027-04-06 | 2027-04-27 | G-CON-CWP CWP-07-CV-01 | 2027-04-05
7 | ALP-EPC-00SAA-CM-CMP-0001 | HVAC - System Commissioning Procedure | NONE | IFR | A | no | 2027-03-24 | 2027-04-28 | G-COM-SC-FF 00SAA | 2028-07-24
7 | ALP-EPC-00UAC-EL-ELY-0001 | 380 kV GIS Switchyard - Electrical Layouts | NONE | IFR | A | no | 2027-04-01 | 2027-04-29 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
7 | ALP-EPC-00GBA-IC-HMI-0001 | Seawater Reverse Osmosis - Operator Displays | NONE | IFR | A | no | 2027-04-14 | 2027-05-05
7 | ALP-EPC-00UGA-HV-GAD-0001 | Water Treatment Building and Basins - Building Services | NONE | IFR | A | no | 2027-04-08 | 2027-05-06 | G-CON-CWP CWP-07-CV-01 | 2027-04-05
7 | ALP-EPC-00GMA-IC-HMI-0001 | Process Drains and Waste Water Collection - Operator Displays | NONE | IFR | A | no | 2027-04-16 | 2027-05-07
7 | ALP-EPC-00GNA-IC-HMI-0001 | Waste Water Treatment - Operator Displays | NONE | IFR | A | no | 2027-04-19 | 2027-05-10
7 | ALP-EPC-00PGA-CM-CMP-0001 | Closed Cooling Water - System Commissioning Procedure | NONE | IFR | A | no | 2027-04-05 | 2027-05-10 | G-COM-SC-FF 00PGA | 2028-07-24
7 | ALP-EPC-00PAA-IC-HMI-0001 | CW Intake, Screens and Outfall - Operator Displays | NONE | IFR | A | no | 2027-04-20 | 2027-05-11
7 | ALP-EPC-00UBA-SS-STL-0001 | Electrical Building - Structural Drawings | NONE | IFR | A | no | 2027-04-08 | 2027-05-13 | G-CON-CWP CWP-03-SS-01 | 2027-05-24
7 | ALP-EPC-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Structural Drawings | NONE | IFR | A | no | 2027-04-08 | 2027-05-13 | G-CON-CWP CWP-07-SS-01 | 2027-06-14
7 | ALP-EPC-00PBA-IC-HMI-0001 | Electro-Chlorination - Operator Displays | NONE | IFR | A | no | 2027-04-26 | 2027-05-17
7 | ALP-EPC-00EKA-IC-LOG-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Logic Diagrams | NONE | IFR | A | no | 2027-04-13 | 2027-05-18
7 | ALP-EPC-10UMA-HV-GAD-0002 | Gas Turbine Hall - Building Services | NONE | IFR | A | no | 2027-04-21 | 2027-05-19 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
7 | ALP-EPC-00EGC-IC-LOG-0001 | LDO Forwarding and Treatment - Logic Diagrams | NONE | IFR | A | no | 2027-04-15 | 2027-05-20
7 | ALP-EPC-20UMB-HV-GAD-0001 | Steam Turbine Hall - Building Services | NONE | IFR | A | no | 2027-04-22 | 2027-05-20 | G-CON-CWP CWP-02-CV-02 | 2027-04-19
7 | ALP-EPC-00QCA-IC-HMI-0001 | Chemical Dosing - Operator Displays | NONE | IFR | A | no | 2027-05-03 | 2027-05-24
7 | ALP-EPC-00GBA-CM-CMP-0001 | Seawater Reverse Osmosis - System Commissioning Procedure | NONE | IFR | A | no | 2027-04-20 | 2027-05-25 | G-COM-SC-FF 00GBA | 2028-07-24
7 | ALP-EPC-00GMA-CM-CMP-0001 | Process Drains and Waste Water Collection - System Commissioning Procedure | NONE | IFR | A | no | 2027-04-22 | 2027-05-27 | G-COM-SC-FF 00GMA | 2028-07-24
7 | ALP-EPC-00UQA-CV-RBR-0001 | Utility Building - Reinforcement Drawings | NONE | IFR | A | no | 2027-05-06 | 2027-05-27 | G-CON-CWP CWP-08-CV-01 | 2027-05-04
7 | ALP-EPC-00EGA-IC-HMI-0001 | LDO Unloading - Operator Displays | NONE | IFR | A | no | 2027-05-07 | 2027-05-28
7 | ALP-EPC-00GNA-CM-CMP-0001 | Waste Water Treatment - System Commissioning Procedure | NONE | IFR | A | no | 2027-04-23 | 2027-05-28 | G-COM-SC-FF 00GNA | 2028-07-24
7 | ALP-EPC-00PAA-CM-CMP-0001 | CW Intake, Screens and Outfall - System Commissioning Procedure | NONE | IFR | A | no | 2027-04-23 | 2027-05-28 | G-COM-SC-FF 00PAA | 2028-07-24
7 | ALP-EPC-00PBA-CM-CMP-0001 | Electro-Chlorination - System Commissioning Procedure | NONE | IFR | A | no | 2027-04-23 | 2027-05-28 | G-COM-SC-FF 00PBA | 2028-07-24
7 | ALP-EPC-00QCA-CM-CMP-0001 | Chemical Dosing - System Commissioning Procedure | NONE | IFR | A | no | 2027-04-23 | 2027-05-28 | G-COM-SC-FF 00QCA | 2028-07-24
7 | ALP-EPC-00QEA-CM-CMP-0001 | Compressed Air - System Commissioning Procedure | NONE | IFR | A | no | 2027-04-26 | 2027-05-31 | G-COM-SC-FF 00QEA | 2028-07-24
7 | ALP-EPC-00UQA-HV-GAD-0001 | Utility Building - Building Services | NONE | IFR | A | no | 2027-05-05 | 2027-06-02 | G-CON-CWP CWP-08-CV-01 | 2027-05-04
7 | ALP-EPC-00EGB-IC-HMI-0001 | LDO Storage - Operator Displays | NONE | IFR | A | no | 2027-05-19 | 2027-06-09
7 | ALP-EPC-00UZD-EL-ELY-0001 | Pipe Racks and Pipe Sleepers - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-05-13 | 2027-06-10 | G-CON-CWP CWP-12-EL-01 | 2027-05-17
7 | ALP-EPC-00EKC-IC-HMI-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Operator Displays | NONE | IFR | A | no | 2027-05-24 | 2027-06-14
7 | ALP-EPC-00GCA-IC-HMI-0001 | Demineralisation - Operator Displays | NONE | IFR | A | no | 2027-05-24 | 2027-06-14
7 | ALP-EPC-00UEG-CV-RBR-0001 | LDO Tank Farm Structures - Reinforcement Drawings | NONE | IFR | A | no | 2027-05-24 | 2027-06-14 | G-CON-CWP CWP-10-CV-01 | 2027-06-03
7 | ALP-EPC-00GHA-IC-HMI-0001 | Demineralised Water Storage and Distribution - Operator Displays | NONE | IFR | A | no | 2027-05-25 | 2027-06-15
7 | ALP-EPC-00LBG-IC-HMI-0001 | Auxiliary Steam - Operator Displays | NONE | IFR | A | no | 2027-05-25 | 2027-06-15
7 | ALP-EPC-00LDA-IC-HMI-0001 | Condensate Polishing - Operator Displays | NONE | IFR | A | no | 2027-05-25 | 2027-06-15
7 | ALP-EPC-00USA-SS-STL-0001 | Workshop and Warehouse - Structural Drawings | NONE | IFR | A | no | 2027-05-11 | 2027-06-15 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
7 | ALP-EPC-00PAB-IC-HMI-0001 | CW Piping - Operator Displays | NONE | IFR | A | no | 2027-05-26 | 2027-06-16
7 | ALP-EPC-00UCA-SS-STL-0001 | Control Building - Structural Drawings | NONE | IFR | A | no | 2027-05-12 | 2027-06-16 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
7 | ALP-EPC-00EGA-CM-CMP-0001 | LDO Unloading - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-13 | 2027-06-17 | G-COM-SC-FF 00EGA | 2028-07-24
7 | ALP-EPC-00PAC-IC-HMI-0001 | CW Pumps - Operator Displays | NONE | IFR | A | no | 2027-05-27 | 2027-06-17
7 | ALP-EPC-00QHA-CM-CMP-0001 | Auxiliary Boiler - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-13 | 2027-06-17 | G-COM-SC-FF 00QHA | 2028-07-24
7 | ALP-EPC-00UZD-CV-RBR-0001 | Pipe Racks and Pipe Sleepers - Reinforcement Drawings | NONE | IFR | A | no | 2027-05-27 | 2027-06-17 | G-CON-CWP CWP-12-CV-02 | 2027-03-22
7 | ALP-EPC-00UYA-SS-STL-0001 | Administration Building - Structural Drawings | NONE | IFR | A | no | 2027-05-17 | 2027-06-21 | G-CON-CWP CWP-11-SS-01 | 2027-05-24
7 | ALP-EPC-00PAH-IC-HMI-0001 | Condenser Tube Cleaning - Operator Displays | NONE | IFR | A | no | 2027-06-01 | 2027-06-22
7 | ALP-EPC-00PGA-IC-LOG-0001 | Closed Cooling Water - Logic Diagrams | NONE | IFR | A | no | 2027-05-18 | 2027-06-22
7 | ALP-EPC-00GMA-IC-LOG-0001 | Process Drains and Waste Water Collection - Logic Diagrams | NONE | IFR | A | no | 2027-05-20 | 2027-06-24
7 | ALP-EPC-00QEA-IC-HMI-0001 | Compressed Air - Operator Displays | NONE | IFR | A | no | 2027-06-03 | 2027-06-24
7 | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | NONE | IFR | A | no | 2027-06-04 | 2027-06-25 | G-OPS-AB 00000 | 2029-07-18
7 | ALP-EPC-00EGB-CM-CMP-0001 | LDO Storage - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-25 | 2027-06-29 | G-COM-SC-FF 00EGB | 2028-07-24
7 | ALP-EPC-00PAA-IC-LOG-0001 | CW Intake, Screens and Outfall - Logic Diagrams | NONE | IFR | A | no | 2027-05-27 | 2027-07-01
7 | ALP-EPC-00EKC-CM-CMP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-28 | 2027-07-02 | G-COM-SC-FF 00EKC | 2028-07-24
7 | ALP-EPC-00GCA-CM-CMP-0001 | Demineralisation - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-28 | 2027-07-02 | G-COM-SC-FF 00GCA | 2028-07-24
7 | ALP-EPC-00GHA-CM-CMP-0001 | Demineralised Water Storage and Distribution - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-31 | 2027-07-05 | G-COM-SC-FF 00GHA | 2028-07-24
7 | ALP-EPC-00LDA-CM-CMP-0001 | Condensate Polishing - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-31 | 2027-07-05 | G-COM-SC-FF 00LDA | 2028-07-24
7 | ALP-EPC-00PAB-CM-CMP-0001 | CW Piping - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-31 | 2027-07-05 | G-COM-SC-FF 00PAB | 2028-07-24
7 | ALP-EPC-00PAB-PI-STR-0001 | CW Piping - Pipe Stress Analysis | NONE | IFR | A | no | 2027-06-14 | 2027-07-05
7 | ALP-EPC-00PAC-CM-CMP-0001 | CW Pumps - System Commissioning Procedure | NONE | IFR | A | no | 2027-05-31 | 2027-07-05 | G-COM-SC-FF 00PAC | 2028-07-24
7 | ALP-EPC-00PAH-CM-CMP-0001 | Condenser Tube Cleaning - System Commissioning Procedure | NONE | IFR | A | no | 2027-06-01 | 2027-07-06 | G-COM-SC-FF 00PAH | 2028-07-24
7 | ALP-EPC-00000-GE-RPT-0009 | Painting and Insulation - Technical Bid Evaluation | NONE | IFR | A | no | 2027-06-30 | 2027-07-07 | G-PRC-PO MR-ME-022 | 2028-01-10
7 | ALP-EPC-00QHA-IC-HMI-0001 | Auxiliary Boiler - Operator Displays | NONE | IFR | A | no | 2027-06-23 | 2027-07-14
7 | ALP-EPC-00EGA-IC-LOG-0001 | LDO Unloading - Logic Diagrams | NONE | IFR | A | no | 2027-06-10 | 2027-07-15
7 | ALP-EPC-00SAA-IC-HMI-0001 | HVAC - Operator Displays | NONE | IFR | A | no | 2027-06-24 | 2027-07-15
7 | ALP-EPC-00UEK-CV-RBR-0001 | Gas Station Structures - Reinforcement Drawings | NONE | IFR | A | no | 2027-06-25 | 2027-07-16 | G-CON-CWP CWP-09-CV-01 | 2027-08-04
7 | ALP-EPC-00EKC-IC-LOG-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Logic Diagrams | NONE | IFR | A | no | 2027-06-14 | 2027-07-19
7 | ALP-EPC-00GKA-IC-HMI-0001 | Potable Water - Operator Displays | NONE | IFR | A | no | 2027-06-28 | 2027-07-19
7 | ALP-EPC-00GUA-IC-HMI-0001 | Sanitary Waste Water Treatment - Operator Displays | NONE | IFR | A | no | 2027-06-28 | 2027-07-19
7 | ALP-EPC-00UEK-IC-ELY-0002 | Gas Station Structures - Fire Detection and Alarm Layouts | NONE | IFR | A | no | 2027-06-21 | 2027-07-19 | G-CON-CWP CWP-09-IC-01 | 2028-01-24
7 | ALP-EPC-00LBG-IC-LOG-0001 | Auxiliary Steam - Logic Diagrams | NONE | IFR | A | no | 2027-06-15 | 2027-07-20
7 | ALP-EPC-00QJA-IC-HMI-0001 | Nitrogen Supply - Operator Displays | NONE | IFR | A | no | 2027-06-29 | 2027-07-20
7 | ALP-EPC-00UEK-HV-GAD-0001 | Gas Station Structures - Building Services | NONE | IFR | A | no | 2027-06-22 | 2027-07-20 | G-CON-CWP CWP-09-CV-01 | 2027-08-04
7 | ALP-EPC-00QJA-CM-CMP-0001 | Nitrogen Supply - System Commissioning Procedure | NONE | IFR | A | no | 2027-06-16 | 2027-07-21 | G-COM-SC-FF 00QJA | 2028-07-24
7 | ALP-EPC-00QJB-IC-HMI-0001 | Hydrogen and CO2 Supply - Operator Displays | NONE | IFR | A | no | 2027-06-30 | 2027-07-21
7 | ALP-EPC-00UAC-IC-HUP-0001 | 380 kV GIS Switchyard - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-14 | 2027-07-21 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
7 | ALP-EPC-00UZA-IC-HUP-0001 | Site-Wide Infrastructure - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-14 | 2027-07-21 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
7 | ALP-EPC-00UZF-GE-SPC-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Specification | NONE | IFR | A | no | 2027-06-16 | 2027-07-21 | G-PRC-ENQ MR-ME-024 | 2027-09-20
7 | ALP-EPC-00EGB-IC-LOG-0001 | LDO Storage - Logic Diagrams | NONE | IFR | A | no | 2027-06-17 | 2027-07-22
7 | ALP-EPC-00QJB-CM-CMP-0001 | Hydrogen and CO2 Supply - System Commissioning Procedure | NONE | IFR | A | no | 2027-06-18 | 2027-07-23 | G-COM-SC-FF 00QJB | 2028-07-24
7 | ALP-EPC-00UBA-IC-HUP-0001 | Electrical Building and Emergency Power - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-16 | 2027-07-23 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
7 | ALP-EPC-00UCA-IC-HUP-0001 | Control, Administration and Workshop Buildings - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-16 | 2027-07-23 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
7 | ALP-EPC-00UEG-IC-HUP-0001 | LDO Tank Farm and Unloading - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-16 | 2027-07-23 | G-CON-CWP CWP-10-IC-01 | 2028-02-21
7 | ALP-EPC-00UEK-IC-HUP-0001 | Fuel Gas Station - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-16 | 2027-07-23 | G-CON-CWP CWP-09-IC-01 | 2028-01-24
7 | ALP-EPC-00UPC-IC-HUP-0001 | CW Pump House and Onshore CW - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-16 | 2027-07-23 | G-CON-CWP CWP-05-IC-01 | 2028-02-28
7 | ALP-EPC-20UMB-IC-HUP-0001 | Power Block - ST and Condenser - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-16 | 2027-07-23 | G-CON-CWP CWP-02-IC-01 | 2028-03-27
7 | ALP-EPC-00UEK-HS-GAD-0001 | Gas Station Structures - Fire Fighting, Escape Route and Safety Signage Layouts | NONE | IFR | A | no | 2027-06-21 | 2027-07-26 | G-CON-CWP CWP-09-CV-01 | 2027-08-04
7 | ALP-EPC-00UGA-IC-HUP-0001 | Water Treatment and Effluents - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-07-20 | 2027-07-27 | G-CON-CWP CWP-07-IC-01 | 2028-03-20
7 | ALP-M22-00000-GE-ITP-0001 | Painting and Insulation - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-07-14 | 2027-07-28
7 | ALP-M22-00000-GE-MOS-0001 | Painting and Insulation - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-07-14 | 2027-07-28
7 | ALP-M22-00000-GE-MOS-0002 | Painting and Insulation - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-07-14 | 2027-07-28
7 | ALP-M22-00000-GE-MOS-0003 | Painting and Insulation - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-07-14 | 2027-07-28
7 | ALP-M22-00000-GE-MOS-0004 | Painting and Insulation - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-07-14 | 2027-07-28
7 | ALP-M22-00000-GE-MOS-0005 | Painting and Insulation - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-07-14 | 2027-07-28
7 | ALP-M22-00000-GE-MOS-0006 | Painting and Insulation - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-07-14 | 2027-07-28
7 | ALP-EPC-00GHA-IC-LOG-0001 | Demineralised Water Storage and Distribution - Logic Diagrams | NONE | IFR | A | no | 2027-06-24 | 2027-07-29
7 | ALP-EPC-00PAB-IC-LOG-0001 | CW Piping - Logic Diagrams | NONE | IFR | A | no | 2027-06-25 | 2027-07-30
7 | ALP-EPC-00QUA-CM-CMP-0001 | Sampling and SWAS - System Commissioning Procedure | NONE | IFR | A | no | 2027-06-25 | 2027-07-30 | G-COM-SC-FF 00QUA | 2028-07-24
7 | ALP-EPC-00QUA-IC-HMI-0001 | Sampling and SWAS - Operator Displays | NONE | IFR | A | no | 2027-07-09 | 2027-07-30
7 | ALP-EPC-00EKA-PI-STR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Stress Analysis | NONE | IFR | A | no | 2027-07-13 | 2027-08-03
7 | ALP-EPC-00PAC-IC-LOG-0001 | CW Pumps - Logic Diagrams | NONE | IFR | A | no | 2027-07-01 | 2027-08-05
7 | ALP-EPC-00QCA-IC-LOG-0001 | Chemical Dosing - Logic Diagrams | NONE | IFR | A | no | 2027-07-01 | 2027-08-05
7 | ALP-EPC-00UPA-CV-MOS-0001 | Marine Works Construction Method Statement | NONE | IFR | A | no | 2027-07-16 | 2027-08-06
7 | ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings | NONE | IFR | A | no | 2027-07-02 | 2027-08-06 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
7 | ALP-EPC-00GKA-CM-CMP-0001 | Potable Water - System Commissioning Procedure | NONE | IFR | A | no | 2027-07-05 | 2027-08-09 | G-COM-SC-FF 00GKA | 2028-07-24
7 | ALP-EPC-00GUA-CM-CMP-0001 | Sanitary Waste Water Treatment - System Commissioning Procedure | NONE | IFR | A | no | 2027-07-05 | 2027-08-09 | G-COM-SC-FF 00GUA | 2028-07-24
7 | ALP-EPC-00PAH-IC-LOG-0001 | Condenser Tube Cleaning - Logic Diagrams | NONE | IFR | A | no | 2027-07-05 | 2027-08-09
7 | ALP-EPC-00UEG-EL-ELY-0001 | LDO Tank Farm and Unloading - Electrical Layouts | NONE | IFR | A | no | 2027-07-12 | 2027-08-09 | G-CON-CWP CWP-10-EL-01 | 2028-01-24
7 | ALP-EPC-10HSB-CM-CMP-0001 | Ammonia Storage and Supply - System Commissioning Procedure | NONE | IFR | A | no | 2027-07-05 | 2027-08-09 | G-COM-SC-FF 10HSB | 2028-07-24
7 | ALP-EPC-00UEK-EL-ELY-0003 | Gas Station Structures - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-07-13 | 2027-08-10 | G-CON-CWP CWP-09-EL-01 | 2027-12-27
7 | ALP-EPC-00UPC-EL-ELY-0001 | CW Pump House and Onshore CW - Electrical Layouts | NONE | IFR | A | no | 2027-07-16 | 2027-08-13 | G-CON-CWP CWP-05-EL-01 | 2028-01-31
7 | ALP-EPC-00EGC-PI-STR-0001 | LDO Forwarding and Treatment - Pipe Stress Analysis | NONE | IFR | A | no | 2027-07-26 | 2027-08-16
7 | ALP-EPC-00UQA-IC-HUP-0001 | BOP Utilities - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-08-09 | 2027-08-16 | G-CON-CWP CWP-08-IC-01 | 2028-02-21
7 | ALP-EPC-00EKC-PI-STR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Stress Analysis | NONE | IFR | A | no | 2027-07-27 | 2027-08-17
7 | ALP-EPC-10UMA-IC-HUP-0001 | Power Block - GT and HRSG - Instrument Hook-Up Drawings | NONE | IFR | A | no | 2027-08-10 | 2027-08-17 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
7 | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | NONE | IFR | A | no | 2027-07-21 | 2027-08-18
7 | ALP-EPC-00GKA-IC-LOG-0001 | Potable Water - Logic Diagrams | NONE | IFR | A | no | 2027-07-16 | 2027-08-20
7 | ALP-EPC-00QJB-IC-LOG-0001 | Hydrogen and CO2 Supply - Logic Diagrams | NONE | IFR | A | no | 2027-07-19 | 2027-08-23
7 | ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | NONE | IFR | A | no | 2027-07-20 | 2027-08-24
7 | ALP-EPC-00UPA-CV-RBR-0001 | CW Intake and Outfall Marine Structures - Reinforcement Drawings | NONE | IFR | A | no | 2027-08-03 | 2027-08-24 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
7 | ALP-EPC-10LBA-PI-STR-0001 | Main Steam Piping - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-03 | 2027-08-24
7 | ALP-EPC-00UAC-IC-ELY-0002 | 380 kV GIS Switchyard - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-07-28 | 2027-08-25 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
7 | ALP-EPC-00UZA-IC-ELY-0001 | Site-Wide Infrastructure - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-07-28 | 2027-08-25 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
7 | ALP-EPC-10LBB-PI-STR-0001 | Hot Reheat Piping - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-05 | 2027-08-26
7 | ALP-EPC-00UAC-EL-ELY-0003 | GIS Building - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-08-02 | 2027-08-30 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
7 | ALP-EPC-00UCA-IC-ELY-0001 | Control, Administration and Workshop Buildings - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-02 | 2027-08-30 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
7 | ALP-EPC-00UEG-IC-ELY-0001 | LDO Tank Farm and Unloading - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-02 | 2027-08-30 | G-CON-CWP CWP-10-IC-01 | 2028-02-21
7 | ALP-EPC-00UEK-IC-ELY-0001 | Fuel Gas Station - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-02 | 2027-08-30 | G-CON-CWP CWP-09-IC-01 | 2028-01-24
7 | ALP-EPC-00UPC-IC-ELY-0001 | CW Pump House and Onshore CW - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-02 | 2027-08-30 | G-CON-CWP CWP-05-IC-01 | 2028-02-28
7 | ALP-EPC-20UMB-IC-ELY-0001 | Power Block - ST and Condenser - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-02 | 2027-08-30 | G-CON-CWP CWP-02-IC-01 | 2028-03-27
7 | ALP-EPC-00UBA-IC-ELY-0002 | Electrical Building and Emergency Power - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-03 | 2027-08-31 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
7 | ALP-EPC-00UGA-IC-ELY-0001 | Water Treatment and Effluents - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-04 | 2027-09-01 | G-CON-CWP CWP-07-IC-01 | 2028-03-20
7 | ALP-EPC-00000-HS-RPT-0004 | HAZOP Close-Out Report | NONE | IFR | A | no | 2027-08-12 | 2027-09-02
7 | ALP-EPC-10HAN-PI-STR-0001 | HRSG Blowdown and Drains - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-13 | 2027-09-03
7 | ALP-EPC-10LBC-PI-STR-0001 | Cold Reheat Piping - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-13 | 2027-09-03
7 | ALP-EPC-00UPA-EL-ELY-0001 | CW Intake and Outfall Marine Structures - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-08-09 | 2027-09-06 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
7 | ALP-EPC-10LBD-PI-STR-0001 | LP Steam Piping - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-17 | 2027-09-07
7 | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | NONE | IFR | A | no | 2027-08-04 | 2027-09-08
7 | ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-18 | 2027-09-08
7 | ALP-EPC-10UMA-IC-ELY-0001 | Power Block - GT and HRSG - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-11 | 2027-09-08 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
7 | ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-19 | 2027-09-09
7 | ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-19 | 2027-09-09
7 | ALP-EPC-00SAA-PI-ISO-0001 | HVAC - Isometric Drawings | NONE | IFR | A | no | 2027-09-02 | 2027-09-09 | G-CON-CWP CWP-03-HV-01 | 2027-10-11
7 | ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-19 | 2027-09-09
7 | ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-20 | 2027-09-10
7 | ALP-EPC-00UQA-IC-ELY-0001 | BOP Utilities - Instrument Location and I&C Cable Routing | NONE | IFR | A | no | 2027-08-16 | 2027-09-13 | G-CON-CWP CWP-08-IC-01 | 2028-02-21
7 | ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | NONE | IFR | A | no | 2027-08-23 | 2027-09-13
7 | ALP-EPC-00UGA-EL-ELY-0001 | Water Treatment and Effluents - Electrical Layouts | NONE | IFR | A | no | 2027-08-20 | 2027-09-17 | G-CON-CWP CWP-07-EL-01 | 2028-02-21
7 | ALP-EPC-00000-HS-HAZ-0010 | Major Accident Assessment and QRA | NONE | IFR | A | no | 2027-08-17 | 2027-09-21
7 | ALP-EPC-00000-GE-RPT-0010 | Mechanical and Piping Erection - Technical Bid Evaluation | NONE | IFR | A | no | 2027-09-15 | 2027-09-22 | G-PRC-PO MR-ME-023 | 2027-11-15
7 | ALP-EPC-00UQA-EL-ELY-0003 | Utility Building - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-08-26 | 2027-09-23 | G-CON-CWP CWP-08-EL-01 | 2028-01-10
7 | ALP-EPC-00UEG-EL-ELY-0003 | LDO Tank Farm Structures - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-08-30 | 2027-09-27 | G-CON-CWP CWP-10-EL-01 | 2028-01-24
7 | ALP-EPC-20UMB-EL-ELY-0001 | Power Block - ST and Condenser - Electrical Layouts | NONE | IFR | A | no | 2027-08-30 | 2027-09-27 | G-CON-CWP CWP-02-EL-01 | 2028-02-28
7 | ALP-EPC-00LBG-CM-CMP-0001 | Auxiliary Steam - System Commissioning Procedure | NONE | IFR | A | no | 2027-08-24 | 2027-09-28 | G-COM-SC-WS 00LBG | 2028-09-25
7 | ALP-EPC-10HAN-CM-CMP-0001 | HRSG Blowdown and Drains - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-01 | 2027-10-06 | G-COM-SC-WS 10HAN | 2028-09-25
7 | ALP-EPC-10LAB-CM-CMP-0001 | Feedwater Piping - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-01 | 2027-10-06 | G-COM-SC-WS 10LAB | 2028-09-25
7 | ALP-EPC-00QJA-IC-LOG-0001 | Nitrogen Supply - Logic Diagrams | NONE | IFR | A | no | 2027-09-02 | 2027-10-07
7 | ALP-EPC-10LAC-CM-CMP-0001 | Boiler Feed Pumps - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-03 | 2027-10-08 | G-COM-SC-WS 10LAC | 2028-09-25
7 | ALP-EPC-10LAE-CM-CMP-0001 | HP Attemperation Spray Water - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-03 | 2027-10-08 | G-COM-SC-WS 10LAE | 2028-09-25
7 | ALP-EPC-10LAF-CM-CMP-0001 | Reheat Attemperation Spray Water - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-03 | 2027-10-08 | G-COM-SC-WS 10LAF | 2028-09-25
7 | ALP-EPC-00UGA-EL-ELY-0003 | Water Treatment Building and Basins - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-09-13 | 2027-10-11 | G-CON-CWP CWP-07-EL-01 | 2028-02-21
7 | ALP-M23-00000-GE-ITP-0001 | Mechanical and Piping Erection - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-09-29 | 2027-10-13
7 | ALP-M23-00000-GE-MOS-0001 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-09-29 | 2027-10-13
7 | ALP-M23-00000-GE-MOS-0002 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-09-29 | 2027-10-13
7 | ALP-M23-00000-GE-MOS-0003 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-09-29 | 2027-10-13
7 | ALP-M23-00000-GE-MOS-0004 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-09-29 | 2027-10-13
7 | ALP-M23-00000-GE-MOS-0005 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-09-29 | 2027-10-13
7 | ALP-M23-00000-GE-MOS-0006 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-09-29 | 2027-10-13
7 | ALP-EPC-00SGA-IC-HMI-0001 | Fire Water System - Operator Displays | NONE | IFR | A | no | 2027-09-23 | 2027-10-14
7 | ALP-EPC-10LBA-CM-CMP-0001 | Main Steam Piping - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-13 | 2027-10-18 | G-COM-SC-WS 10LBA | 2028-09-25
7 | ALP-EPC-10LBB-CM-CMP-0001 | Hot Reheat Piping - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-14 | 2027-10-19 | G-COM-SC-WS 10LBB | 2028-09-25
7 | ALP-EPC-10LBC-CM-CMP-0001 | Cold Reheat Piping - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-14 | 2027-10-19 | G-COM-SC-WS 10LBC | 2028-09-25
7 | ALP-EPC-10LBD-CM-CMP-0001 | LP Steam Piping - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-16 | 2027-10-21 | G-COM-SC-WS 10LBD | 2028-09-25
7 | ALP-EPC-20LCA-CM-CMP-0001 | Main Condensate Piping - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-16 | 2027-10-21 | G-COM-SC-WS 20LCA | 2028-09-25
7 | ALP-EPC-20LCB-CM-CMP-0001 | Condensate Extraction Pumps - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-21 | 2027-10-26 | G-COM-SC-WS 20LCB | 2028-09-25
7 | ALP-EPC-00000-EL-STU-0006 | Grid Code Compliance and Reactive Capability Study | NONE | IFR | A | no | 2027-09-29 | 2027-10-27
7 | ALP-EPC-00000-EL-SPC-0003 | Revenue Metering and TSO SCADA Interface Specification | NONE | IFR | A | no | 2027-09-24 | 2027-10-29
7 | ALP-EPC-00SAA-IC-LOG-0001 | HVAC - Logic Diagrams, Part 1 of 2 | NONE | IFR | A | no | 2027-09-24 | 2027-10-29
7 | ALP-EPC-00QUA-IC-LOG-0001 | Sampling and SWAS - Logic Diagrams | NONE | IFR | A | no | 2027-09-27 | 2027-11-01
7 | ALP-EPC-20MAN-CM-CMP-0001 | Turbine Bypass Stations and Piping - System Commissioning Procedure | NONE | IFR | A | no | 2027-09-29 | 2027-11-03 | G-COM-SC-WS 20MAN | 2028-09-25
7 | ALP-EPC-00SGC-IC-HMI-0001 | Deluge, Spray and Foam Systems - Operator Displays | NONE | IFR | A | no | 2027-10-15 | 2027-11-05
7 | ALP-EPC-10HAN-IC-HMI-0001 | HRSG Blowdown and Drains - Operator Displays | NONE | IFR | A | no | 2027-10-15 | 2027-11-05
7 | ALP-EPC-10HSB-IC-HMI-0001 | Ammonia Storage and Supply - Operator Displays | NONE | IFR | A | no | 2027-10-18 | 2027-11-08
7 | ALP-EPC-10LAB-IC-HMI-0001 | Feedwater Piping - Operator Displays | NONE | IFR | A | no | 2027-10-18 | 2027-11-08
7 | ALP-EPC-10LAC-IC-HMI-0001 | Boiler Feed Pumps - Operator Displays | NONE | IFR | A | no | 2027-10-21 | 2027-11-11
7 | ALP-EPC-00SAA-IC-LOG-0002 | HVAC - Logic Diagrams, Part 2 of 2 | NONE | IFR | A | no | 2027-10-08 | 2027-11-12
7 | ALP-EPC-10LAE-IC-HMI-0001 | HP Attemperation Spray Water - Operator Displays | NONE | IFR | A | no | 2027-10-22 | 2027-11-12
7 | ALP-EPC-10LAE-PI-STR-0001 | HP Attemperation Spray Water - Pipe Stress Analysis | NONE | IFR | A | no | 2027-10-29 | 2027-11-19
7 | ALP-EPC-10LAF-IC-HMI-0001 | Reheat Attemperation Spray Water - Operator Displays | NONE | IFR | A | no | 2027-10-29 | 2027-11-19
7 | ALP-EPC-10LBA-IC-HMI-0001 | Main Steam Piping - Operator Displays | NONE | IFR | A | no | 2027-10-29 | 2027-11-19
7 | ALP-EPC-10LBB-IC-HMI-0001 | Hot Reheat Piping - Operator Displays | NONE | IFR | A | no | 2027-11-02 | 2027-11-23
7 | ALP-EPC-10LBC-IC-HMI-0001 | Cold Reheat Piping - Operator Displays | NONE | IFR | A | no | 2027-11-03 | 2027-11-24
7 | ALP-EPC-10LBD-IC-HMI-0001 | LP Steam Piping - Operator Displays | NONE | IFR | A | no | 2027-11-08 | 2027-11-29
7 | ALP-EPC-10LAF-PI-STR-0001 | Reheat Attemperation Spray Water - Pipe Stress Analysis | NONE | IFR | A | no | 2027-11-09 | 2027-11-30
7 | ALP-EPC-00ACA-EL-SLD-0001 | 380 kV GIS Switchyard - Single Line Diagram | NONE | IFR | A | no | 2027-10-29 | 2027-12-03 | G-OPS-AB 00000 | 2029-07-18
7 | ALP-EPC-20LCA-IC-HMI-0001 | Main Condensate Piping - Operator Displays | NONE | IFR | A | no | 2027-11-12 | 2027-12-03
7 | ALP-EPC-00BLA-EL-SLD-0001 | Lighting and Small Power - Single Line Diagram | NONE | IFR | A | no | 2027-11-01 | 2027-12-06 | G-OPS-AB 00000 | 2029-07-18
7 | ALP-EPC-00SGA-IC-LOG-0001 | Fire Water System - Logic Diagrams | NONE | IFR | A | no | 2027-11-02 | 2027-12-07
7 | ALP-EPC-20LCB-IC-HMI-0001 | Condensate Extraction Pumps - Operator Displays | NONE | IFR | A | no | 2027-11-16 | 2027-12-07
7 | ALP-EPC-10HAN-IC-LOG-0001 | HRSG Blowdown and Drains - Logic Diagrams | NONE | IFR | A | no | 2027-11-08 | 2027-12-13
7 | ALP-EPC-00BMA-EL-SLD-0001 | Emergency LV Switchgear - Single Line Diagram | NONE | IFR | A | no | 2027-11-09 | 2027-12-14 | G-OPS-AB 00000 | 2029-07-18
7 | ALP-EPC-10LAE-IC-LOG-0001 | HP Attemperation Spray Water - Logic Diagrams | NONE | IFR | A | no | 2027-11-09 | 2027-12-14
7 | ALP-EPC-20MAN-IC-HMI-0001 | Turbine Bypass Stations and Piping - Operator Displays | NONE | IFR | A | no | 2027-11-23 | 2027-12-14
7 | ALP-EPC-00BRA-EL-SLD-0001 | UPS - Single Line Diagram | NONE | IFR | A | no | 2027-11-10 | 2027-12-15 | G-OPS-AB 00000 | 2029-07-18
7 | ALP-EPC-10LAF-IC-LOG-0001 | Reheat Attemperation Spray Water - Logic Diagrams | NONE | IFR | A | no | 2027-11-10 | 2027-12-15
7 | ALP-EPC-10LAB-IC-LOG-0001 | Feedwater Piping - Logic Diagrams | NONE | IFR | A | no | 2027-11-11 | 2027-12-16
7 | ALP-EPC-10LBA-IC-LOG-0001 | Main Steam Piping - Logic Diagrams | NONE | IFR | A | no | 2027-11-16 | 2027-12-21
7 | ALP-EPC-00SGC-IC-LOG-0001 | Deluge, Spray and Foam Systems - Logic Diagrams | NONE | IFR | A | no | 2027-11-17 | 2027-12-22
7 | ALP-EPC-10LBB-IC-LOG-0001 | Hot Reheat Piping - Logic Diagrams | NONE | IFR | A | no | 2027-11-18 | 2027-12-23
7 | ALP-EPC-10HSB-IC-LOG-0001 | Ammonia Storage and Supply - Logic Diagrams | NONE | IFR | A | no | 2027-11-19 | 2027-12-24
7 | ALP-EPC-10LBC-IC-LOG-0001 | Cold Reheat Piping - Logic Diagrams | NONE | IFR | A | no | 2027-11-19 | 2027-12-24
7 | ALP-EPC-10LBD-IC-LOG-0001 | LP Steam Piping - Logic Diagrams | NONE | IFR | A | no | 2027-11-22 | 2027-12-27
7 | ALP-EPC-10LAC-IC-LOG-0001 | Boiler Feed Pumps - Logic Diagrams | NONE | IFR | A | no | 2027-11-25 | 2027-12-30
7 | ALP-P02-10LBA-ME-MDB-0001 | Alloy Piping P91 / P22 - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-11-04 | 2027-12-30 | G-PRC-SHP MR-PI-002 | 2027-11-18
7 | ALP-EPC-20LCA-IC-LOG-0001 | Main Condensate Piping - Logic Diagrams | NONE | IFR | A | no | 2027-12-09 | 2028-01-13
7 | ALP-EPC-20MAN-IC-LOG-0001 | Turbine Bypass Stations and Piping - Logic Diagrams | NONE | IFR | A | no | 2027-12-14 | 2028-01-18
7 | ALP-EPC-20MAN-PI-STR-0001 | Turbine Bypass Stations and Piping - Pipe Stress Analysis | NONE | IFR | A | no | 2027-12-31 | 2028-01-21
7 | ALP-EPC-20LCB-PI-STR-0001 | Condensate Extraction Pumps - Pipe Stress Analysis | NONE | IFR | A | no | 2028-01-05 | 2028-01-26
7 | ALP-EPC-20LCA-PI-STR-0001 | Main Condensate Piping - Pipe Stress Analysis | NONE | IFR | A | no | 2028-01-06 | 2028-01-27
7 | ALP-EPC-20LCB-IC-LOG-0001 | Condensate Extraction Pumps - Logic Diagrams | NONE | IFR | A | no | 2027-12-23 | 2028-01-27
7 | ALP-EPC-00000-CM-TRP-0001 | Steam Blowing and Chemical Cleaning Report | NONE | IFR | A | no | 2028-09-25 | 2028-10-16 | G-OWN-TO 00000 | 2029-04-18
7 | ALP-EPC-00000-CM-TRP-0005 | Tests on LDO Report | NONE | IFR | A | no | 2029-03-05 | 2029-03-26 | G-OWN-TO 00000 | 2029-04-18
7 | ALP-EPC-00000-CM-TRP-0006 | Emission Test and Noise Survey Reports | NONE | IFR | A | no | 2029-04-03 | 2029-04-24 | G-OWN-TO 00000 | 2029-04-18
8 | ALP-EPC-00000-GE-SPC-0001 | Construction Power Supply - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-11-16 | G-PRC-ENQ MR-EL-011 | 2026-11-09
8 | ALP-EPC-00BBA-EL-DSH-0001 | MV Switchgear 10.5 kV - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-00BFA-EL-DSH-0001 | LV Switchgear 0.4 kV - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-00BFT-EL-DSH-0001 | LV Transformers - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-00BMA-EL-DSH-0001 | Emergency LV Switchgear - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-00BTA-EL-DSH-0001 | Batteries and DC 220 V: Battery - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-00XJA-EL-DSH-0001 | Emergency Diesel Generator - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-10BBT-EL-DSH-0001 | GT Unit Auxiliary Transformer - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-20BBT-EL-DSH-0001 | ST Unit Auxiliary Transformer - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
8 | ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-EL-001 | 2026-12-15
8 | ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification | NONE | IFR | A | no | 2026-11-02 | 2026-12-07 | G-PRC-ENQ MR-IC-001 | 2026-11-30
8 | ALP-EPC-00BBA-EL-ITP-0001 | MV Switchgear 10.5 kV - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-EL-003 | 2027-02-15
8 | ALP-EPC-00BRA-EL-DSH-0002 | UPS: Switchgear - Datasheet | NONE | IFR | A | no | 2026-11-16 | 2026-12-14
8 | ALP-EPC-00XJA-EL-ITP-0001 | Emergency Diesel Generator - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-EL-006 | 2027-02-15
8 | ALP-EPC-00BFA-EL-ITP-0001 | LV Switchboards and MCCs - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-23 | 2026-12-21 | G-PRC-PO MR-EL-005 | 2027-03-29
8 | ALP-EPC-10BBT-EL-ITP-0001 | Unit Auxiliary Transformers - Inspection and Test Plan | NONE | IFR | A | no | 2026-12-02 | 2026-12-30 | G-PRC-PO MR-EL-002 | 2027-04-05
8 | ALP-EPC-00BFT-EL-ITP-0001 | LV Transformers - Inspection and Test Plan | NONE | IFR | A | no | 2026-12-10 | 2027-01-07 | G-PRC-PO MR-EL-004 | 2027-05-10
8 | ALP-EPC-00BRA-EL-ITP-0001 | UPS, Batteries and DC Systems - Inspection and Test Plan | NONE | IFR | A | no | 2026-12-16 | 2027-01-13 | G-PRC-PO MR-EL-007 | 2027-05-10
8 | ALP-EPC-00EGA-GE-RPT-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-07 | 2027-01-14 | G-PRC-PO MR-ME-016 | 2027-01-25
8 | ALP-EPC-00EKA-GE-RPT-0001 | Gas Receiving and Metering Station - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-07 | 2027-01-14 | G-PRC-PO MR-ME-015 | 2027-01-25
8 | ALP-EPC-00PAC-GE-RPT-0001 | CW Pumps - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-07 | 2027-01-14 | G-PRC-PO MR-ME-003 | 2027-02-01
8 | ALP-EPC-00QHA-GE-RPT-0001 | Auxiliary Boiler - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-07 | 2027-01-14 | G-PRC-PO MR-ME-009 | 2027-01-25
8 | ALP-EPC-00SMA-GE-RPT-0001 | EOT Cranes - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-07 | 2027-01-14 | G-PRC-PO MR-ME-021 | 2027-02-08
8 | ALP-EPC-10LAC-GE-RPT-0001 | Boiler Feed Pumps - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-07 | 2027-01-14 | G-PRC-PO MR-ME-001 | 2027-01-25
8 | ALP-EPC-00PAB-GE-RPT-0001 | GRP CW Pipes and Fittings - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-13 | 2027-01-20 | G-PRC-PO MR-PI-004 | 2027-02-22
8 | ALP-EPC-00GBA-GE-RPT-0001 | Water Treatment Package - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-14 | 2027-01-21 | G-PRC-PO MR-ME-012 | 2027-02-08
8 | ALP-EPC-00GHA-GE-RPT-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-22 | 2027-01-29 | G-PRC-PO MR-ME-013 | 2027-05-17
8 | ALP-EPC-00GNA-GE-RPT-0001 | Waste Water and Sanitary Treatment Packages - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-28 | 2027-02-04 | G-PRC-PO MR-ME-014 | 2027-05-31
8 | ALP-EPC-00SAA-GE-RPT-0001 | HVAC Plant and Equipment - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-28 | 2027-02-04 | G-PRC-PO MR-HV-001 | 2027-03-15
8 | ALP-EPC-00SGA-GE-RPT-0001 | Fire Pumps and Fire Protection Systems - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-28 | 2027-02-04 | G-PRC-PO MR-ME-020 | 2027-03-22
8 | ALP-EPC-00PAA-GE-RPT-0001 | Travelling Band Screens and Trash Rakes - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-12 | 2027-02-19 | G-PRC-PO MR-ME-004 | 2027-04-12
8 | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | NONE | IFR | A | no | 2027-02-01 | 2027-02-22
8 | ALP-EPC-00PBA-GE-RPT-0001 | Electro-Chlorination Package - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-15 | 2027-02-22 | G-PRC-PO MR-ME-005 | 2027-04-12
8 | ALP-EPC-00XJA-ME-DSH-0001 | Emergency Diesel Generator: Tank - Datasheet | NONE | IFR | A | no | 2027-01-25 | 2027-02-22
8 | ALP-EPC-10HAN-GE-RPT-0001 | HRSG Blowdown and Drain Tanks - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-15 | 2027-02-22 | G-PRC-PO MR-ME-019 | 2027-05-03
8 | ALP-P04-00PAB-ME-DSH-0001 | GRP CW Pipes and Fittings - Supplier Catalogues and Material Datasheets | NONE | IFR | A | no | 2027-02-03 | 2027-02-24
8 | ALP-P04-00PAB-ME-ITP-0001 | GRP CW Pipes and Fittings - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-03 | 2027-02-24
8 | ALP-EPC-00PGA-GE-RPT-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-18 | 2027-02-25 | G-PRC-PO MR-ME-007 | 2027-04-05
8 | ALP-EPC-00QEA-GE-RPT-0001 | Air Compressors and Dryers - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-18 | 2027-02-25 | G-PRC-PO MR-ME-008 | 2027-04-05
8 | ALP-EPC-10HSB-GE-RPT-0001 | Aqueous Ammonia Storage and Forwarding - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-22 | 2027-03-01 | G-PRC-PO MR-ME-018 | 2027-04-05
8 | ALP-EPC-20LCB-GE-RPT-0001 | Condensate Extraction Pumps - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-22 | 2027-03-01 | G-PRC-PO MR-ME-002 | 2027-04-12
8 | ALP-M13-00GHA-ME-ITP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-10 | 2027-03-01 | G-PRC-FAB MR-ME-013 | 2027-07-28
8 | ALP-M16-00EGA-ME-ITP-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-09 | 2027-03-05 | G-PRC-FAB MR-ME-016 | 2027-05-05
8 | ALP-M21-00SMA-ME-ITP-0001 | EOT Cranes - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-09 | 2027-03-05 | G-PRC-FAB MR-ME-021 | 2027-05-19
8 | ALP-M13-00GHA-CV-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-02-19 | 2027-03-09 | G-PRC-FAB MR-ME-013 | 2027-07-28
8 | ALP-M13-00GHA-ME-DSH-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-10 | 2027-03-09 | G-PRC-FAB MR-ME-013 | 2027-07-28
8 | ALP-H01-00SAA-ME-ITP-0001 | HVAC Plant and Equipment - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-18 | 2027-03-11 | G-PRC-FAB MR-HV-001 | 2027-06-07
8 | ALP-M01-10LAC-ME-ITP-0001 | Boiler Feed Pumps - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-11 | 2027-03-11 | G-PRC-FAB MR-ME-001 | 2027-05-17
8 | ALP-M03-00PAC-ME-ITP-0001 | CW Pumps - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-11 | 2027-03-11 | G-PRC-FAB MR-ME-003 | 2027-06-03
8 | ALP-M09-00QHA-ME-ITP-0001 | Auxiliary Boiler - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-11 | 2027-03-11 | G-PRC-FAB MR-ME-009 | 2027-05-17
8 | ALP-M14-00GNA-ME-ITP-0001 | Waste Water and Sanitary Treatment Packages - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-18 | 2027-03-11 | G-PRC-FAB MR-ME-014 | 2027-08-23
8 | ALP-M15-00EKA-ME-ITP-0001 | Gas Receiving and Metering Station - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-11 | 2027-03-11 | G-PRC-FAB MR-ME-015 | 2027-05-17
8 | ALP-EPC-00000-EL-STU-0002 | Protection Coordination Study and Relay Settings | NONE | IFR | A | no | 2027-02-15 | 2027-03-15
8 | ALP-M20-00SGA-ME-ITP-0001 | Fire Pumps and Fire Protection Systems - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-19 | 2027-03-15 | G-PRC-FAB MR-ME-020 | 2027-06-18
8 | ALP-M13-00GHA-ME-GAD-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-19 | 2027-03-18 | G-PRC-FAB MR-ME-013 | 2027-07-28
8 | ALP-M16-00EGA-CV-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-02-22 | 2027-03-18 | G-PRC-FAB MR-ME-016 | 2027-05-05
8 | ALP-M16-00EGA-ME-DSH-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-09 | 2027-03-18 | G-PRC-FAB MR-ME-016 | 2027-05-05
8 | ALP-M21-00SMA-CV-CAL-0001 | EOT Cranes - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-02-22 | 2027-03-18 | G-PRC-FAB MR-ME-021 | 2027-05-19
8 | ALP-M21-00SMA-ME-DSH-0001 | EOT Cranes - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-09 | 2027-03-18 | G-PRC-FAB MR-ME-021 | 2027-05-19
8 | ALP-H01-00SAA-ME-DSH-0001 | HVAC Plant and Equipment - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-18 | 2027-03-23 | G-PRC-FAB MR-HV-001 | 2027-06-07
8 | ALP-M14-00GNA-CV-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-01 | 2027-03-23 | G-PRC-FAB MR-ME-014 | 2027-08-23
8 | ALP-M14-00GNA-ME-DSH-0001 | Waste Water and Sanitary Treatment Packages - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-18 | 2027-03-23 | G-PRC-FAB MR-ME-014 | 2027-08-23
8 | ALP-M19-10HAN-ME-ITP-0001 | HRSG Blowdown and Drain Tanks - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-04 | 2027-03-23 | G-PRC-FAB MR-ME-019 | 2027-07-14
8 | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | NONE | IFR | A | no | 2027-03-19 | 2027-03-24 | G-PRC-ENQ MR-EL-012 | 2027-09-06
8 | ALP-EPC-00PAH-GE-RPT-0001 | Condenser Tube Cleaning System - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-17 | 2027-03-24 | G-PRC-PO MR-ME-006 | 2027-07-05
8 | ALP-M01-10LAC-CV-CAL-0001 | Boiler Feed Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-03-25 | G-PRC-FAB MR-ME-001 | 2027-05-17
8 | ALP-M01-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-11 | 2027-03-25 | G-PRC-FAB MR-ME-001 | 2027-05-17
8 | ALP-M03-00PAC-CV-CAL-0001 | CW Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-03-25 | G-PRC-FAB MR-ME-003 | 2027-06-03
8 | ALP-M03-00PAC-ME-DSH-0001 | CW Pumps - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-11 | 2027-03-25 | G-PRC-FAB MR-ME-003 | 2027-06-03
8 | ALP-M09-00QHA-CV-CAL-0001 | Auxiliary Boiler - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-03-25 | G-PRC-FAB MR-ME-009 | 2027-05-17
8 | ALP-M09-00QHA-ME-DSH-0001 | Auxiliary Boiler - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-11 | 2027-03-25 | G-PRC-FAB MR-ME-009 | 2027-05-17
8 | ALP-M12-00GBA-ME-ITP-0001 | Water Treatment Package - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-25 | 2027-03-25 | G-PRC-FAB MR-ME-012 | 2027-06-10
8 | ALP-M15-00EKA-CV-CAL-0001 | Gas Receiving and Metering Station - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-03-25 | G-PRC-FAB MR-ME-015 | 2027-05-17
8 | ALP-M15-00EKA-ME-DSH-0001 | Gas Receiving and Metering Station - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-11 | 2027-03-25 | G-PRC-FAB MR-ME-015 | 2027-05-17
8 | ALP-M20-00SGA-CV-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-03 | 2027-03-25 | G-PRC-FAB MR-ME-020 | 2027-06-18
8 | ALP-M20-00SGA-ME-DSH-0001 | Fire Pumps and Fire Protection Systems - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-19 | 2027-03-25 | G-PRC-FAB MR-ME-020 | 2027-06-18
8 | ALP-EPC-00CQA-GE-RPT-0001 | Continuous Emission Monitoring System - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-19 | 2027-03-26 | G-PRC-PO MR-IC-002 | 2027-07-12
8 | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | NONE | IFR | A | no | 2027-03-24 | 2027-03-29 | G-PRC-ENQ MR-IC-006 | 2027-05-24
8 | ALP-M13-00GHA-IC-IOL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-01 | 2027-03-29
8 | ALP-M13-00GHA-ME-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-01 | 2027-03-29 | G-PRC-FAB MR-ME-013 | 2027-07-28
8 | ALP-M13-00GHA-PR-PID-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier P&IDs | NONE | IFR | A | no | 2027-03-01 | 2027-03-29 | G-PRC-FAB MR-ME-013 | 2027-07-28
8 | ALP-EPC-00QUA-GE-RPT-0001 | Steam/Water Analysis System - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-23 | 2027-03-30 | G-PRC-PO MR-IC-003 | 2027-07-12
8 | ALP-M16-00EGA-ME-GAD-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-22 | 2027-03-31 | G-PRC-FAB MR-ME-016 | 2027-05-05
8 | ALP-M19-10HAN-CV-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-15 | 2027-03-31 | G-PRC-FAB MR-ME-019 | 2027-07-14
8 | ALP-M19-10HAN-ME-DSH-0001 | HRSG Blowdown and Drain Tanks - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-04 | 2027-03-31 | G-PRC-FAB MR-ME-019 | 2027-07-14
8 | ALP-M21-00SMA-ME-GAD-0001 | EOT Cranes - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-22 | 2027-03-31 | G-PRC-FAB MR-ME-021 | 2027-05-19
8 | ALP-EPC-00EGB-GE-RPT-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-25 | 2027-04-01 | G-PRC-PO MR-ME-017 | 2027-07-26
8 | ALP-H01-00SAA-ME-GAD-0001 | HVAC Plant and Equipment - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-01 | 2027-04-01 | G-PRC-FAB MR-HV-001 | 2027-06-07
8 | ALP-M07-00PGA-ME-ITP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-11 | 2027-04-01 | G-PRC-FAB MR-ME-007 | 2027-06-28
8 | ALP-M08-00QEA-ME-ITP-0001 | Air Compressors and Dryers - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-11 | 2027-04-01 | G-PRC-FAB MR-ME-008 | 2027-06-28
8 | ALP-M14-00GNA-ME-GAD-0001 | Waste Water and Sanitary Treatment Packages - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-01 | 2027-04-01 | G-PRC-FAB MR-ME-014 | 2027-08-23
8 | ALP-M04-00PAA-ME-ITP-0001 | Travelling Band Screens and Trash Rakes - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-10 | 2027-04-05 | G-PRC-FAB MR-ME-004 | 2027-07-21
8 | ALP-M18-10HSB-ME-ITP-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-15 | 2027-04-05 | G-PRC-FAB MR-ME-018 | 2027-06-28
8 | ALP-M05-00PBA-ME-ITP-0001 | Electro-Chlorination Package - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-11 | 2027-04-06 | G-PRC-FAB MR-ME-005 | 2027-07-21
8 | ALP-M20-00SGA-ME-GAD-0001 | Fire Pumps and Fire Protection Systems - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-03 | 2027-04-06 | G-PRC-FAB MR-ME-020 | 2027-06-18
8 | ALP-M01-10LAC-ME-GAD-0001 | Boiler Feed Pumps - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-04-08 | G-PRC-FAB MR-ME-001 | 2027-05-17
8 | ALP-M03-00PAC-ME-GAD-0001 | CW Pumps - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-04-08 | G-PRC-FAB MR-ME-003 | 2027-06-03
8 | ALP-M09-00QHA-ME-GAD-0001 | Auxiliary Boiler - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-04-08 | G-PRC-FAB MR-ME-009 | 2027-05-17
8 | ALP-M12-00GBA-CV-CAL-0001 | Water Treatment Package - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-11 | 2027-04-08 | G-PRC-FAB MR-ME-012 | 2027-06-10
8 | ALP-M12-00GBA-ME-DSH-0001 | Water Treatment Package - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-25 | 2027-04-08 | G-PRC-FAB MR-ME-012 | 2027-06-10
8 | ALP-M15-00EKA-ME-GAD-0001 | Gas Receiving and Metering Station - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-25 | 2027-04-08 | G-PRC-FAB MR-ME-015 | 2027-05-17
8 | ALP-M19-10HAN-ME-GAD-0001 | HRSG Blowdown and Drain Tanks - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-15 | 2027-04-09 | G-PRC-FAB MR-ME-019 | 2027-07-14
8 | ALP-H01-00SAA-IC-IOL-0001 | HVAC Plant and Equipment - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-11 | 2027-04-12
8 | ALP-H01-00SAA-ME-CAL-0001 | HVAC Plant and Equipment - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-11 | 2027-04-12 | G-PRC-FAB MR-HV-001 | 2027-06-07
8 | ALP-H01-00SAA-PR-PID-0001 | HVAC Plant and Equipment - Supplier P&IDs | NONE | IFR | A | no | 2027-03-11 | 2027-04-12 | G-PRC-FAB MR-HV-001 | 2027-06-07
8 | ALP-M14-00GNA-IC-IOL-0001 | Waste Water and Sanitary Treatment Packages - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-11 | 2027-04-12
8 | ALP-M14-00GNA-ME-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-11 | 2027-04-12 | G-PRC-FAB MR-ME-014 | 2027-08-23
8 | ALP-M14-00GNA-PR-PID-0001 | Waste Water and Sanitary Treatment Packages - Supplier P&IDs | NONE | IFR | A | no | 2027-03-11 | 2027-04-12 | G-PRC-FAB MR-ME-014 | 2027-08-23
8 | ALP-EPC-00UZA-EL-ELY-0002 | Site-Wide Infrastructure - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-03-16 | 2027-04-13 | G-CON-CWP CWP-12-EL-01 | 2027-05-17
8 | ALP-M02-20LCB-ME-ITP-0001 | Condensate Extraction Pumps - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-18 | 2027-04-13 | G-PRC-FAB MR-ME-002 | 2027-07-21
8 | ALP-M07-00PGA-CV-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-22 | 2027-04-13 | G-PRC-FAB MR-ME-007 | 2027-06-28
8 | ALP-M07-00PGA-ME-DSH-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-11 | 2027-04-13 | G-PRC-FAB MR-ME-007 | 2027-06-28
8 | ALP-M08-00QEA-CV-CAL-0001 | Air Compressors and Dryers - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-22 | 2027-04-13 | G-PRC-FAB MR-ME-008 | 2027-06-28
8 | ALP-M08-00QEA-ME-DSH-0001 | Air Compressors and Dryers - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-11 | 2027-04-13 | G-PRC-FAB MR-ME-008 | 2027-06-28
8 | ALP-M16-00EGA-IC-IOL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-05 | 2027-04-13
8 | ALP-M16-00EGA-ME-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-05 | 2027-04-13 | G-PRC-FAB MR-ME-016 | 2027-05-05
8 | ALP-M16-00EGA-PR-PID-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier P&IDs | NONE | IFR | A | no | 2027-03-05 | 2027-04-13 | G-PRC-FAB MR-ME-016 | 2027-05-05
8 | ALP-M21-00SMA-IC-IOL-0001 | EOT Cranes - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-05 | 2027-04-13
8 | ALP-M21-00SMA-ME-CAL-0001 | EOT Cranes - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-05 | 2027-04-13 | G-PRC-FAB MR-ME-021 | 2027-05-19
8 | ALP-M13-00GHA-EL-WIR-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-09 | 2027-04-15 | G-CON-CWP CWP-07-ME-01 | 2027-12-27
8 | ALP-M13-00GHA-IC-DSH-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-09 | 2027-04-15
8 | ALP-M18-10HSB-CV-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-24 | 2027-04-15 | G-PRC-FAB MR-ME-018 | 2027-06-28
8 | ALP-M18-10HSB-ME-DSH-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-15 | 2027-04-15 | G-PRC-FAB MR-ME-018 | 2027-06-28
8 | ALP-M04-00PAA-CV-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-23 | 2027-04-16 | G-PRC-FAB MR-ME-004 | 2027-07-21
8 | ALP-M04-00PAA-ME-DSH-0001 | Travelling Band Screens and Trash Rakes - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-10 | 2027-04-16 | G-PRC-FAB MR-ME-004 | 2027-07-21
8 | ALP-M20-00SGA-IC-IOL-0001 | Fire Pumps and Fire Protection Systems - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-15 | 2027-04-16
8 | ALP-M20-00SGA-ME-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-15 | 2027-04-16 | G-PRC-FAB MR-ME-020 | 2027-06-18
8 | ALP-M20-00SGA-PR-PID-0001 | Fire Pumps and Fire Protection Systems - Supplier P&IDs | NONE | IFR | A | no | 2027-03-15 | 2027-04-16 | G-PRC-FAB MR-ME-020 | 2027-06-18
8 | ALP-M05-00PBA-CV-CAL-0001 | Electro-Chlorination Package - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-24 | 2027-04-19 | G-PRC-FAB MR-ME-005 | 2027-07-21
8 | ALP-M05-00PBA-ME-DSH-0001 | Electro-Chlorination Package - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-11 | 2027-04-19 | G-PRC-FAB MR-ME-005 | 2027-07-21
8 | ALP-M19-10HAN-IC-IOL-0001 | HRSG Blowdown and Drain Tanks - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-23 | 2027-04-20
8 | ALP-M19-10HAN-ME-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-23 | 2027-04-20 | G-PRC-FAB MR-ME-019 | 2027-07-14
8 | ALP-M19-10HAN-PR-PID-0001 | HRSG Blowdown and Drain Tanks - Supplier P&IDs | NONE | IFR | A | no | 2027-03-23 | 2027-04-20 | G-PRC-FAB MR-ME-019 | 2027-07-14
8 | ALP-M01-10LAC-IC-IOL-0001 | Boiler Feed Pumps - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-11 | 2027-04-22
8 | ALP-M01-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-001 | 2027-05-17
8 | ALP-M01-10LAC-PR-PID-0001 | Boiler Feed Pumps - Supplier P&IDs | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-001 | 2027-05-17
8 | ALP-M03-00PAC-IC-IOL-0001 | CW Pumps - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-11 | 2027-04-22
8 | ALP-M03-00PAC-ME-CAL-0001 | CW Pumps - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-003 | 2027-06-03
8 | ALP-M03-00PAC-PR-PID-0001 | CW Pumps - Supplier P&IDs | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-003 | 2027-06-03
8 | ALP-M07-00PGA-ME-GAD-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-22 | 2027-04-22 | G-PRC-FAB MR-ME-007 | 2027-06-28
8 | ALP-M08-00QEA-ME-GAD-0001 | Air Compressors and Dryers - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-22 | 2027-04-22 | G-PRC-FAB MR-ME-008 | 2027-06-28
8 | ALP-M09-00QHA-IC-IOL-0001 | Auxiliary Boiler - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-11 | 2027-04-22
8 | ALP-M09-00QHA-ME-CAL-0001 | Auxiliary Boiler - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-009 | 2027-05-17
8 | ALP-M09-00QHA-PR-PID-0001 | Auxiliary Boiler - Supplier P&IDs | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-009 | 2027-05-17
8 | ALP-M12-00GBA-ME-GAD-0001 | Water Treatment Package - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-012 | 2027-06-10
8 | ALP-M15-00EKA-IC-IOL-0001 | Gas Receiving and Metering Station - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-11 | 2027-04-22
8 | ALP-M15-00EKA-ME-CAL-0001 | Gas Receiving and Metering Station - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-015 | 2027-05-17
8 | ALP-M15-00EKA-PR-PID-0001 | Gas Receiving and Metering Station - Supplier P&IDs | NONE | IFR | A | no | 2027-03-11 | 2027-04-22 | G-PRC-FAB MR-ME-015 | 2027-05-17
8 | ALP-M17-00EGB-GE-ITP-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-04-08 | 2027-04-22
8 | ALP-M17-00EGB-GE-MOS-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-04-08 | 2027-04-22
8 | ALP-M17-00EGB-GE-MOS-0002 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-04-08 | 2027-04-22
8 | ALP-M17-00EGB-GE-MOS-0003 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-04-08 | 2027-04-22
8 | ALP-M17-00EGB-GE-MOS-0004 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-04-08 | 2027-04-22
8 | ALP-M17-00EGB-GE-MOS-0005 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-04-08 | 2027-04-22
8 | ALP-M17-00EGB-GE-MOS-0006 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-04-08 | 2027-04-22
8 | ALP-M13-00GHA-ME-LST-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-03-18 | 2027-04-23
8 | ALP-M02-20LCB-CV-CAL-0001 | Condensate Extraction Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-03-31 | 2027-04-26 | G-PRC-FAB MR-ME-002 | 2027-07-21
8 | ALP-M02-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-18 | 2027-04-26 | G-PRC-FAB MR-ME-002 | 2027-07-21
8 | ALP-M18-10HSB-ME-GAD-0001 | Aqueous Ammonia Storage and Forwarding - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-24 | 2027-04-26 | G-PRC-FAB MR-ME-018 | 2027-06-28
8 | ALP-EPC-00BFA-EL-WIR-0001 | LV Schematic and Wiring Diagrams, Part 1 of 13 | NONE | IFR | A | no | 2027-04-20 | 2027-04-27 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-M06-00PAH-ME-ITP-0001 | Condenser Tube Cleaning System - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-04-07 | 2027-04-28 | G-PRC-FAB MR-ME-006 | 2027-09-27
8 | ALP-M04-00PAA-ME-GAD-0001 | Travelling Band Screens and Trash Rakes - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-23 | 2027-04-29 | G-PRC-FAB MR-ME-004 | 2027-07-21
8 | ALP-EPC-00BFA-EL-WIR-0002 | LV Schematic and Wiring Diagrams, Part 10 of 13 | NONE | IFR | A | no | 2027-04-23 | 2027-04-30 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-I02-00CQA-ME-ITP-0001 | Continuous Emission Monitoring System - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-04-09 | 2027-04-30 | G-PRC-FAB MR-IC-002 | 2027-10-04
8 | ALP-M05-00PBA-ME-GAD-0001 | Electro-Chlorination Package - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-24 | 2027-04-30 | G-PRC-FAB MR-ME-005 | 2027-07-21
8 | ALP-M07-00PGA-IC-IOL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-01 | 2027-05-03
8 | ALP-M07-00PGA-ME-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-01 | 2027-05-03 | G-PRC-FAB MR-ME-007 | 2027-06-28
8 | ALP-M07-00PGA-PR-PID-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier P&IDs | NONE | IFR | A | no | 2027-04-01 | 2027-05-03 | G-PRC-FAB MR-ME-007 | 2027-06-28
8 | ALP-M08-00QEA-IC-IOL-0001 | Air Compressors and Dryers - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-01 | 2027-05-03
8 | ALP-M08-00QEA-ME-CAL-0001 | Air Compressors and Dryers - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-01 | 2027-05-03 | G-PRC-FAB MR-ME-008 | 2027-06-28
8 | ALP-M08-00QEA-PR-PID-0001 | Air Compressors and Dryers - Supplier P&IDs | NONE | IFR | A | no | 2027-04-01 | 2027-05-03 | G-PRC-FAB MR-ME-008 | 2027-06-28
8 | ALP-H01-00SAA-EL-WIR-0001 | HVAC Plant and Equipment - Supplier Electrical Schematics and Wiring Diagrams, Part 1 of 2 | NONE | IFR | A | no | 2027-03-23 | 2027-05-04 | G-CON-CWP CWP-03-HV-01 | 2027-10-11
8 | ALP-H01-00SAA-EL-WIR-0002 | HVAC Plant and Equipment - Supplier Electrical Schematics and Wiring Diagrams, Part 2 of 2 | NONE | IFR | A | no | 2027-03-23 | 2027-05-04 | G-CON-CWP CWP-03-HV-01 | 2027-10-11
8 | ALP-H01-00SAA-IC-DSH-0001 | HVAC Plant and Equipment - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-23 | 2027-05-04
8 | ALP-I03-00QUA-ME-ITP-0001 | Steam/Water Analysis System - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-04-13 | 2027-05-04 | G-PRC-FAB MR-IC-003 | 2027-10-04
8 | ALP-M14-00GNA-EL-WIR-0001 | Waste Water and Sanitary Treatment Packages - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-23 | 2027-05-04 | G-CON-CWP CWP-07-ME-01 | 2027-12-27
8 | ALP-M14-00GNA-IC-DSH-0001 | Waste Water and Sanitary Treatment Packages - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-23 | 2027-05-04
8 | ALP-M18-10HSB-IC-IOL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-05 | 2027-05-05
8 | ALP-M18-10HSB-ME-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-05 | 2027-05-05 | G-PRC-FAB MR-ME-018 | 2027-06-28
8 | ALP-M18-10HSB-PR-PID-0001 | Aqueous Ammonia Storage and Forwarding - Supplier P&IDs | NONE | IFR | A | no | 2027-04-05 | 2027-05-05 | G-PRC-FAB MR-ME-018 | 2027-06-28
8 | ALP-EPC-00CJG-GE-RPT-0001 | BOP Safety Instrumented System - Technical Bid Evaluation | NONE | IFR | A | no | 2027-04-29 | 2027-05-06 | G-PRC-PO MR-IC-008 | 2027-06-07
8 | ALP-M12-00GBA-IC-IOL-0001 | Water Treatment Package - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-25 | 2027-05-06
8 | ALP-M12-00GBA-ME-CAL-0001 | Water Treatment Package - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-25 | 2027-05-06 | G-PRC-FAB MR-ME-012 | 2027-06-10
8 | ALP-M12-00GBA-PR-PID-0001 | Water Treatment Package - Supplier P&IDs | NONE | IFR | A | no | 2027-03-25 | 2027-05-06 | G-PRC-FAB MR-ME-012 | 2027-06-10
8 | ALP-EPC-00BFA-EL-WIR-0003 | LV Schematic and Wiring Diagrams, Part 11 of 13 | NONE | IFR | A | no | 2027-04-30 | 2027-05-07 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-M02-20LCB-ME-GAD-0001 | Condensate Extraction Pumps - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-31 | 2027-05-07 | G-PRC-FAB MR-ME-002 | 2027-07-21
8 | ALP-M16-00EGA-EL-WIR-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-18 | 2027-05-07 | G-CON-CWP CWP-10-ME-01 | 2027-10-04
8 | ALP-M16-00EGA-IC-DSH-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-18 | 2027-05-07
8 | ALP-M19-10HAN-EL-WIR-0001 | HRSG Blowdown and Drain Tanks - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-31 | 2027-05-07 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
8 | ALP-M19-10HAN-IC-DSH-0001 | HRSG Blowdown and Drain Tanks - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-31 | 2027-05-07
8 | ALP-M21-00SMA-EL-WIR-0001 | EOT Cranes - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-18 | 2027-05-07 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
8 | ALP-EPC-00UPC-CV-RBR-0001 | CW Pump House - Reinforcement Drawings | NONE | IFR | A | no | 2027-04-19 | 2027-05-10 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
8 | ALP-M06-00PAH-ME-DSH-0001 | Condenser Tube Cleaning System - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-04-07 | 2027-05-10 | G-PRC-FAB MR-ME-006 | 2027-09-27
8 | ALP-M20-00SGA-EL-WIR-0001 | Fire Pumps and Fire Protection Systems - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-25 | 2027-05-10 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M20-00SGA-IC-DSH-0001 | Fire Pumps and Fire Protection Systems - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-25 | 2027-05-10
8 | ALP-I02-00CQA-ME-DSH-0001 | Continuous Emission Monitoring System - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-04-09 | 2027-05-12 | G-PRC-FAB MR-IC-002 | 2027-10-04
8 | ALP-M04-00PAA-IC-IOL-0001 | Travelling Band Screens and Trash Rakes - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-05 | 2027-05-12
8 | ALP-M04-00PAA-ME-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-05 | 2027-05-12 | G-PRC-FAB MR-ME-004 | 2027-07-21
8 | ALP-M04-00PAA-PR-PID-0001 | Travelling Band Screens and Trash Rakes - Supplier P&IDs | NONE | IFR | A | no | 2027-04-05 | 2027-05-12 | G-PRC-FAB MR-ME-004 | 2027-07-21
8 | ALP-EPC-00BFA-EL-WIR-0004 | LV Schematic and Wiring Diagrams, Part 12 of 13 | NONE | IFR | A | no | 2027-05-06 | 2027-05-13 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-H01-00SAA-ME-LST-0001 | HVAC Plant and Equipment - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-01 | 2027-05-13
8 | ALP-M05-00PBA-IC-IOL-0001 | Electro-Chlorination Package - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-06 | 2027-05-13
8 | ALP-M05-00PBA-ME-CAL-0001 | Electro-Chlorination Package - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-06 | 2027-05-13 | G-PRC-FAB MR-ME-005 | 2027-07-21
8 | ALP-M05-00PBA-PR-PID-0001 | Electro-Chlorination Package - Supplier P&IDs | NONE | IFR | A | no | 2027-04-06 | 2027-05-13 | G-PRC-FAB MR-ME-005 | 2027-07-21
8 | ALP-M14-00GNA-ME-LST-0001 | Waste Water and Sanitary Treatment Packages - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-01 | 2027-05-13
8 | ALP-I03-00QUA-ME-DSH-0001 | Steam/Water Analysis System - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-04-13 | 2027-05-14 | G-PRC-FAB MR-IC-003 | 2027-10-04
8 | ALP-M13-00GHA-ME-TST-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-04-02 | 2027-05-14 | G-PRC-FAT MR-ME-013 | 2027-06-25
8 | ALP-M19-10HAN-ME-LST-0001 | HRSG Blowdown and Drain Tanks - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-09 | 2027-05-17
8 | ALP-EPC-10UHA-CV-RBR-0001 | HRSG Foundations and Structures - Reinforcement Drawings | NONE | IFR | A | no | 2027-04-27 | 2027-05-18 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
8 | ALP-EPC-10UMA-CV-RBR-0001 | Gas Turbine Hall - Reinforcement Drawings | NONE | IFR | A | no | 2027-04-27 | 2027-05-18 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
8 | ALP-EPC-00QCA-GE-RPT-0001 | Chemical Dosing Skid - Technical Bid Evaluation | NONE | IFR | A | no | 2027-05-12 | 2027-05-19 | G-PRC-PO MR-ME-011 | 2027-05-17
8 | ALP-EPC-20UMB-CV-RBR-0001 | Steam Turbine Hall - Reinforcement Drawings | NONE | IFR | A | no | 2027-04-28 | 2027-05-19 | G-CON-CWP CWP-02-CV-02 | 2027-04-19
8 | ALP-M06-00PAH-ME-GAD-0001 | Condenser Tube Cleaning System - Supplier GA Drawings | NONE | IFR | A | no | 2027-04-16 | 2027-05-19 | G-PRC-FAB MR-ME-006 | 2027-09-27
8 | ALP-EPC-00CKA-GE-RPT-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Bid Evaluation | NONE | IFR | A | no | 2027-05-13 | 2027-05-20 | G-PRC-PO MR-IC-009 | 2027-06-21
8 | ALP-EPC-10UHN-CV-RBR-0001 | Stack Foundation - Reinforcement Drawings | NONE | IFR | A | no | 2027-04-29 | 2027-05-20 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
8 | ALP-M01-10LAC-EL-WIR-0001 | Boiler Feed Pumps - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-25 | 2027-05-20 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M01-10LAC-IC-DSH-0001 | Boiler Feed Pumps - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-25 | 2027-05-20
8 | ALP-M02-20LCB-IC-IOL-0001 | Condensate Extraction Pumps - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-13 | 2027-05-20
8 | ALP-M02-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-13 | 2027-05-20 | G-PRC-FAB MR-ME-002 | 2027-07-21
8 | ALP-M02-20LCB-PR-PID-0001 | Condensate Extraction Pumps - Supplier P&IDs | NONE | IFR | A | no | 2027-04-13 | 2027-05-20 | G-PRC-FAB MR-ME-002 | 2027-07-21
8 | ALP-M03-00PAC-EL-WIR-0001 | CW Pumps - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-25 | 2027-05-20 | G-CON-CWP CWP-05-ME-01 | 2027-12-20
8 | ALP-M03-00PAC-IC-DSH-0001 | CW Pumps - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-25 | 2027-05-20
8 | ALP-M09-00QHA-EL-WIR-0001 | Auxiliary Boiler - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-25 | 2027-05-20 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M09-00QHA-IC-DSH-0001 | Auxiliary Boiler - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-25 | 2027-05-20
8 | ALP-M15-00EKA-EL-WIR-0001 | Gas Receiving and Metering Station - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-25 | 2027-05-20 | G-CON-CWP CWP-09-ME-01 | 2027-11-01
8 | ALP-M15-00EKA-IC-DSH-0001 | Gas Receiving and Metering Station - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-25 | 2027-05-20
8 | ALP-M16-00EGA-ME-LST-0001 | LDO Unloading and Forwarding / Treatment Skids - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-03-31 | 2027-05-20
8 | ALP-M20-00SGA-ME-LST-0001 | Fire Pumps and Fire Protection Systems - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-06 | 2027-05-20
8 | ALP-M21-00SMA-ME-LST-0001 | EOT Cranes - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-03-31 | 2027-05-20
8 | ALP-EPC-00UBF-CV-RBR-0001 | Transformer Bays - Reinforcement Drawings | NONE | IFR | A | no | 2027-04-30 | 2027-05-21 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
8 | ALP-I02-00CQA-ME-GAD-0001 | Continuous Emission Monitoring System - Supplier GA Drawings | NONE | IFR | A | no | 2027-04-20 | 2027-05-21 | G-PRC-FAB MR-IC-002 | 2027-10-04
8 | ALP-EPC-00EKA-CM-OMM-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Operating Procedures | NONE | IFR | A | no | 2027-04-27 | 2027-05-25 | G-COM-SC-FF 00EKA | 2028-07-24
8 | ALP-EPC-00QJA-GE-RPT-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Bid Evaluation | NONE | IFR | A | no | 2027-05-18 | 2027-05-25 | G-PRC-PO MR-ME-010 | 2027-06-28
8 | ALP-I03-00QUA-ME-GAD-0001 | Steam/Water Analysis System - Supplier GA Drawings | NONE | IFR | A | no | 2027-04-22 | 2027-05-25 | G-PRC-FAB MR-IC-003 | 2027-10-04
8 | ALP-M07-00PGA-EL-WIR-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-13 | 2027-05-25 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M07-00PGA-IC-DSH-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-04-13 | 2027-05-25
8 | ALP-M08-00QEA-EL-WIR-0001 | Air Compressors and Dryers - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-13 | 2027-05-25 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M08-00QEA-IC-DSH-0001 | Air Compressors and Dryers - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-04-13 | 2027-05-25
8 | ALP-EPC-00EGC-CM-OMM-0001 | LDO Forwarding and Treatment - Operating Procedures | NONE | IFR | A | no | 2027-04-29 | 2027-05-27 | G-COM-SC-FF 00EGC | 2028-07-24
8 | ALP-M18-10HSB-EL-WIR-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-15 | 2027-05-27 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M18-10HSB-IC-DSH-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-04-15 | 2027-05-27
8 | ALP-M06-00PAH-IC-IOL-0001 | Condenser Tube Cleaning System - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-28 | 2027-05-28
8 | ALP-M06-00PAH-ME-CAL-0001 | Condenser Tube Cleaning System - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-28 | 2027-05-28 | G-PRC-FAB MR-ME-006 | 2027-09-27
8 | ALP-M06-00PAH-PR-PID-0001 | Condenser Tube Cleaning System - Supplier P&IDs | NONE | IFR | A | no | 2027-04-28 | 2027-05-28 | G-PRC-FAB MR-ME-006 | 2027-09-27
8 | ALP-EPC-00BFA-EL-WIR-0005 | LV Schematic and Wiring Diagrams, Part 13 of 13 | NONE | IFR | A | no | 2027-05-24 | 2027-05-31 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-EPC-00CYA-GE-RPT-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Bid Evaluation | NONE | IFR | A | no | 2027-05-24 | 2027-05-31 | G-PRC-PO MR-IC-007 | 2027-07-19
8 | ALP-I02-00CQA-IC-IOL-0001 | Continuous Emission Monitoring System - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-30 | 2027-06-01
8 | ALP-I02-00CQA-ME-CAL-0001 | Continuous Emission Monitoring System - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-30 | 2027-06-01 | G-PRC-FAB MR-IC-002 | 2027-10-04
8 | ALP-I03-00QUA-IC-IOL-0001 | Steam/Water Analysis System - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-05-04 | 2027-06-03
8 | ALP-I03-00QUA-ME-CAL-0001 | Steam/Water Analysis System - Supplier Design Calculations | NONE | IFR | A | no | 2027-05-04 | 2027-06-03 | G-PRC-FAB MR-IC-003 | 2027-10-04
8 | ALP-I03-00QUA-PR-PID-0001 | Steam/Water Analysis System - Supplier P&IDs | NONE | IFR | A | no | 2027-05-04 | 2027-06-03 | G-PRC-FAB MR-IC-003 | 2027-10-04
8 | ALP-M01-10LAC-ME-LST-0001 | Boiler Feed Pumps - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-08 | 2027-06-03
8 | ALP-M03-00PAC-ME-LST-0001 | CW Pumps - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-08 | 2027-06-03
8 | ALP-M07-00PGA-ME-LST-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-22 | 2027-06-03
8 | ALP-M08-00QEA-ME-LST-0001 | Air Compressors and Dryers - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-22 | 2027-06-03
8 | ALP-M09-00QHA-ME-LST-0001 | Auxiliary Boiler - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-08 | 2027-06-03
8 | ALP-M12-00GBA-EL-WIR-0001 | Water Treatment Package - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-08 | 2027-06-03 | G-CON-CWP CWP-07-ME-01 | 2027-12-27
8 | ALP-M12-00GBA-IC-DSH-0001 | Water Treatment Package - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-04-08 | 2027-06-03
8 | ALP-M15-00EKA-ME-LST-0001 | Gas Receiving and Metering Station - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-08 | 2027-06-03
8 | ALP-I08-00CJG-ME-ITP-0001 | BOP Safety Instrumented System - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-05-18 | 2027-06-04 | G-PRC-FAB MR-IC-008 | 2027-08-18
8 | ALP-M04-00PAA-EL-WIR-0001 | Travelling Band Screens and Trash Rakes - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-16 | 2027-06-07 | G-CON-CWP CWP-05-ME-01 | 2027-12-20
8 | ALP-M04-00PAA-IC-DSH-0001 | Travelling Band Screens and Trash Rakes - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-04-16 | 2027-06-07
8 | ALP-M18-10HSB-ME-LST-0001 | Aqueous Ammonia Storage and Forwarding - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-26 | 2027-06-07
8 | ALP-M19-10HAN-ME-TST-0001 | HRSG Blowdown and Drain Tanks - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-04-26 | 2027-06-07 | G-PRC-FAT MR-ME-019 | 2027-07-19
8 | ALP-EPC-00BFA-EL-WIR-0006 | LV Schematic and Wiring Diagrams, Part 2 of 13 | NONE | IFR | A | no | 2027-06-01 | 2027-06-08 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-M05-00PBA-EL-WIR-0001 | Electro-Chlorination Package - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-19 | 2027-06-08 | G-CON-CWP CWP-05-ME-01 | 2027-12-20
8 | ALP-M05-00PBA-IC-DSH-0001 | Electro-Chlorination Package - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-04-19 | 2027-06-08
8 | ALP-M13-00GHA-ME-PRC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-04-30 | 2027-06-11 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-EPC-00BFA-EL-WIR-0007 | LV Schematic and Wiring Diagrams, Part 3 of 13 | NONE | IFR | A | no | 2027-06-07 | 2027-06-14 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-I08-00CJG-ME-DSH-0001 | BOP Safety Instrumented System - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-05-18 | 2027-06-14 | G-PRC-FAB MR-IC-008 | 2027-08-18
8 | ALP-M02-20LCB-EL-WIR-0001 | Condensate Extraction Pumps - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-26 | 2027-06-15 | G-CON-CWP CWP-02-ME-01 | 2027-12-20
8 | ALP-M02-20LCB-IC-DSH-0001 | Condensate Extraction Pumps - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-04-26 | 2027-06-15
8 | ALP-M10-00QJA-ME-ITP-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-06-01 | 2027-06-15 | G-PRC-FAB MR-ME-010 | 2027-08-23
8 | ALP-EPC-00BFA-EL-WIR-0008 | LV Schematic and Wiring Diagrams, Part 4 of 13 | NONE | IFR | A | no | 2027-06-09 | 2027-06-16 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-H01-00SAA-ME-TST-0001 | HVAC Plant and Equipment - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-06 | 2027-06-17 | G-PRC-FAT MR-HV-001 | 2027-07-29
8 | ALP-M11-00QCA-ME-ITP-0001 | Chemical Dosing Skid - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-05-31 | 2027-06-17 | G-PRC-FAB MR-ME-011 | 2027-07-28
8 | ALP-M12-00GBA-ME-LST-0001 | Water Treatment Package - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-22 | 2027-06-17
8 | ALP-M14-00GNA-ME-TST-0001 | Waste Water and Sanitary Treatment Packages - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-06 | 2027-06-17 | G-PRC-FAT MR-ME-014 | 2027-07-29
8 | ALP-EPC-10UHN-CV-EFD-0001 | Stack Foundation - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-05-14 | 2027-06-18 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
8 | ALP-M04-00PAA-ME-LST-0001 | Travelling Band Screens and Trash Rakes - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-29 | 2027-06-18
8 | ALP-I07-00CYA-ME-ITP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-06-07 | 2027-06-21 | G-PRC-FAB MR-IC-007 | 2027-09-13
8 | ALP-M05-00PBA-ME-LST-0001 | Electro-Chlorination Package - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-30 | 2027-06-21
8 | ALP-M06-00PAH-EL-WIR-0001 | Condenser Tube Cleaning System - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-05-10 | 2027-06-21 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
8 | ALP-M06-00PAH-IC-DSH-0001 | Condenser Tube Cleaning System - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-05-10 | 2027-06-21
8 | ALP-EPC-00BFA-EL-WIR-0009 | LV Schematic and Wiring Diagrams, Part 5 of 13 | NONE | IFR | A | no | 2027-06-15 | 2027-06-22 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-M10-00QJA-ME-DSH-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-06-01 | 2027-06-22 | G-PRC-FAB MR-ME-010 | 2027-08-23
8 | ALP-I02-00CQA-EL-WIR-0001 | Continuous Emission Monitoring System - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-05-12 | 2027-06-23 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
8 | ALP-I02-00CQA-IC-DSH-0001 | Continuous Emission Monitoring System - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-05-12 | 2027-06-23
8 | ALP-I08-00CJG-ME-GAD-0001 | BOP Safety Instrumented System - Supplier GA Drawings | NONE | IFR | A | no | 2027-05-27 | 2027-06-23 | G-PRC-FAB MR-IC-008 | 2027-08-18
8 | ALP-I03-00QUA-EL-WIR-0001 | Steam/Water Analysis System - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-05-14 | 2027-06-25 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
8 | ALP-I03-00QUA-IC-DSH-0001 | Steam/Water Analysis System - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-05-14 | 2027-06-25
8 | ALP-M11-00QCA-ME-DSH-0001 | Chemical Dosing Skid - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-05-31 | 2027-06-25 | G-PRC-FAB MR-ME-011 | 2027-07-28
8 | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | NONE | IFR | A | no | 2027-06-23 | 2027-06-28 | G-PRC-ENQ MR-ME-024 | 2027-09-20
8 | ALP-I07-00CYA-ME-DSH-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-06-07 | 2027-06-28 | G-PRC-FAB MR-IC-007 | 2027-09-13
8 | ALP-M02-20LCB-ME-LST-0001 | Condensate Extraction Pumps - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-05-07 | 2027-06-28
8 | ALP-EPC-00GBA-CM-OMM-0001 | Seawater Reverse Osmosis - Operating Procedures | NONE | IFR | A | no | 2027-06-01 | 2027-06-29 | G-COM-SC-FF 00GBA | 2028-07-24
8 | ALP-M10-00QJA-ME-GAD-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier GA Drawings | NONE | IFR | A | no | 2027-06-08 | 2027-06-29 | G-PRC-FAB MR-ME-010 | 2027-08-23
8 | ALP-EPC-00BFA-EL-WIR-0010 | LV Schematic and Wiring Diagrams, Part 6 of 13 | NONE | IFR | A | no | 2027-06-23 | 2027-06-30 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-M06-00PAH-ME-LST-0001 | Condenser Tube Cleaning System - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-05-19 | 2027-06-30
8 | ALP-M20-00SGA-ME-TST-0001 | Fire Pumps and Fire Protection Systems - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-20 | 2027-07-01 | G-PRC-FAT MR-ME-020 | 2027-08-12
8 | ALP-I02-00CQA-ME-LST-0001 | Continuous Emission Monitoring System - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-05-21 | 2027-07-02
8 | ALP-I08-00CJG-IC-IOL-0001 | BOP Safety Instrumented System - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-06-04 | 2027-07-02
8 | ALP-I08-00CJG-ME-CAL-0001 | BOP Safety Instrumented System - Supplier Design Calculations | NONE | IFR | A | no | 2027-06-04 | 2027-07-02 | G-PRC-FAB MR-IC-008 | 2027-08-18
8 | ALP-EPC-00GMA-CM-OMM-0001 | Process Drains and Waste Water Collection - Operating Procedures | NONE | IFR | A | no | 2027-06-07 | 2027-07-05 | G-COM-SC-FF 00GMA | 2028-07-24
8 | ALP-I07-00CYA-ME-GAD-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier GA Drawings | NONE | IFR | A | no | 2027-06-14 | 2027-07-05 | G-PRC-FAB MR-IC-007 | 2027-09-13
8 | ALP-M19-10HAN-ME-PRC-0001 | HRSG Blowdown and Drain Tanks - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-05-24 | 2027-07-05 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
8 | ALP-I03-00QUA-ME-LST-0001 | Steam/Water Analysis System - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-05-25 | 2027-07-06
8 | ALP-M10-00QJA-IC-IOL-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-06-15 | 2027-07-06
8 | ALP-M10-00QJA-ME-CAL-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Design Calculations | NONE | IFR | A | no | 2027-06-15 | 2027-07-06 | G-PRC-FAB MR-ME-010 | 2027-08-23
8 | ALP-M10-00QJA-PR-PID-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier P&IDs | NONE | IFR | A | no | 2027-06-15 | 2027-07-06 | G-PRC-FAB MR-ME-010 | 2027-08-23
8 | ALP-M11-00QCA-ME-GAD-0001 | Chemical Dosing Skid - Supplier GA Drawings | NONE | IFR | A | no | 2027-06-09 | 2027-07-06 | G-PRC-FAB MR-ME-011 | 2027-07-28
8 | ALP-I09-00CKA-ME-ITP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-06-10 | 2027-07-08 | G-PRC-FAB MR-IC-009 | 2027-10-11
8 | ALP-M07-00PGA-ME-TST-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-27 | 2027-07-08 | G-PRC-FAT MR-ME-007 | 2027-08-19
8 | ALP-M08-00QEA-ME-TST-0001 | Air Compressors and Dryers - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-27 | 2027-07-08 | G-PRC-FAT MR-ME-008 | 2027-08-19
8 | ALP-M13-00GHA-ME-TRP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-06-25 | 2027-07-09 | G-PRC-SHP MR-ME-013 | 2027-07-23
8 | ALP-I07-00CYA-IC-IOL-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-06-21 | 2027-07-12
8 | ALP-I07-00CYA-ME-CAL-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Design Calculations | NONE | IFR | A | no | 2027-06-21 | 2027-07-12 | G-PRC-FAB MR-IC-007 | 2027-09-13
8 | ALP-M18-10HSB-ME-TST-0001 | Aqueous Ammonia Storage and Forwarding - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-31 | 2027-07-12 | G-PRC-FAT MR-ME-018 | 2027-08-23
8 | ALP-EPC-00BFA-EL-WIR-0011 | LV Schematic and Wiring Diagrams, Part 7 of 13 | NONE | IFR | A | no | 2027-07-06 | 2027-07-13 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-H01-00SAA-ME-PRC-0001 | HVAC Plant and Equipment - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-03 | 2027-07-15 | G-CON-CWP CWP-03-HV-01 | 2027-10-11
8 | ALP-M11-00QCA-IC-IOL-0001 | Chemical Dosing Skid - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-06-17 | 2027-07-15
8 | ALP-M11-00QCA-ME-CAL-0001 | Chemical Dosing Skid - Supplier Design Calculations | NONE | IFR | A | no | 2027-06-17 | 2027-07-15 | G-PRC-FAB MR-ME-011 | 2027-07-28
8 | ALP-M11-00QCA-PR-PID-0001 | Chemical Dosing Skid - Supplier P&IDs | NONE | IFR | A | no | 2027-06-17 | 2027-07-15 | G-PRC-FAB MR-ME-011 | 2027-07-28
8 | ALP-M14-00GNA-IC-LOG-0001 | Waste Water and Sanitary Treatment Packages - Supplier Logic Diagrams | NONE | IFR | A | no | 2027-05-13 | 2027-07-15
8 | ALP-M14-00GNA-ME-PRC-0001 | Waste Water and Sanitary Treatment Packages - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-03 | 2027-07-15 | G-CON-CWP CWP-07-ME-01 | 2027-12-27
8 | ALP-M16-00EGA-ME-TST-0001 | LDO Unloading and Forwarding / Treatment Skids - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-03 | 2027-07-15 | G-PRC-FAT MR-ME-016 | 2027-08-26
8 | ALP-M21-00SMA-ME-TST-0001 | EOT Cranes - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-03 | 2027-07-15 | G-PRC-FAT MR-ME-021 | 2027-08-26
8 | ALP-M10-00QJA-EL-WIR-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-06-22 | 2027-07-20 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M10-00QJA-IC-DSH-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-06-22 | 2027-07-20
8 | ALP-EPC-00BFA-EL-WIR-0012 | LV Schematic and Wiring Diagrams, Part 8 of 13 | NONE | IFR | A | no | 2027-07-14 | 2027-07-21 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-EPC-00GNA-CM-OMM-0001 | Waste Water Treatment - Operating Procedures | NONE | IFR | A | no | 2027-06-23 | 2027-07-21 | G-COM-SC-FF 00GNA | 2028-07-24
8 | ALP-I08-00CJG-EL-WIR-0001 | BOP Safety Instrumented System - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-06-14 | 2027-07-21 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
8 | ALP-EPC-00EGA-CM-OMM-0001 | LDO Unloading - Operating Procedures | NONE | IFR | A | no | 2027-06-24 | 2027-07-22 | G-COM-SC-FF 00EGA | 2028-07-24
8 | ALP-I09-00CKA-ME-DSH-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-06-10 | 2027-07-22 | G-PRC-FAB MR-IC-009 | 2027-10-11
8 | ALP-EPC-00PAA-CM-OMM-0001 | CW Intake, Screens and Outfall - Operating Procedures | NONE | IFR | A | no | 2027-06-25 | 2027-07-23 | G-COM-SC-FF 00PAA | 2028-07-24
8 | ALP-EPC-00BFA-EL-WIR-0013 | LV Schematic and Wiring Diagrams, Part 9 of 13 | NONE | IFR | A | no | 2027-07-19 | 2027-07-26 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-I07-00CYA-EL-WIR-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-06-28 | 2027-07-26 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
8 | ALP-EPC-00PGA-CM-OMM-0001 | Closed Cooling Water - Operating Procedures | NONE | IFR | A | no | 2027-06-29 | 2027-07-27 | G-COM-SC-FF 00PGA | 2028-07-24
8 | ALP-M10-00QJA-ME-LST-0001 | Nitrogen, Hydrogen and CO2 Supply - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-06-29 | 2027-07-27
8 | ALP-M10-00QJA-ME-TST-0001 | Nitrogen, Hydrogen and CO2 Supply - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-15 | 2027-07-27 | G-PRC-FAT MR-ME-010 | 2027-09-07
8 | ALP-EPC-00UEK-EL-ELY-0002 | Fuel Gas Station - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-07-01 | 2027-07-29 | G-CON-CWP CWP-09-EL-01 | 2027-12-27
8 | ALP-I08-00CJG-ME-LST-0001 | BOP Safety Instrumented System - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-06-23 | 2027-07-29
8 | ALP-M20-00SGA-ME-PRC-0001 | Fire Pumps and Fire Protection Systems - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-17 | 2027-07-29 | G-CON-CWP CWP-01-HV-01 | 2027-11-01
8 | ALP-I07-00CYA-ME-LST-0001 | Telecom, CCTV, Access Control and Perimeter Security - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-07-05 | 2027-08-02
8 | ALP-I07-00CYA-ME-TST-0001 | Telecom, CCTV, Access Control and Perimeter Security - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-21 | 2027-08-02 | G-PRC-FAT MR-IC-007 | 2027-09-13
8 | ALP-M19-10HAN-ME-TRP-0001 | HRSG Blowdown and Drain Tanks - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-07-19 | 2027-08-02 | G-PRC-SHP MR-ME-019 | 2027-08-16
8 | ALP-EPC-00EGB-CM-OMM-0001 | LDO Storage - Operating Procedures | NONE | IFR | A | no | 2027-07-06 | 2027-08-03 | G-COM-SC-FF 00EGB | 2028-07-24
8 | ALP-M11-00QCA-EL-WIR-0001 | Chemical Dosing Skid - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-06-25 | 2027-08-03 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M11-00QCA-IC-DSH-0001 | Chemical Dosing Skid - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-06-25 | 2027-08-03
8 | ALP-M06-00PAH-ME-TST-0001 | Condenser Tube Cleaning System - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-23 | 2027-08-04 | G-PRC-FAT MR-ME-006 | 2027-09-15
8 | ALP-I09-00CKA-ME-GAD-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier GA Drawings | NONE | IFR | A | no | 2027-06-24 | 2027-08-05 | G-PRC-FAB MR-IC-009 | 2027-10-11
8 | ALP-M07-00PGA-ME-PRC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-24 | 2027-08-05 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M08-00QEA-IC-LOG-0001 | Air Compressors and Dryers - Supplier Logic Diagrams | NONE | IFR | A | no | 2027-06-03 | 2027-08-05
8 | ALP-M08-00QEA-ME-PRC-0001 | Air Compressors and Dryers - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-24 | 2027-08-05 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-EPC-00EKC-CM-OMM-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Operating Procedures | NONE | IFR | A | no | 2027-07-09 | 2027-08-06 | G-COM-SC-FF 00EKC | 2028-07-24
8 | ALP-EPC-00GCA-CM-OMM-0001 | Demineralisation - Operating Procedures | NONE | IFR | A | no | 2027-07-09 | 2027-08-06 | G-COM-SC-FF 00GCA | 2028-07-24
8 | ALP-EPC-00PBA-CM-OMM-0001 | Electro-Chlorination - Operating Procedures | NONE | IFR | A | no | 2027-07-09 | 2027-08-06 | G-COM-SC-FF 00PBA | 2028-07-24
8 | ALP-I02-00CQA-ME-TST-0001 | Continuous Emission Monitoring System - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-25 | 2027-08-06 | G-PRC-FAT MR-IC-002 | 2027-09-17
8 | ALP-EPC-00GHA-CM-OMM-0001 | Demineralised Water Storage and Distribution - Operating Procedures | NONE | IFR | A | no | 2027-07-12 | 2027-08-09 | G-COM-SC-FF 00GHA | 2028-07-24
8 | ALP-EPC-00GMA-PI-ISO-0001 | Process Drains and Waste Water Collection - Isometric Drawings | NONE | IFR | A | no | 2027-08-02 | 2027-08-09 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
8 | ALP-EPC-00LDA-CM-OMM-0001 | Condensate Polishing - Operating Procedures | NONE | IFR | A | no | 2027-07-12 | 2027-08-09 | G-COM-SC-FF 00LDA | 2028-07-24
8 | ALP-EPC-00PAB-CM-OMM-0001 | CW Piping - Operating Procedures | NONE | IFR | A | no | 2027-07-12 | 2027-08-09 | G-COM-SC-FF 00PAB | 2028-07-24
8 | ALP-M18-10HSB-ME-PRC-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-28 | 2027-08-09 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-I03-00QUA-ME-TST-0001 | Steam/Water Analysis System - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-29 | 2027-08-10 | G-PRC-FAT MR-IC-003 | 2027-09-21
8 | ALP-M11-00QCA-ME-LST-0001 | Chemical Dosing Skid - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-07-06 | 2027-08-11
8 | ALP-EPC-00SAA-CM-OMM-0001 | HVAC - Operating Procedures | NONE | IFR | A | no | 2027-07-15 | 2027-08-12 | G-COM-SC-FF 00SAA | 2028-07-24
8 | ALP-H01-00SAA-ME-TRP-0001 | HVAC Plant and Equipment - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-07-29 | 2027-08-12 | G-PRC-SHP MR-HV-001 | 2027-08-26
8 | ALP-M01-10LAC-ME-TST-0001 | Boiler Feed Pumps - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-01 | 2027-08-12 | G-PRC-FAT MR-ME-001 | 2027-09-23
8 | ALP-M09-00QHA-ME-TST-0001 | Auxiliary Boiler - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-01 | 2027-08-12 | G-PRC-FAT MR-ME-009 | 2027-09-23
8 | ALP-M14-00GNA-ME-TRP-0001 | Waste Water and Sanitary Treatment Packages - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-07-29 | 2027-08-12 | G-PRC-SHP MR-ME-014 | 2027-08-26
8 | ALP-M15-00EKA-ME-TST-0001 | Gas Receiving and Metering Station - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-01 | 2027-08-12 | G-PRC-FAT MR-ME-015 | 2027-09-23
8 | ALP-M16-00EGA-ME-PRC-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-01 | 2027-08-12 | G-CON-CWP CWP-10-ME-01 | 2027-10-04
8 | ALP-M21-00SMA-ME-PRC-0001 | EOT Cranes - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-01 | 2027-08-12 | G-CON-CWP CWP-01-ME-01 | 2027-10-18
8 | ALP-M04-00PAA-ME-TST-0001 | Travelling Band Screens and Trash Rakes - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-02 | 2027-08-13 | G-PRC-FAT MR-ME-004 | 2027-09-24
8 | ALP-EPC-00SGA-CM-OMM-0001 | Fire Water System - Operating Procedures | NONE | IFR | A | no | 2027-07-19 | 2027-08-16 | G-COM-SC-FF 00SGA | 2028-07-24
8 | ALP-M05-00PBA-ME-TST-0001 | Electro-Chlorination Package - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-05 | 2027-08-16 | G-PRC-FAT MR-ME-005 | 2027-09-27
8 | ALP-EPC-00PAC-CM-OMM-0001 | CW Pumps - Operating Procedures | NONE | IFR | A | no | 2027-07-21 | 2027-08-18 | G-COM-SC-FF 00PAC | 2028-07-24
8 | ALP-EPC-00QCA-CM-OMM-0001 | Chemical Dosing - Operating Procedures | NONE | IFR | A | no | 2027-07-21 | 2027-08-18 | G-COM-SC-FF 00QCA | 2028-07-24
8 | ALP-EPC-00PAH-CM-OMM-0001 | Condenser Tube Cleaning - Operating Procedures | NONE | IFR | A | no | 2027-07-22 | 2027-08-19 | G-COM-SC-FF 00PAH | 2028-07-24
8 | ALP-EPC-00UZF-CV-RBR-0001 | Temporary Barge Landing - Reinforcement Drawings | NONE | IFR | A | no | 2027-07-29 | 2027-08-19 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
8 | ALP-I08-00CJG-ME-TST-0001 | BOP Safety Instrumented System - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-08 | 2027-08-19 | G-PRC-FAT MR-IC-008 | 2027-09-30
8 | ALP-I09-00CKA-IC-IOL-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-07-08 | 2027-08-19
8 | ALP-I09-00CKA-ME-CAL-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Design Calculations | NONE | IFR | A | no | 2027-07-08 | 2027-08-19 | G-PRC-FAB MR-IC-009 | 2027-10-11
8 | ALP-M02-20LCB-ME-TST-0001 | Condensate Extraction Pumps - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-12 | 2027-08-23 | G-PRC-FAT MR-ME-002 | 2027-10-04
8 | ALP-M10-00QJA-ME-PRC-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-13 | 2027-08-24 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-EPC-00SGC-CM-OMM-0001 | Deluge, Spray and Foam Systems - Operating Procedures | NONE | IFR | A | no | 2027-07-28 | 2027-08-25 | G-COM-SC-FF 00SGC | 2028-07-24
8 | ALP-EPC-00GKA-PI-ISO-0001 | Potable Water - Isometric Drawings | NONE | IFR | A | no | 2027-08-19 | 2027-08-26 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
8 | ALP-EPC-00QEA-CM-OMM-0001 | Compressed Air - Operating Procedures | NONE | IFR | A | no | 2027-07-29 | 2027-08-26 | G-COM-SC-FF 00QEA | 2028-07-24
8 | ALP-M09-00QHA-IC-LOG-0001 | Auxiliary Boiler - Supplier Logic Diagrams | NONE | IFR | A | no | 2027-06-03 | 2027-08-26
8 | ALP-M20-00SGA-ME-TRP-0001 | Fire Pumps and Fire Protection Systems - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-12 | 2027-08-26 | G-PRC-SHP MR-ME-020 | 2027-09-09
8 | ALP-EPC-00PAA-PI-ISO-0001 | CW Intake, Screens and Outfall - Isometric Drawings | NONE | IFR | A | no | 2027-08-20 | 2027-08-27 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
8 | ALP-EPC-00PAC-PI-ISO-0001 | CW Pumps - Isometric Drawings | NONE | IFR | A | no | 2027-08-20 | 2027-08-27 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
8 | ALP-EPC-00UAC-IC-LOP-0001 | 380 kV GIS Switchyard - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-08-20 | 2027-08-27 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
8 | ALP-EPC-00UZA-IC-LOP-0001 | Site-Wide Infrastructure - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-08-20 | 2027-08-27 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
8 | ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings | NONE | IFR | A | no | 2027-08-23 | 2027-08-30 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
8 | ALP-EPC-00PBA-PI-ISO-0001 | Electro-Chlorination - Isometric Drawings | NONE | IFR | A | no | 2027-08-23 | 2027-08-30 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
8 | ALP-I07-00CYA-ME-PRC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-19 | 2027-08-30 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
8 | ALP-EPC-00UZF-EL-ELY-0001 | Temporary Barge Landing - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-08-03 | 2027-08-31 | G-CON-CWP CWP-06-CV-01 | 2027-09-03
8 | ALP-M06-00PAH-ME-PRC-0001 | Condenser Tube Cleaning System - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-21 | 2027-09-01 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
8 | ALP-M11-00QCA-ME-TST-0001 | Chemical Dosing Skid - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-21 | 2027-09-01 | G-PRC-FAT MR-ME-011 | 2027-10-13
8 | ALP-M07-00PGA-ME-TRP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-19 | 2027-09-02 | G-PRC-SHP MR-ME-007 | 2027-09-16
8 | ALP-M08-00QEA-ME-TRP-0001 | Air Compressors and Dryers - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-19 | 2027-09-02 | G-PRC-SHP MR-ME-008 | 2027-09-16
8 | ALP-EPC-00QHA-CM-OMM-0001 | Auxiliary Boiler - Operating Procedures | NONE | IFR | A | no | 2027-08-06 | 2027-09-03 | G-COM-SC-FF 00QHA | 2028-07-24
8 | ALP-EPC-00QJA-CM-OMM-0001 | Nitrogen Supply - Operating Procedures | NONE | IFR | A | no | 2027-08-06 | 2027-09-03 | G-COM-SC-FF 00QJA | 2028-07-24
8 | ALP-EPC-00QJB-CM-OMM-0001 | Hydrogen and CO2 Supply - Operating Procedures | NONE | IFR | A | no | 2027-08-06 | 2027-09-03 | G-COM-SC-FF 00QJB | 2028-07-24
8 | ALP-I02-00CQA-ME-PRC-0001 | Continuous Emission Monitoring System - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-23 | 2027-09-03 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
8 | ALP-M05-00PBA-IC-LOG-0001 | Electro-Chlorination Package - Supplier Logic Diagrams | NONE | IFR | A | no | 2027-06-21 | 2027-09-03
8 | ALP-M13-00GHA-ME-MDB-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-07-09 | 2027-09-03 | G-PRC-SHP MR-ME-013 | 2027-07-23
8 | ALP-M18-10HSB-ME-TRP-0001 | Aqueous Ammonia Storage and Forwarding - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-23 | 2027-09-06 | G-PRC-SHP MR-ME-018 | 2027-09-20
8 | ALP-EPC-00QUA-CM-OMM-0001 | Sampling and SWAS - Operating Procedures | NONE | IFR | A | no | 2027-08-10 | 2027-09-07 | G-COM-SC-FF 00QUA | 2028-07-24
8 | ALP-EPC-00UBA-EL-ELY-0002 | Electrical Building and Emergency Power - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-08-10 | 2027-09-07 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-EPC-00UCA-EL-ELY-0002 | Control, Administration and Workshop Buildings - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-08-10 | 2027-09-07 | G-CON-CWP CWP-11-EL-01 | 2027-11-08
8 | ALP-I03-00QUA-ME-PRC-0001 | Steam/Water Analysis System - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-27 | 2027-09-07 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
8 | ALP-EPC-00UAC-IC-LOP-0002 | 380 kV GIS Switchyard - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
8 | ALP-EPC-00UBA-IC-LOP-0002 | Electrical Building and Emergency Power - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-EPC-00UCA-IC-LOP-0001 | Control, Administration and Workshop Buildings - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
8 | ALP-EPC-00UEG-IC-LOP-0001 | LDO Tank Farm and Unloading - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-10-IC-01 | 2028-02-21
8 | ALP-EPC-00UEG-IC-LOP-0002 | LDO Tank Farm and Unloading - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-10-IC-01 | 2028-02-21
8 | ALP-EPC-00UEK-IC-LOP-0001 | Fuel Gas Station - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-09-IC-01 | 2028-01-24
8 | ALP-EPC-00UPC-IC-LOP-0001 | CW Pump House and Onshore CW - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-05-IC-01 | 2028-02-28
8 | ALP-EPC-00UPC-IC-LOP-0002 | CW Pump House and Onshore CW - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-05-IC-01 | 2028-02-28
8 | ALP-EPC-00UQA-IC-LOP-0001 | BOP Utilities - Loop and Connection Diagrams, Part 1 of 2 | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-08-IC-01 | 2028-02-21
8 | ALP-EPC-00UQA-IC-LOP-0003 | BOP Utilities - Loop and Connection Diagrams, Part 2 of 2 | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-08-IC-01 | 2028-02-21
8 | ALP-EPC-00UZA-IC-LOP-0002 | Site-Wide Infrastructure - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
8 | ALP-EPC-10UMA-IC-LOP-0001 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 1 of 2 | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
8 | ALP-EPC-10UMA-IC-LOP-0003 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 2 of 2 | NONE | IFR | A | no | 2027-09-01 | 2027-09-08 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
8 | ALP-EPC-00UEK-IC-LOP-0002 | Fuel Gas Station - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-02 | 2027-09-09 | G-CON-CWP CWP-09-IC-01 | 2028-01-24
8 | ALP-EPC-10UMA-EL-ELY-0002 | Power Block - GT and HRSG - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-08-12 | 2027-09-09 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
8 | ALP-M01-10LAC-ME-PRC-0001 | Boiler Feed Pumps - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-29 | 2027-09-09 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M03-00PAC-ME-TST-0001 | CW Pumps - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-29 | 2027-09-09 | G-PRC-FAT MR-ME-003 | 2027-10-21
8 | ALP-M09-00QHA-ME-PRC-0001 | Auxiliary Boiler - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-29 | 2027-09-09 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-M12-00GBA-IC-LOG-0001 | Water Treatment Package - Supplier Logic Diagrams | NONE | IFR | A | no | 2027-06-17 | 2027-09-09
8 | ALP-M15-00EKA-ME-PRC-0001 | Gas Receiving and Metering Station - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-29 | 2027-09-09 | G-CON-CWP CWP-09-ME-01 | 2027-11-01
8 | ALP-M16-00EGA-ME-TRP-0001 | LDO Unloading and Forwarding / Treatment Skids - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-26 | 2027-09-09 | G-PRC-SHP MR-ME-016 | 2027-09-23
8 | ALP-M21-00SMA-ME-TRP-0001 | EOT Cranes - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-26 | 2027-09-09 | G-PRC-SHP MR-ME-021 | 2027-09-23
8 | ALP-EPC-00UAC-EL-ELY-0002 | 380 kV GIS Switchyard - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-08-13 | 2027-09-10 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
8 | ALP-EPC-00UCA-IC-LOP-0002 | Control, Administration and Workshop Buildings - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-03 | 2027-09-10 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
8 | ALP-M04-00PAA-ME-PRC-0001 | Travelling Band Screens and Trash Rakes - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-30 | 2027-09-10 | G-CON-CWP CWP-05-ME-01 | 2027-12-20
8 | ALP-EPC-00GKA-CM-OMM-0001 | Potable Water - Operating Procedures | NONE | IFR | A | no | 2027-08-16 | 2027-09-13 | G-COM-SC-FF 00GKA | 2028-07-24
8 | ALP-EPC-00GUA-CM-OMM-0001 | Sanitary Waste Water Treatment - Operating Procedures | NONE | IFR | A | no | 2027-08-16 | 2027-09-13 | G-COM-SC-FF 00GUA | 2028-07-24
8 | ALP-M05-00PBA-ME-PRC-0001 | Electro-Chlorination Package - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-08-02 | 2027-09-13 | G-CON-CWP CWP-05-ME-01 | 2027-12-20
8 | ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings | NONE | IFR | A | no | 2027-09-07 | 2027-09-14 | G-CON-CWP CWP-09-PI-01 | 2027-11-29
8 | ALP-EPC-10HSB-CM-OMM-0001 | Ammonia Storage and Supply - Operating Procedures | NONE | IFR | A | no | 2027-08-17 | 2027-09-14 | G-COM-SC-FF 10HSB | 2028-07-24
8 | ALP-EPC-00000-HS-RPT-0005 | Explosion Protection Document | NONE | IFR | A | no | 2027-08-25 | 2027-09-15
8 | ALP-EPC-00UBA-IC-LOP-0001 | Electrical Building and Emergency Power - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-08 | 2027-09-15 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
8 | ALP-I08-00CJG-ME-PRC-0001 | BOP Safety Instrumented System - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-08-05 | 2027-09-16 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
8 | ALP-I09-00CKA-EL-WIR-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-07-22 | 2027-09-16 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
8 | ALP-EPC-00UGA-IC-LOP-0001 | Water Treatment and Effluents - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-10 | 2027-09-17 | G-CON-CWP CWP-07-IC-01 | 2028-03-20
8 | ALP-EPC-00UGA-IC-LOP-0002 | Water Treatment and Effluents - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-13 | 2027-09-20 | G-CON-CWP CWP-07-IC-01 | 2028-03-20
8 | ALP-EPC-20UMB-IC-LOP-0002 | Power Block - ST and Condenser - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-13 | 2027-09-20 | G-CON-CWP CWP-02-IC-01 | 2028-03-27
8 | ALP-M02-20LCB-ME-PRC-0001 | Condensate Extraction Pumps - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-08-09 | 2027-09-20 | G-CON-CWP CWP-02-ME-01 | 2027-12-20
8 | ALP-M10-00QJA-ME-TRP-0001 | Nitrogen, Hydrogen and CO2 Supply - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-07 | 2027-09-21 | G-PRC-SHP MR-ME-010 | 2027-10-05
8 | ALP-EPC-00UQA-EL-ELY-0002 | BOP Utilities - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-08-25 | 2027-09-22 | G-CON-CWP CWP-08-EL-01 | 2028-01-10
8 | ALP-I08-00CJG-IC-LOG-0001 | BOP Safety Instrumented System - Supplier Logic Diagrams | NONE | IFR | A | no | 2027-07-29 | 2027-09-22
8 | ALP-P04-00PAB-ME-MDB-0001 | GRP CW Pipes and Fittings - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-07-28 | 2027-09-22 | G-PRC-SHP MR-PI-004 | 2027-08-11
8 | ALP-M12-00GBA-ME-TST-0001 | Water Treatment Package - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-08-12 | 2027-09-23 | G-PRC-FAT MR-ME-012 | 2027-11-04
8 | ALP-EPC-00UEG-EL-ELY-0002 | LDO Tank Farm and Unloading - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-08-30 | 2027-09-27 | G-CON-CWP CWP-10-EL-01 | 2028-01-24
8 | ALP-EPC-10UHN-EL-ELY-0001 | Stack Foundation - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-08-30 | 2027-09-27 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
8 | ALP-EPC-20UMB-IC-LOP-0001 | Power Block - ST and Condenser - Loop and Connection Diagrams | NONE | IFR | A | no | 2027-09-20 | 2027-09-27 | G-CON-CWP CWP-02-IC-01 | 2028-03-27
8 | ALP-I07-00CYA-ME-TRP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-13 | 2027-09-27 | G-PRC-SHP MR-IC-007 | 2027-10-11
8 | ALP-M19-10HAN-ME-MDB-0001 | HRSG Blowdown and Drain Tanks - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-02 | 2027-09-27 | G-PRC-SHP MR-ME-019 | 2027-08-16
8 | ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings | NONE | IFR | A | no | 2027-09-21 | 2027-09-28 | G-CON-CWP CWP-09-PI-01 | 2027-11-29
8 | ALP-EPC-10UMA-IC-LOP-0002 | Power Block - GT and HRSG - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-22 | 2027-09-29 | G-CON-CWP CWP-01-IC-01 | 2028-02-07
8 | ALP-M06-00PAH-ME-TRP-0001 | Condenser Tube Cleaning System - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-15 | 2027-09-29 | G-PRC-SHP MR-ME-006 | 2027-10-13
8 | ALP-M11-00QCA-ME-PRC-0001 | Chemical Dosing Skid - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-08-18 | 2027-09-29 | G-CON-CWP CWP-08-ME-01 | 2027-11-01
8 | ALP-EPC-00000-IC-LST-0003 | Interlock and Trip List | NONE | IFR | A | no | 2027-09-02 | 2027-09-30 | G-OWN-TO 00000 | 2029-04-18
8 | ALP-I09-00CKA-ME-LST-0001 | Operator Training Simulator, Historian and Performance Monitoring - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-08-05 | 2027-09-30
8 | ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings | NONE | IFR | A | no | 2027-09-24 | 2027-10-01 | G-CON-CWP CWP-10-PI-01 | 2027-12-27
8 | ALP-I02-00CQA-ME-TRP-0001 | Continuous Emission Monitoring System - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-17 | 2027-10-01 | G-PRC-SHP MR-IC-002 | 2027-10-15
8 | ALP-EPC-00UQA-IC-LOP-0002 | BOP Utilities - Junction Box and Cabinet Interconnection Diagrams | NONE | IFR | A | no | 2027-09-27 | 2027-10-04 | G-CON-CWP CWP-08-IC-01 | 2028-02-21
8 | ALP-I03-00QUA-ME-TRP-0001 | Steam/Water Analysis System - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-21 | 2027-10-05 | G-PRC-SHP MR-IC-003 | 2027-10-19
8 | ALP-EPC-00UBF-EL-ELY-0001 | Transformer Bays - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-09-08 | 2027-10-06 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
8 | ALP-EPC-00UPC-EL-ELY-0002 | CW Pump House and Onshore CW - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-09-08 | 2027-10-06 | G-CON-CWP CWP-05-EL-01 | 2028-01-31
8 | ALP-EPC-10UHA-EL-ELY-0001 | HRSG Foundations and Structures - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-09-09 | 2027-10-07 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
8 | ALP-EPC-10UMA-EL-ELY-0003 | Gas Turbine Hall - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-09-09 | 2027-10-07 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
8 | ALP-H01-00SAA-ME-MDB-0001 | HVAC Plant and Equipment - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-12 | 2027-10-07 | G-PRC-SHP MR-HV-001 | 2027-08-26
8 | ALP-M01-10LAC-ME-TRP-0001 | Boiler Feed Pumps - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-23 | 2027-10-07 | G-PRC-SHP MR-ME-001 | 2027-10-21
8 | ALP-M03-00PAC-ME-PRC-0001 | CW Pumps - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-08-26 | 2027-10-07 | G-CON-CWP CWP-05-ME-01 | 2027-12-20
8 | ALP-M09-00QHA-ME-TRP-0001 | Auxiliary Boiler - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-23 | 2027-10-07 | G-PRC-SHP MR-ME-009 | 2027-10-21
8 | ALP-M14-00GNA-ME-MDB-0001 | Waste Water and Sanitary Treatment Packages - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-12 | 2027-10-07 | G-PRC-SHP MR-ME-014 | 2027-08-26
8 | ALP-M15-00EKA-ME-TRP-0001 | Gas Receiving and Metering Station - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-23 | 2027-10-07 | G-PRC-SHP MR-ME-015 | 2027-10-21
8 | ALP-EPC-00UPC-EL-ELY-0003 | CW Pump House - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-09-10 | 2027-10-08 | G-CON-CWP CWP-05-EL-01 | 2028-01-31
8 | ALP-M04-00PAA-ME-TRP-0001 | Travelling Band Screens and Trash Rakes - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-24 | 2027-10-08 | G-PRC-SHP MR-ME-004 | 2027-10-22
8 | ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | NONE | IFR | A | no | 2027-10-04 | 2027-10-11 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-M05-00PBA-ME-TRP-0001 | Electro-Chlorination Package - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-27 | 2027-10-11 | G-PRC-SHP MR-ME-005 | 2027-10-25
8 | ALP-EPC-00000-HS-STU-0003 | Fire and Gas Detector Mapping Study | NONE | IFR | A | no | 2027-09-15 | 2027-10-13
8 | ALP-I08-00CJG-ME-TRP-0001 | BOP Safety Instrumented System - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-30 | 2027-10-14 | G-PRC-SHP MR-IC-008 | 2027-10-28
8 | ALP-M13-00GHA-ME-OMM-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-05-28 | 2027-10-15 | G-COM-SC-FF 00GHA | 2028-07-24
8 | ALP-EPC-00EGA-IC-CEM-0001 | LDO Unloading - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-13 | 2027-10-18
8 | ALP-M02-20LCB-ME-TRP-0001 | Condensate Extraction Pumps - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-10-04 | 2027-10-18 | G-PRC-SHP MR-ME-002 | 2027-11-01
8 | ALP-EPC-00000-HS-PLN-0005 | Emergency Response Plan | NONE | IFR | A | no | 2027-09-14 | 2027-10-19
8 | ALP-EPC-00UGA-EL-ELY-0002 | Water Treatment and Effluents - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-09-21 | 2027-10-19 | G-CON-CWP CWP-07-EL-01 | 2028-02-21
8 | ALP-EPC-00EKC-IC-CEM-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-15 | 2027-10-20
8 | ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | NONE | IFR | A | no | 2027-10-13 | 2027-10-20 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
8 | ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | NONE | IFR | A | no | 2027-10-14 | 2027-10-21 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-M12-00GBA-ME-PRC-0001 | Water Treatment Package - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-09-09 | 2027-10-21 | G-CON-CWP CWP-07-ME-01 | 2027-12-27
8 | ALP-M20-00SGA-ME-MDB-0001 | Fire Pumps and Fire Protection Systems - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-26 | 2027-10-21 | G-PRC-SHP MR-ME-020 | 2027-09-09
8 | ALP-EPC-00SAA-PI-SUP-0001 | HVAC - Pipe Support Drawings | NONE | IFR | A | no | 2027-10-15 | 2027-10-22 | G-CON-CWP CWP-03-HV-01 | 2027-10-11
8 | ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | NONE | IFR | A | no | 2027-10-15 | 2027-10-22 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-EPC-20UMB-EL-ELY-0003 | Steam Turbine Hall - Earthing and Lightning Protection Layouts | NONE | IFR | A | no | 2027-09-27 | 2027-10-25 | G-CON-CWP CWP-02-EL-01 | 2028-02-28
8 | ALP-EPC-00000-EL-LST-0004 | Hazardous Area Electrical Equipment Register | NONE | IFR | A | no | 2027-09-29 | 2027-10-27 | G-OWN-TO 00000 | 2029-04-18
8 | ALP-EPC-00LBG-IC-CEM-0001 | Auxiliary Steam - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-22 | 2027-10-27
8 | ALP-EPC-00QJA-IC-CEM-0001 | Nitrogen Supply - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-22 | 2027-10-27
8 | ALP-EPC-00QJB-IC-CEM-0001 | Hydrogen and CO2 Supply - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-22 | 2027-10-27
8 | ALP-M11-00QCA-ME-TRP-0001 | Chemical Dosing Skid - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-10-13 | 2027-10-27 | G-PRC-SHP MR-ME-011 | 2027-11-10
8 | ALP-EPC-00EGB-IC-CEM-0001 | LDO Storage - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-23 | 2027-10-28
8 | ALP-EPC-00EGC-IC-CEM-0001 | LDO Forwarding and Treatment - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-23 | 2027-10-28
8 | ALP-EPC-00QCA-IC-CEM-0001 | Chemical Dosing - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-23 | 2027-10-28
8 | ALP-EPC-00QEA-IC-CEM-0001 | Compressed Air - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-23 | 2027-10-28
8 | ALP-EPC-00QHA-IC-CEM-0001 | Auxiliary Boiler - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-23 | 2027-10-28
8 | ALP-EPC-00QUA-IC-CEM-0001 | Sampling and SWAS - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-23 | 2027-10-28
8 | ALP-M07-00PGA-ME-MDB-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-02 | 2027-10-28 | G-PRC-SHP MR-ME-007 | 2027-09-16
8 | ALP-M08-00QEA-ME-MDB-0001 | Air Compressors and Dryers - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-02 | 2027-10-28 | G-PRC-SHP MR-ME-008 | 2027-09-16
8 | ALP-EPC-00EKA-IC-CEM-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-24 | 2027-10-29
8 | ALP-EPC-00SGA-IC-CEM-0001 | Fire Water System - Cause and Effect Matrix | NONE | IFR | A | no | 2027-09-24 | 2027-10-29
8 | ALP-M18-10HSB-ME-MDB-0001 | Aqueous Ammonia Storage and Forwarding - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-06 | 2027-11-01 | G-PRC-SHP MR-ME-018 | 2027-09-20
8 | ALP-EPC-00000-IC-SPC-0006 | BOP SIS - Safety Requirements Specification | NONE | IFR | A | no | 2027-09-29 | 2027-11-03
8 | ALP-EPC-20UMB-EL-ELY-0002 | Power Block - ST and Condenser - Cable Routing, Tray and Trench Layouts | NONE | IFR | A | no | 2027-10-07 | 2027-11-04 | G-CON-CWP CWP-02-EL-01 | 2028-02-28
8 | ALP-M03-00PAC-ME-TRP-0001 | CW Pumps - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-10-21 | 2027-11-04 | G-PRC-SHP MR-ME-003 | 2027-11-18
8 | ALP-M16-00EGA-ME-MDB-0001 | LDO Unloading and Forwarding / Treatment Skids - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-09 | 2027-11-04 | G-PRC-SHP MR-ME-016 | 2027-09-23
8 | ALP-M21-00SMA-ME-MDB-0001 | EOT Cranes - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-09 | 2027-11-04 | G-PRC-SHP MR-ME-021 | 2027-09-23
8 | ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | NONE | IFR | A | no | 2027-10-29 | 2027-11-05 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-M19-10HAN-ME-OMM-0001 | HRSG Blowdown and Drain Tanks - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-06-21 | 2027-11-08 | G-COM-SC-WS 10HAN | 2028-09-25
8 | ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | NONE | IFR | A | no | 2027-11-02 | 2027-11-09 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-EPC-00SGC-IC-CEM-0001 | Deluge, Spray and Foam Systems - Cause and Effect Matrix | NONE | IFR | A | no | 2027-10-05 | 2027-11-09
8 | ALP-EPC-00LBG-CM-OMM-0001 | Auxiliary Steam - Operating Procedures | NONE | IFR | A | no | 2027-10-13 | 2027-11-10 | G-COM-SC-WS 00LBG | 2028-09-25
8 | ALP-EPC-10HAN-CM-OMM-0001 | HRSG Blowdown and Drains - Operating Procedures | NONE | IFR | A | no | 2027-10-13 | 2027-11-10 | G-COM-SC-WS 10HAN | 2028-09-25
8 | ALP-EPC-10LAB-CM-OMM-0001 | Feedwater Piping - Operating Procedures | NONE | IFR | A | no | 2027-10-15 | 2027-11-12 | G-COM-SC-WS 10LAB | 2028-09-25
8 | ALP-EPC-10LAC-CM-OMM-0001 | Boiler Feed Pumps - Operating Procedures | NONE | IFR | A | no | 2027-10-15 | 2027-11-12 | G-COM-SC-WS 10LAC | 2028-09-25
8 | ALP-EPC-10LAE-CM-OMM-0001 | HP Attemperation Spray Water - Operating Procedures | NONE | IFR | A | no | 2027-10-15 | 2027-11-12 | G-COM-SC-WS 10LAE | 2028-09-25
8 | ALP-EPC-10LAF-CM-OMM-0001 | Reheat Attemperation Spray Water - Operating Procedures | NONE | IFR | A | no | 2027-10-15 | 2027-11-12 | G-COM-SC-WS 10LAF | 2028-09-25
8 | ALP-EPC-10HAN-IC-CEM-0001 | HRSG Blowdown and Drains - Cause and Effect Matrix | NONE | IFR | A | no | 2027-10-11 | 2027-11-15
8 | ALP-M10-00QJA-ME-MDB-0001 | Nitrogen, Hydrogen and CO2 Supply - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-21 | 2027-11-16 | G-PRC-SHP MR-ME-010 | 2027-10-05
8 | ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | NONE | IFR | A | no | 2027-11-11 | 2027-11-18 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-EPC-10LAB-IC-CEM-0001 | Feedwater Piping - Cause and Effect Matrix | NONE | IFR | A | no | 2027-10-14 | 2027-11-18
8 | ALP-H01-00SAA-ME-OMM-0001 | HVAC Plant and Equipment - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-01 | 2027-11-18 | G-COM-SC-FF 00SAA | 2028-07-24
8 | ALP-M12-00GBA-ME-TRP-0001 | Water Treatment Package - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-11-04 | 2027-11-18 | G-PRC-SHP MR-ME-012 | 2027-12-02
8 | ALP-M14-00GNA-ME-OMM-0001 | Waste Water and Sanitary Treatment Packages - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-01 | 2027-11-18 | G-COM-SC-FF 00GMA | 2028-07-24
8 | ALP-EPC-10HSB-IC-CEM-0001 | Ammonia Storage and Supply - Cause and Effect Matrix | NONE | IFR | A | no | 2027-10-15 | 2027-11-19
8 | ALP-EPC-10LBA-CM-OMM-0001 | Main Steam Piping - Operating Procedures | NONE | IFR | A | no | 2027-10-25 | 2027-11-22 | G-COM-SC-WS 10LBA | 2028-09-25
8 | ALP-I07-00CYA-ME-MDB-0001 | Telecom, CCTV, Access Control and Perimeter Security - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-27 | 2027-11-22 | G-PRC-SHP MR-IC-007 | 2027-10-11
8 | ALP-EPC-00EGA-PI-ISO-0001 | LDO Unloading - Isometric Drawings | NONE | IFR | A | no | 2027-11-16 | 2027-11-23 | G-CON-CWP CWP-10-PI-01 | 2027-12-27
8 | ALP-EPC-10LBB-CM-OMM-0001 | Hot Reheat Piping - Operating Procedures | NONE | IFR | A | no | 2027-10-26 | 2027-11-23 | G-COM-SC-WS 10LBB | 2028-09-25
8 | ALP-EPC-10LBC-CM-OMM-0001 | Cold Reheat Piping - Operating Procedures | NONE | IFR | A | no | 2027-10-26 | 2027-11-23 | G-COM-SC-WS 10LBC | 2028-09-25
8 | ALP-EPC-10LAC-IC-CEM-0001 | Boiler Feed Pumps - Cause and Effect Matrix | NONE | IFR | A | no | 2027-10-20 | 2027-11-24
8 | ALP-M06-00PAH-ME-MDB-0001 | Condenser Tube Cleaning System - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-29 | 2027-11-24 | G-PRC-SHP MR-ME-006 | 2027-10-13
8 | ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | NONE | IFR | A | no | 2027-11-18 | 2027-11-25 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-EPC-10LBD-CM-OMM-0001 | LP Steam Piping - Operating Procedures | NONE | IFR | A | no | 2027-10-28 | 2027-11-25 | G-COM-SC-WS 10LBD | 2028-09-25
8 | ALP-EPC-20LCA-CM-OMM-0001 | Main Condensate Piping - Operating Procedures | NONE | IFR | A | no | 2027-10-28 | 2027-11-25 | G-COM-SC-WS 20LCA | 2028-09-25
8 | ALP-EPC-00000-EL-BLK-0001 | Cable Block Diagrams, Part 1 of 2 | NONE | IFR | A | no | 2027-10-22 | 2027-11-26
8 | ALP-I02-00CQA-ME-MDB-0001 | Continuous Emission Monitoring System - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-01 | 2027-11-26 | G-PRC-SHP MR-IC-002 | 2027-10-15
8 | ALP-EPC-10LAE-IC-CEM-0001 | HP Attemperation Spray Water - Cause and Effect Matrix | NONE | IFR | A | no | 2027-10-26 | 2027-11-30
8 | ALP-EPC-20LCB-CM-OMM-0001 | Condensate Extraction Pumps - Operating Procedures | NONE | IFR | A | no | 2027-11-02 | 2027-11-30 | G-COM-SC-WS 20LCB | 2028-09-25
8 | ALP-I03-00QUA-ME-MDB-0001 | Steam/Water Analysis System - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-05 | 2027-11-30 | G-PRC-SHP MR-IC-003 | 2027-10-19
8 | ALP-EPC-00000-CM-CMP-0003 | Grid Code Compliance Test Programme | NONE | IFR | A | no | 2027-10-27 | 2027-12-01 | G-OWN-TOC 00000 | 2028-08-21
8 | ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | NONE | IFR | A | no | 2027-11-24 | 2027-12-01 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-EPC-10LAF-IC-CEM-0001 | Reheat Attemperation Spray Water - Cause and Effect Matrix | NONE | IFR | A | no | 2027-10-28 | 2027-12-02
8 | ALP-M01-10LAC-ME-MDB-0001 | Boiler Feed Pumps - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-07 | 2027-12-02 | G-PRC-SHP MR-ME-001 | 2027-10-21
8 | ALP-M09-00QHA-ME-MDB-0001 | Auxiliary Boiler - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-07 | 2027-12-02 | G-PRC-SHP MR-ME-009 | 2027-10-21
8 | ALP-M15-00EKA-ME-MDB-0001 | Gas Receiving and Metering Station - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-07 | 2027-12-02 | G-PRC-SHP MR-ME-015 | 2027-10-21
8 | ALP-M20-00SGA-ME-OMM-0001 | Fire Pumps and Fire Protection Systems - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-15 | 2027-12-02 | G-COM-SC-FF 00SGA | 2028-07-24
8 | ALP-EPC-10LBA-IC-CEM-0001 | Main Steam Piping - Cause and Effect Matrix | NONE | IFR | A | no | 2027-10-29 | 2027-12-03
8 | ALP-M04-00PAA-ME-MDB-0001 | Travelling Band Screens and Trash Rakes - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-08 | 2027-12-03 | G-PRC-SHP MR-ME-004 | 2027-10-22
8 | ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | NONE | IFR | A | no | 2027-11-29 | 2027-12-06 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-EPC-10LBB-IC-CEM-0001 | Hot Reheat Piping - Cause and Effect Matrix | NONE | IFR | A | no | 2027-11-01 | 2027-12-06
8 | ALP-M05-00PBA-ME-MDB-0001 | Electro-Chlorination Package - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-11 | 2027-12-06 | G-PRC-SHP MR-ME-005 | 2027-10-25
8 | ALP-EPC-10LBC-IC-CEM-0001 | Cold Reheat Piping - Cause and Effect Matrix | NONE | IFR | A | no | 2027-11-03 | 2027-12-08
8 | ALP-EPC-20MAN-CM-OMM-0001 | Turbine Bypass Stations and Piping - Operating Procedures | NONE | IFR | A | no | 2027-11-10 | 2027-12-08 | G-COM-SC-WS 20MAN | 2028-09-25
8 | ALP-EPC-00000-EL-BLK-0002 | Cable Block Diagrams, Part 2 of 2 | NONE | IFR | A | no | 2027-11-04 | 2027-12-09
8 | ALP-I08-00CJG-ME-MDB-0001 | BOP Safety Instrumented System - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-14 | 2027-12-09 | G-PRC-SHP MR-IC-008 | 2027-10-28
8 | ALP-I09-00CKA-ME-TST-0001 | Operator Training Simulator, Historian and Performance Monitoring - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-10-28 | 2027-12-09 | G-PRC-FAT MR-IC-009 | 2028-01-20
8 | ALP-M07-00PGA-ME-OMM-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-22 | 2027-12-09 | G-COM-SC-FF 00PGA | 2028-07-24
8 | ALP-M08-00QEA-ME-OMM-0001 | Air Compressors and Dryers - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-22 | 2027-12-09 | G-COM-SC-FF 00QEA | 2028-07-24
8 | ALP-EPC-10LBD-IC-CEM-0001 | LP Steam Piping - Cause and Effect Matrix | NONE | IFR | A | no | 2027-11-05 | 2027-12-10
8 | ALP-M02-20LCB-ME-MDB-0001 | Condensate Extraction Pumps - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-18 | 2027-12-13 | G-PRC-SHP MR-ME-002 | 2027-11-01
8 | ALP-M18-10HSB-ME-OMM-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-26 | 2027-12-13 | G-COM-SC-FF 10HSB | 2028-07-24
8 | ALP-EPC-00EGB-PI-ISO-0001 | LDO Storage - Isometric Drawings | NONE | IFR | A | no | 2027-12-07 | 2027-12-14 | G-CON-CWP CWP-10-PI-01 | 2027-12-27
8 | ALP-EPC-20LCA-IC-CEM-0001 | Main Condensate Piping - Cause and Effect Matrix | NONE | IFR | A | no | 2027-11-09 | 2027-12-14
8 | ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | NONE | IFR | A | no | 2027-12-08 | 2027-12-15 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
8 | ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | NONE | IFR | A | no | 2027-12-09 | 2027-12-16 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings | NONE | IFR | A | no | 2027-12-09 | 2027-12-16 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings | NONE | IFR | A | no | 2027-12-09 | 2027-12-16 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-M16-00EGA-ME-OMM-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-29 | 2027-12-16 | G-COM-SC-FF 00EGA | 2028-07-24
8 | ALP-M21-00SMA-ME-OMM-0001 | EOT Cranes - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-29 | 2027-12-16 | G-COM-SC-FF 00SMA | 2028-07-24
8 | ALP-EPC-20LCB-IC-CEM-0001 | Condensate Extraction Pumps - Cause and Effect Matrix | NONE | IFR | A | no | 2027-11-15 | 2027-12-20
8 | ALP-M11-00QCA-ME-MDB-0001 | Chemical Dosing Skid - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-27 | 2027-12-22 | G-PRC-SHP MR-ME-011 | 2027-11-10
8 | ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings | NONE | IFR | A | no | 2027-12-16 | 2027-12-23 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-EPC-20MAN-IC-CEM-0001 | Turbine Bypass Stations and Piping - Cause and Effect Matrix | NONE | IFR | A | no | 2027-11-18 | 2027-12-23
8 | ALP-M10-00QJA-ME-OMM-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-10 | 2027-12-28 | G-COM-SC-FF 00QJA | 2028-07-24
8 | ALP-M03-00PAC-ME-MDB-0001 | CW Pumps - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-11-04 | 2027-12-30 | G-PRC-SHP MR-ME-003 | 2027-11-18
8 | ALP-EPC-00QUA-PI-ISO-0001 | Sampling and SWAS - Isometric Drawings | NONE | IFR | A | no | 2027-12-24 | 2027-12-31 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-I07-00CYA-ME-OMM-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-16 | 2028-01-03 | G-COM-SC-FF 00CYA | 2028-07-24
8 | ALP-EPC-00GBA-PI-ISO-0001 | Seawater Reverse Osmosis - Isometric Drawings | NONE | IFR | A | no | 2027-12-28 | 2028-01-04 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
8 | ALP-M06-00PAH-ME-OMM-0001 | Condenser Tube Cleaning System - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-18 | 2028-01-05 | G-COM-SC-FF 00PAH | 2028-07-24
8 | ALP-I09-00CKA-ME-PRC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-11-25 | 2028-01-06
8 | ALP-I02-00CQA-ME-OMM-0001 | Continuous Emission Monitoring System - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-20 | 2028-01-07 | G-COM-SC-FF 00CQA | 2028-07-24
8 | ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings | NONE | IFR | A | no | 2028-01-03 | 2028-01-10 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-I03-00QUA-ME-OMM-0001 | Steam/Water Analysis System - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-24 | 2028-01-11 | G-COM-SC-FF 00QUA | 2028-07-24
8 | ALP-EPC-00GCA-PI-ISO-0001 | Demineralisation - Isometric Drawings | NONE | IFR | A | no | 2028-01-06 | 2028-01-13 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
8 | ALP-M01-10LAC-ME-OMM-0001 | Boiler Feed Pumps - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-26 | 2028-01-13 | G-COM-SC-WS 10LAC | 2028-09-25
8 | ALP-M09-00QHA-ME-OMM-0001 | Auxiliary Boiler - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-26 | 2028-01-13 | G-COM-SC-FF 00QHA | 2028-07-24
8 | ALP-M12-00GBA-ME-MDB-0001 | Water Treatment Package - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-11-18 | 2028-01-13 | G-PRC-SHP MR-ME-012 | 2027-12-02
8 | ALP-M15-00EKA-ME-OMM-0001 | Gas Receiving and Metering Station - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-26 | 2028-01-13 | G-COM-SC-FF 00EKA | 2028-07-24
8 | ALP-M04-00PAA-ME-OMM-0001 | Travelling Band Screens and Trash Rakes - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-27 | 2028-01-14 | G-COM-SC-FF 00PAA | 2028-07-24
8 | ALP-M05-00PBA-ME-OMM-0001 | Electro-Chlorination Package - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-30 | 2028-01-17 | G-COM-SC-FF 00PBA | 2028-07-24
8 | ALP-EPC-00GNA-PI-ISO-0001 | Waste Water Treatment - Isometric Drawings | NONE | IFR | A | no | 2028-01-11 | 2028-01-18 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
8 | ALP-EPC-00LDA-PI-ISO-0001 | Condensate Polishing - Isometric Drawings | NONE | IFR | A | no | 2028-01-13 | 2028-01-20 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
8 | ALP-I08-00CJG-ME-OMM-0001 | BOP Safety Instrumented System - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-09-02 | 2028-01-20 | G-COM-SC-FF 00CJG | 2028-07-24
8 | ALP-EPC-00QJB-PI-ISO-0001 | Hydrogen and CO2 Supply - Isometric Drawings | NONE | IFR | A | no | 2028-01-17 | 2028-01-24 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-M02-20LCB-ME-OMM-0001 | Condensate Extraction Pumps - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-09-06 | 2028-01-24 | G-COM-SC-WS 20LCB | 2028-09-25
8 | ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings | NONE | IFR | A | no | 2028-01-19 | 2028-01-26 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings | NONE | IFR | A | no | 2028-01-19 | 2028-01-26 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
8 | ALP-EPC-00GHA-PI-ISO-0001 | Demineralised Water Storage and Distribution - Isometric Drawings | NONE | IFR | A | no | 2028-01-21 | 2028-01-28 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
8 | ALP-M11-00QCA-ME-OMM-0001 | Chemical Dosing Skid - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-09-15 | 2028-02-02 | G-COM-SC-FF 00QCA | 2028-07-24
8 | ALP-I09-00CKA-ME-TRP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Factory Acceptance Test Report | NONE | IFR | A | no | 2028-01-20 | 2028-02-03 | G-PRC-SHP MR-IC-009 | 2028-02-17
8 | ALP-EPC-00GUA-PI-ISO-0001 | Sanitary Waste Water Treatment - Isometric Drawings | NONE | IFR | A | no | 2028-02-01 | 2028-02-08 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
8 | ALP-M03-00PAC-ME-OMM-0001 | CW Pumps - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-09-23 | 2028-02-10 | G-COM-SC-FF 00PAC | 2028-07-24
8 | ALP-EPC-00PAH-PI-ISO-0001 | Condenser Tube Cleaning - Isometric Drawings | NONE | IFR | A | no | 2028-02-07 | 2028-02-14 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
8 | ALP-M12-00GBA-ME-OMM-0001 | Water Treatment Package - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-10-07 | 2028-02-24 | G-COM-SC-FF 00GBA | 2028-07-24
8 | ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings | NONE | IFR | A | no | 2028-02-25 | 2028-03-03 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
8 | ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings | NONE | IFR | A | no | 2028-03-01 | 2028-03-08 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
8 | ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings | NONE | IFR | A | no | 2028-03-02 | 2028-03-09 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
8 | ALP-I09-00CKA-ME-MDB-0001 | Operator Training Simulator, Historian and Performance Monitoring - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2028-02-03 | 2028-03-30 | G-PRC-SHP MR-IC-009 | 2028-02-17
8 | ALP-EPC-00EGA-CM-MDB-0001 | LDO Unloading - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00EGA | 2028-06-26
8 | ALP-EPC-00EGB-CM-MDB-0001 | LDO Storage - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00EGB | 2028-06-26
8 | ALP-EPC-00EGC-CM-MDB-0001 | LDO Forwarding and Treatment - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00EGC | 2028-06-26
8 | ALP-EPC-00EKA-CM-MDB-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00EKA | 2028-06-26
8 | ALP-EPC-00EKC-CM-MDB-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00EKC | 2028-06-26
8 | ALP-EPC-00GBA-CM-MDB-0001 | Seawater Reverse Osmosis - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00GBA | 2028-06-26
8 | ALP-EPC-00GCA-CM-MDB-0001 | Demineralisation - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00GCA | 2028-06-26
8 | ALP-EPC-00GHA-CM-MDB-0001 | Demineralised Water Storage and Distribution - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00GHA | 2028-06-26
8 | ALP-EPC-00GKA-CM-MDB-0001 | Potable Water - System Turnover Dossier | NONE | IFR | A | no | 2028-04-03 | 2028-04-10 | G-COM-MC-FF 00GKA | 2028-06-26
8 | ALP-EPC-00GMA-CM-MDB-0001 | Process Drains and Waste Water Collection - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00GMA | 2028-06-26
8 | ALP-EPC-00GNA-CM-MDB-0001 | Waste Water Treatment - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00GNA | 2028-06-26
8 | ALP-EPC-00GUA-CM-MDB-0001 | Sanitary Waste Water Treatment - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00GUA | 2028-06-26
8 | ALP-EPC-00LDA-CM-MDB-0001 | Condensate Polishing - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00LDA | 2028-06-26
8 | ALP-EPC-00PAA-CM-MDB-0001 | CW Intake, Screens and Outfall - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00PAA | 2028-06-26
8 | ALP-EPC-00PAB-CM-MDB-0001 | CW Piping - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00PAB | 2028-06-26
8 | ALP-EPC-00PAC-CM-MDB-0001 | CW Pumps - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00PAC | 2028-06-26
8 | ALP-EPC-00PAH-CM-MDB-0001 | Condenser Tube Cleaning - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00PAH | 2028-06-26
8 | ALP-EPC-00PBA-CM-MDB-0001 | Electro-Chlorination - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00PBA | 2028-06-26
8 | ALP-EPC-00PGA-CM-MDB-0001 | Closed Cooling Water - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00PGA | 2028-06-26
8 | ALP-EPC-00QCA-CM-MDB-0001 | Chemical Dosing - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00QCA | 2028-06-26
8 | ALP-EPC-00QEA-CM-MDB-0001 | Compressed Air - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00QEA | 2028-06-26
8 | ALP-EPC-00QHA-CM-MDB-0001 | Auxiliary Boiler - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00QHA | 2028-06-26
8 | ALP-EPC-00QJA-CM-MDB-0001 | Nitrogen Supply - System Turnover Dossier | NONE | IFR | A | no | 2028-04-17 | 2028-04-24 | G-COM-MC-FF 00QJA | 2028-06-26
8 | ALP-EPC-00QJB-CM-MDB-0001 | Hydrogen and CO2 Supply - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 00QJB | 2028-06-26
8 | ALP-EPC-00QUA-CM-MDB-0001 | Sampling and SWAS - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 00QUA | 2028-06-26
8 | ALP-EPC-00SAA-CM-MDB-0001 | HVAC - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 00SAA | 2028-06-26
8 | ALP-EPC-00SGA-CM-MDB-0001 | Fire Water System - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 00SGA | 2028-06-26
8 | ALP-EPC-00SGC-CM-MDB-0001 | Deluge, Spray and Foam Systems - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 00SGC | 2028-06-26
8 | ALP-EPC-10HSB-CM-MDB-0001 | Ammonia Storage and Supply - System Turnover Dossier | NONE | IFR | A | no | 2028-05-01 | 2028-05-08 | G-COM-MC-FF 10HSB | 2028-06-26
8 | ALP-I09-00CKA-ME-OMM-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-12-23 | 2028-05-11 | G-COM-SC-FF 00CKA | 2028-07-24
8 | ALP-EPC-00LBG-CM-MDB-0001 | Auxiliary Steam - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 00LBG | 2028-08-28
8 | ALP-EPC-10HAN-CM-MDB-0001 | HRSG Blowdown and Drains - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10HAN | 2028-08-28
8 | ALP-EPC-10LAB-CM-MDB-0001 | Feedwater Piping - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10LAB | 2028-08-28
8 | ALP-EPC-10LAC-CM-MDB-0001 | Boiler Feed Pumps - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10LAC | 2028-08-28
8 | ALP-EPC-10LAE-CM-MDB-0001 | HP Attemperation Spray Water - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10LAE | 2028-08-28
8 | ALP-EPC-10LAF-CM-MDB-0001 | Reheat Attemperation Spray Water - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10LAF | 2028-08-28
8 | ALP-EPC-10LBA-CM-MDB-0001 | Main Steam Piping - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10LBA | 2028-08-28
8 | ALP-EPC-10LBB-CM-MDB-0001 | Hot Reheat Piping - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10LBB | 2028-08-28
8 | ALP-EPC-10LBC-CM-MDB-0001 | Cold Reheat Piping - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10LBC | 2028-08-28
8 | ALP-EPC-10LBD-CM-MDB-0001 | LP Steam Piping - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 10LBD | 2028-08-28
8 | ALP-EPC-20LCA-CM-MDB-0001 | Main Condensate Piping - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 20LCA | 2028-08-28
8 | ALP-EPC-20LCB-CM-MDB-0001 | Condensate Extraction Pumps - System Turnover Dossier | NONE | IFR | A | no | 2028-06-05 | 2028-06-12 | G-COM-MC-WS 20LCB | 2028-08-28
8 | ALP-EPC-20MAN-CM-MDB-0001 | Turbine Bypass Stations and Piping - System Turnover Dossier | NONE | IFR | A | no | 2028-06-19 | 2028-06-26 | G-COM-MC-WS 20MAN | 2028-08-28
8 | ALP-EPC-00000-CM-TRP-0007 | Fire Protection System Test Certificates | NONE | IFR | A | no | 2028-07-11 | 2028-08-01 | G-OWN-TO 00000 | 2029-04-18
8 | ALP-EPC-00000-EL-TRP-0001 | Revenue Metering and TSO SCADA Interface Test Report | NONE | IFR | A | no | 2028-07-11 | 2028-08-01 | G-OWN-TO 00000 | 2029-04-18
9 | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-EL-011 | 2026-11-09
9 | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-EL-003 | 2026-12-07
9 | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-EL-005 | 2027-01-18
9 | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-EL-006 | 2026-12-07
9 | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-EL-002 | 2027-01-25
9 | ALP-EPC-00000-GE-ITP-0001 | Construction Power Supply - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-02 | 2026-11-09 | G-PRC-PO MR-EL-011 | 2026-11-16
9 | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | NONE | IFR | A | no | 2026-11-23 | 2026-11-26 | G-PRC-ENQ MR-EL-004 | 2027-03-22
9 | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | NONE | IFR | A | no | 2026-11-23 | 2026-11-26 | G-PRC-ENQ MR-EL-007 | 2027-03-22
9 | ALP-EPC-00ACA-EL-DSH-0001 | 380 kV GIS Switchyard: Switchgear - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
9 | ALP-EPC-00CJA-IC-DSH-0001 | Plant DCS: Control Systems - Datasheet | NONE | IFR | A | no | 2026-11-02 | 2026-11-30
9 | ALP-EPC-00ACA-EL-ITP-0001 | 380 kV GIS - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-EL-001 | 2026-12-15
9 | ALP-EPC-00CJA-IC-ITP-0001 | Plant DCS - Inspection and Test Plan | NONE | IFR | A | no | 2026-11-16 | 2026-12-14 | G-PRC-PO MR-IC-001 | 2027-02-15
9 | ALP-EPC-00UZA-EL-CBL-0001 | Site-Wide Infrastructure - Cable Schedule and Routing | NONE | IFR | A | no | 2027-02-26 | 2027-03-05 | G-CON-CWP CWP-12-EL-01 | 2027-05-17
9 | ALP-EPC-00UBA-EL-CBL-0001 | Electrical Building and Emergency Power - Cable Schedule and Routing | NONE | IFR | A | no | 2027-03-08 | 2027-03-15 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
9 | ALP-EPC-00UCA-EL-CBL-0001 | Control, Administration and Workshop Buildings - Cable Schedule and Routing | NONE | IFR | A | no | 2027-03-18 | 2027-03-25 | G-CON-CWP CWP-11-EL-01 | 2027-11-08
9 | ALP-EPC-00BBA-EL-WIR-0001 | MV Schematic and Wiring Diagrams | NONE | IFR | A | no | 2027-04-26 | 2027-05-03 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
9 | ALP-EPC-00UGA-CV-EFD-0001 | Water Treatment Building and Basins - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-04-27 | 2027-06-01 | G-CON-CWP CWP-07-CV-01 | 2027-04-05
9 | ALP-EPC-00UPC-CV-EFD-0001 | CW Pump House - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-04-30 | 2027-06-04 | G-CON-CWP CWP-05-CV-01 | 2027-03-25
9 | ALP-EPC-00SGY-GE-RPT-0001 | Fire Detection and Alarm System - Technical Bid Evaluation | NONE | IFR | A | no | 2027-05-31 | 2027-06-07 | G-PRC-PO MR-IC-006 | 2027-07-19
9 | ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-05-03 | 2027-06-07 | G-CON-CWP CWP-08-CV-01 | 2027-05-04
9 | ALP-EPC-00000-GE-RPT-0005 | Electrical and I&C Installation - Technical Bid Evaluation | NONE | IFR | A | no | 2027-06-09 | 2027-06-16 | G-PRC-PO MR-EL-012 | 2027-11-22
9 | ALP-EPC-10UHA-CV-EFD-0001 | HRSG Foundations and Structures - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-05-12 | 2027-06-16 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
9 | ALP-EPC-10UMA-CV-EFD-0001 | Gas Turbine Hall - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-05-12 | 2027-06-16 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
9 | ALP-EPC-00UEG-CV-EFD-0001 | LDO Tank Farm Structures - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-05-19 | 2027-06-23 | G-CON-CWP CWP-10-CV-01 | 2027-06-03
9 | ALP-EPC-20UMB-CV-EFD-0001 | Steam Turbine Hall - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-05-24 | 2027-06-28 | G-CON-CWP CWP-02-CV-02 | 2027-04-19
9 | ALP-I06-00SGY-ME-ITP-0001 | Fire Detection and Alarm System - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-06-14 | 2027-06-28 | G-PRC-FAB MR-IC-006 | 2027-09-13
9 | ALP-I06-00SGY-ME-DSH-0001 | Fire Detection and Alarm System - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-06-14 | 2027-07-05 | G-PRC-FAB MR-IC-006 | 2027-09-13
9 | ALP-E12-00000-GE-ITP-0001 | Electrical and I&C Installation - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-06-23 | 2027-07-07
9 | ALP-E12-00000-GE-MOS-0001 | Electrical and I&C Installation - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-06-23 | 2027-07-07
9 | ALP-E12-00000-GE-MOS-0002 | Electrical and I&C Installation - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-06-23 | 2027-07-07
9 | ALP-E12-00000-GE-MOS-0003 | Electrical and I&C Installation - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-06-23 | 2027-07-07
9 | ALP-E12-00000-GE-MOS-0004 | Electrical and I&C Installation - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-06-23 | 2027-07-07
9 | ALP-E12-00000-GE-MOS-0005 | Electrical and I&C Installation - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-06-23 | 2027-07-07
9 | ALP-E12-00000-GE-MOS-0006 | Electrical and I&C Installation - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-06-23 | 2027-07-07
9 | ALP-I06-00SGY-ME-GAD-0001 | Fire Detection and Alarm System - Supplier GA Drawings | NONE | IFR | A | no | 2027-06-21 | 2027-07-12 | G-PRC-FAB MR-IC-006 | 2027-09-13
9 | ALP-I06-00SGY-IC-IOL-0001 | Fire Detection and Alarm System - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-06-28 | 2027-07-19
9 | ALP-I06-00SGY-ME-CAL-0001 | Fire Detection and Alarm System - Supplier Design Calculations | NONE | IFR | A | no | 2027-06-28 | 2027-07-19 | G-PRC-FAB MR-IC-006 | 2027-09-13
9 | ALP-EPC-00UEK-CV-EFD-0001 | Gas Station Structures - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-06-22 | 2027-07-27 | G-CON-CWP CWP-09-CV-01 | 2027-08-04
9 | ALP-I06-00SGY-EL-WIR-0001 | Fire Detection and Alarm System - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-07-05 | 2027-08-02 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
9 | ALP-I06-00SGY-ME-LST-0001 | Fire Detection and Alarm System - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-07-12 | 2027-08-09
9 | ALP-I06-00SGY-ME-TST-0001 | Fire Detection and Alarm System - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-28 | 2027-08-09 | G-PRC-FAT MR-IC-006 | 2027-09-20
9 | ALP-EPC-00UEK-EL-CBL-0001 | Fuel Gas Station - Cable Schedule and Routing | NONE | IFR | A | no | 2027-08-18 | 2027-08-25 | G-CON-CWP CWP-09-EL-01 | 2027-12-27
9 | ALP-EPC-00UZF-GE-RPT-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Bid Evaluation | NONE | IFR | A | no | 2027-08-30 | 2027-09-06 | G-PRC-PO MR-ME-024 | 2027-11-15
9 | ALP-I06-00SGY-ME-PRC-0001 | Fire Detection and Alarm System - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-26 | 2027-09-06 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
9 | ALP-EPC-00UEG-EL-CBL-0001 | LDO Tank Farm and Unloading - Cable Schedule and Routing | NONE | IFR | A | no | 2027-09-07 | 2027-09-14 | G-CON-CWP CWP-10-EL-01 | 2028-01-24
9 | ALP-EPC-00UAC-EL-CBL-0001 | 380 kV GIS Switchyard - Cable Schedule and Routing | NONE | IFR | A | no | 2027-09-09 | 2027-09-16 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
9 | ALP-EPC-00GMA-PI-SUP-0001 | Process Drains and Waste Water Collection - Pipe Support Drawings | NONE | IFR | A | no | 2027-09-14 | 2027-09-21 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
9 | ALP-EPC-00UPC-EL-CBL-0001 | CW Pump House and Onshore CW - Cable Schedule and Routing | NONE | IFR | A | no | 2027-09-16 | 2027-09-23 | G-CON-CWP CWP-05-EL-01 | 2028-01-31
9 | ALP-M24-00UZF-GE-ITP-0001 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Inspection and Test Plans | NONE | IFR | A | no | 2027-09-13 | 2027-09-27
9 | ALP-M24-00UZF-GE-MOS-0001 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 1 of 6 | NONE | IFR | A | no | 2027-09-13 | 2027-09-27
9 | ALP-M24-00UZF-GE-MOS-0002 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 2 of 6 | NONE | IFR | A | no | 2027-09-13 | 2027-09-27
9 | ALP-M24-00UZF-GE-MOS-0003 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 3 of 6 | NONE | IFR | A | no | 2027-09-13 | 2027-09-27
9 | ALP-M24-00UZF-GE-MOS-0004 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 4 of 6 | NONE | IFR | A | no | 2027-09-13 | 2027-09-27
9 | ALP-M24-00UZF-GE-MOS-0005 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 5 of 6 | NONE | IFR | A | no | 2027-09-13 | 2027-09-27
9 | ALP-M24-00UZF-GE-MOS-0006 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 6 of 6 | NONE | IFR | A | no | 2027-09-13 | 2027-09-27
9 | ALP-EPC-00UQA-EL-CBL-0001 | BOP Utilities - Cable Schedule and Routing | NONE | IFR | A | no | 2027-09-21 | 2027-09-28 | G-CON-CWP CWP-08-EL-01 | 2028-01-10
9 | ALP-EPC-00PAA-PI-SUP-0001 | CW Intake, Screens and Outfall - Pipe Support Drawings | NONE | IFR | A | no | 2027-09-22 | 2027-09-29 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
9 | ALP-EPC-00PAC-PI-SUP-0001 | CW Pumps - Pipe Support Drawings | NONE | IFR | A | no | 2027-09-22 | 2027-09-29 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
9 | ALP-EPC-00GKA-PI-SUP-0001 | Potable Water - Pipe Support Drawings | NONE | IFR | A | no | 2027-09-23 | 2027-09-30 | G-CON-CWP CWP-12-PI-01 | 2027-07-12
9 | ALP-EPC-00UGA-EL-CBL-0001 | Water Treatment and Effluents - Cable Schedule and Routing | NONE | IFR | A | no | 2027-09-24 | 2027-10-01 | G-CON-CWP CWP-07-EL-01 | 2028-02-21
9 | ALP-EPC-10UMA-EL-CBL-0001 | Power Block - GT and HRSG - Cable Schedule and Routing | NONE | IFR | A | no | 2027-09-27 | 2027-10-04 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
9 | ALP-I06-00SGY-ME-TRP-0001 | Fire Detection and Alarm System - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-20 | 2027-10-04 | G-PRC-SHP MR-IC-006 | 2027-10-18
9 | ALP-EPC-00PAB-PI-SUP-0001 | CW Piping - Pipe Support Drawings | NONE | IFR | A | no | 2027-09-29 | 2027-10-06 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
9 | ALP-EPC-00PBA-PI-SUP-0001 | Electro-Chlorination - Pipe Support Drawings | NONE | IFR | A | no | 2027-10-01 | 2027-10-08 | G-CON-CWP CWP-05-PI-01 | 2027-09-20
9 | ALP-EPC-20UMB-EL-CBL-0001 | Power Block - ST and Condenser - Cable Schedule and Routing | NONE | IFR | A | no | 2027-10-11 | 2027-10-18 | G-CON-CWP CWP-02-EL-01 | 2028-02-28
9 | ALP-EPC-00000-EL-LST-0003 | Protection Relay Settings List | NONE | IFR | A | no | 2027-09-29 | 2027-10-27 | G-OWN-TO 00000 | 2029-04-18
9 | ALP-I06-00SGY-ME-MDB-0001 | Fire Detection and Alarm System - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-04 | 2027-11-29 | G-PRC-SHP MR-IC-006 | 2027-10-18
9 | ALP-EPC-00EKA-PI-SUP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Support Drawings | NONE | IFR | A | no | 2027-11-24 | 2027-12-01 | G-CON-CWP CWP-09-PI-01 | 2027-11-29
9 | ALP-EPC-00EKC-PI-SUP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Support Drawings | NONE | IFR | A | no | 2027-12-03 | 2027-12-10 | G-CON-CWP CWP-09-PI-01 | 2027-11-29
9 | ALP-I06-00SGY-ME-OMM-0001 | Fire Detection and Alarm System - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-08-23 | 2028-01-10 | G-COM-SC-FF 00SGY | 2028-07-24
9 | ALP-EPC-00EGA-PI-SUP-0001 | LDO Unloading - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-14 | 2028-01-21 | G-CON-CWP CWP-10-PI-01 | 2027-12-27
9 | ALP-EPC-00QCA-PI-SUP-0001 | Chemical Dosing - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-14 | 2028-01-21 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-00QJA-PI-SUP-0001 | Nitrogen Supply - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-14 | 2028-01-21 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-10HSB-PI-SUP-0001 | Ammonia Storage and Supply - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-14 | 2028-01-21 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-00EGB-PI-SUP-0001 | LDO Storage - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-17 | 2028-01-24 | G-CON-CWP CWP-10-PI-01 | 2027-12-27
9 | ALP-EPC-10LAC-PI-SUP-0001 | Boiler Feed Pumps - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-18 | 2028-01-25 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-00EGC-PI-SUP-0001 | LDO Forwarding and Treatment - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-19 | 2028-01-26 | G-CON-CWP CWP-10-PI-01 | 2027-12-27
9 | ALP-EPC-00LBG-PI-SUP-0001 | Auxiliary Steam - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-19 | 2028-01-26 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-00QHA-PI-SUP-0001 | Auxiliary Boiler - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-19 | 2028-01-26 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-00PGA-PI-SUP-0001 | Closed Cooling Water - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-20 | 2028-01-27 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-00QEA-PI-SUP-0001 | Compressed Air - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-20 | 2028-01-27 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-00SGA-PI-SUP-0001 | Fire Water System - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-20 | 2028-01-27 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-00SGC-PI-SUP-0001 | Deluge, Spray and Foam Systems - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-20 | 2028-01-27 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-10LAB-PI-SUP-0001 | Feedwater Piping - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-20 | 2028-01-27 | G-CON-CWP CWP-08-PI-01 | 2027-12-13
9 | ALP-EPC-10HAN-PI-SUP-0001 | HRSG Blowdown and Drains - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-26 | 2028-02-02 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-10LBA-PI-SUP-0001 | Main Steam Piping - Pipe Support Drawings | NONE | IFR | A | no | 2028-01-27 | 2028-02-03 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-10LBC-PI-SUP-0001 | Cold Reheat Piping - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-01 | 2028-02-08 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-10LBB-PI-SUP-0001 | Hot Reheat Piping - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-02 | 2028-02-09 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-00QUA-PI-SUP-0001 | Sampling and SWAS - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-07 | 2028-02-14 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-10LBD-PI-SUP-0001 | LP Steam Piping - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-11 | 2028-02-18 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-00GBA-PI-SUP-0001 | Seawater Reverse Osmosis - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-14 | 2028-02-21 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
9 | ALP-EPC-00GCA-PI-SUP-0001 | Demineralisation - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-18 | 2028-02-25 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
9 | ALP-EPC-00QJB-PI-SUP-0001 | Hydrogen and CO2 Supply - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-21 | 2028-02-28 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-00GNA-PI-SUP-0001 | Waste Water Treatment - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-23 | 2028-03-01 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
9 | ALP-EPC-10LAE-PI-SUP-0001 | HP Attemperation Spray Water - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-23 | 2028-03-01 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-10LAF-PI-SUP-0001 | Reheat Attemperation Spray Water - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-23 | 2028-03-01 | G-CON-CWP CWP-01-PI-01 | 2027-12-13
9 | ALP-EPC-00LDA-PI-SUP-0001 | Condensate Polishing - Pipe Support Drawings | NONE | IFR | A | no | 2028-02-25 | 2028-03-03 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
9 | ALP-EPC-00GHA-PI-SUP-0001 | Demineralised Water Storage and Distribution - Pipe Support Drawings | NONE | IFR | A | no | 2028-03-02 | 2028-03-09 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
9 | ALP-EPC-00GUA-PI-SUP-0001 | Sanitary Waste Water Treatment - Pipe Support Drawings | NONE | IFR | A | no | 2028-03-03 | 2028-03-10 | G-CON-CWP CWP-07-PI-01 | 2028-01-24
9 | ALP-EPC-00PAH-PI-SUP-0001 | Condenser Tube Cleaning - Pipe Support Drawings | NONE | IFR | A | no | 2028-03-13 | 2028-03-20 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
9 | ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | NONE | IFR | A | no | 2028-03-23 | 2028-04-13 | G-OPS-AB 00000 | 2029-07-18
9 | ALP-EPC-20LCB-PI-SUP-0001 | Condensate Extraction Pumps - Pipe Support Drawings | NONE | IFR | A | no | 2028-04-07 | 2028-04-14 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
9 | ALP-EPC-20MAN-PI-SUP-0001 | Turbine Bypass Stations and Piping - Pipe Support Drawings | NONE | IFR | A | no | 2028-04-14 | 2028-04-21 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
9 | ALP-EPC-20LCA-PI-SUP-0001 | Main Condensate Piping - Pipe Support Drawings | NONE | IFR | A | no | 2028-04-20 | 2028-04-27 | G-CON-CWP CWP-02-PI-01 | 2028-01-31
9 | ALP-EPC-00000-CM-TRP-0003 | Grid Code Compliance Test Report | NONE | IFR | A | no | 2029-02-05 | 2029-02-26 | G-OWN-TO 00000 | 2029-04-18
10 | ALP-E11-00000-ME-TST-0001 | Construction Power Supply - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2026-11-02 | 2026-11-02 | G-PRC-FAT MR-EL-011 | 2026-12-14
10 | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-EL-001 | 2026-12-15
10 | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | NONE | IFR | A | no | 2026-11-02 | 2026-11-05 | G-PRC-ENQ MR-IC-001 | 2026-11-30
10 | ALP-EPC-00000-GE-RPT-0004 | Construction Power Supply - Technical Bid Evaluation | NONE | IFR | A | no | 2026-11-02 | 2026-11-09 | G-PRC-PO MR-EL-011 | 2026-11-16
10 | ALP-E11-00000-ME-PRC-0001 | Construction Power Supply - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2026-11-02 | 2026-11-30 | G-CON-CWP CWP-12-CV-01 | 2027-01-18
10 | ALP-E11-00000-ME-ITP-0001 | Construction Power Supply - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2026-11-23 | 2026-12-07 | G-PRC-FAB MR-EL-011 | 2026-12-08
10 | ALP-E11-00000-ME-TRP-0001 | Construction Power Supply - Factory Acceptance Test Report | NONE | IFR | A | no | 2026-12-14 | 2026-12-28 | G-PRC-SHP MR-EL-011 | 2027-01-11
10 | ALP-E11-00000-IC-IOL-0001 | Construction Power Supply - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2026-12-14 | 2027-01-04
10 | ALP-EPC-00BBA-GE-RPT-0001 | MV Switchgear 10.5 kV - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-07 | 2027-01-14 | G-PRC-PO MR-EL-003 | 2027-02-15
10 | ALP-EPC-00XJA-GE-RPT-0001 | Emergency Diesel Generator - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-07 | 2027-01-14 | G-PRC-PO MR-EL-006 | 2027-02-15
10 | ALP-E11-00000-ME-LST-0001 | Construction Power Supply - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2026-12-28 | 2027-01-25 | G-OWN-TO 00000 | 2029-04-18
10 | ALP-EPC-00BFA-GE-RPT-0001 | LV Switchboards and MCCs - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-04 | 2027-02-11 | G-PRC-PO MR-EL-005 | 2027-03-29
10 | ALP-E11-00000-ME-MDB-0001 | Construction Power Supply - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2026-12-28 | 2027-02-22 | G-PRC-SHP MR-EL-011 | 2027-01-11
10 | ALP-EPC-10BBT-GE-RPT-0001 | Unit Auxiliary Transformers - Technical Bid Evaluation | NONE | IFR | A | no | 2027-02-18 | 2027-02-25 | G-PRC-PO MR-EL-002 | 2027-04-05
10 | ALP-E03-00BBA-ME-ITP-0001 | MV Switchgear 10.5 kV - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-09 | 2027-03-05 | G-PRC-FAB MR-EL-003 | 2027-05-26
10 | ALP-E06-00XJA-ME-ITP-0001 | Emergency Diesel Generator - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-09 | 2027-03-05 | G-PRC-FAB MR-EL-006 | 2027-05-26
10 | ALP-EPC-00BFT-GE-RPT-0001 | LV Transformers - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-02 | 2027-03-09 | G-PRC-PO MR-EL-004 | 2027-05-10
10 | ALP-EPC-00BRA-GE-RPT-0001 | UPS, Batteries and DC Systems - Technical Bid Evaluation | NONE | IFR | A | no | 2027-03-10 | 2027-03-17 | G-PRC-PO MR-EL-007 | 2027-05-10
10 | ALP-E03-00BBA-ME-DSH-0001 | MV Switchgear 10.5 kV - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-09 | 2027-03-18 | G-PRC-FAB MR-EL-003 | 2027-05-26
10 | ALP-E05-00BFA-ME-ITP-0001 | LV Switchboards and MCCs - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-25 | 2027-03-18 | G-PRC-FAB MR-EL-005 | 2027-06-21
10 | ALP-E06-00XJA-CV-CAL-0001 | Emergency Diesel Generator - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-02-22 | 2027-03-18 | G-PRC-FAB MR-EL-006 | 2027-05-26
10 | ALP-E06-00XJA-ME-DSH-0001 | Emergency Diesel Generator - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-09 | 2027-03-18 | G-PRC-FAB MR-EL-006 | 2027-05-26
10 | ALP-E05-00BFA-ME-DSH-0001 | LV Switchboards and MCCs - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-25 | 2027-03-30 | G-PRC-FAB MR-EL-005 | 2027-06-21
10 | ALP-E03-00BBA-ME-GAD-0001 | MV Switchgear 10.5 kV - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-22 | 2027-03-31 | G-PRC-FAB MR-EL-003 | 2027-05-26
10 | ALP-E06-00XJA-ME-GAD-0001 | Emergency Diesel Generator - Supplier GA Drawings | NONE | IFR | A | no | 2027-02-22 | 2027-03-31 | G-PRC-FAB MR-EL-006 | 2027-05-26
10 | ALP-E11-00000-ME-OMM-0001 | Construction Power Supply - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2026-11-16 | 2027-04-05
10 | ALP-E04-00BFT-ME-ITP-0001 | LV Transformers - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-19 | 2027-04-07 | G-PRC-FAB MR-EL-004 | 2027-07-21
10 | ALP-E05-00BFA-ME-GAD-0001 | LV Switchboards and MCCs - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-08 | 2027-04-08 | G-PRC-FAB MR-EL-005 | 2027-06-21
10 | ALP-E03-00BBA-IC-IOL-0001 | MV Switchgear 10.5 kV - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-05 | 2027-04-13
10 | ALP-E03-00BBA-ME-CAL-0001 | MV Switchgear 10.5 kV - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-05 | 2027-04-13 | G-PRC-FAB MR-EL-003 | 2027-05-26
10 | ALP-E06-00XJA-IC-IOL-0001 | Emergency Diesel Generator - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-05 | 2027-04-13
10 | ALP-E06-00XJA-ME-CAL-0001 | Emergency Diesel Generator - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-05 | 2027-04-13 | G-PRC-FAB MR-EL-006 | 2027-05-26
10 | ALP-E02-10BBT-ME-ITP-0001 | Unit Auxiliary Transformers - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-18 | 2027-04-15 | G-PRC-FAB MR-EL-002 | 2027-07-26
10 | ALP-E04-00BFT-ME-DSH-0001 | LV Transformers - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-19 | 2027-04-15 | G-PRC-FAB MR-EL-004 | 2027-07-21
10 | ALP-E07-00BRA-ME-ITP-0001 | UPS, Batteries and DC Systems - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-03-29 | 2027-04-15 | G-PRC-FAB MR-EL-007 | 2027-07-21
10 | ALP-E05-00BFA-IC-IOL-0001 | LV Switchboards and MCCs - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-18 | 2027-04-19
10 | ALP-E05-00BFA-ME-CAL-0001 | LV Switchboards and MCCs - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-18 | 2027-04-19 | G-PRC-FAB MR-EL-005 | 2027-06-21
10 | ALP-E07-00BRA-ME-DSH-0001 | UPS, Batteries and DC Systems - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-29 | 2027-04-23 | G-PRC-FAB MR-EL-007 | 2027-07-21
10 | ALP-E04-00BFT-ME-GAD-0001 | LV Transformers - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-30 | 2027-04-26 | G-PRC-FAB MR-EL-004 | 2027-07-21
10 | ALP-E02-10BBT-CV-CAL-0001 | Unit Auxiliary Transformers - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-04-01 | 2027-04-29 | G-PRC-FAB MR-EL-002 | 2027-07-26
10 | ALP-E02-10BBT-ME-DSH-0001 | Unit Auxiliary Transformers - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-03-18 | 2027-04-29 | G-PRC-FAB MR-EL-002 | 2027-07-26
10 | ALP-E07-00BRA-ME-GAD-0001 | UPS, Batteries and DC Systems - Supplier GA Drawings | NONE | IFR | A | no | 2027-04-07 | 2027-05-04 | G-PRC-FAB MR-EL-007 | 2027-07-21
10 | ALP-E04-00BFT-IC-IOL-0001 | LV Transformers - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-07 | 2027-05-05
10 | ALP-E04-00BFT-ME-CAL-0001 | LV Transformers - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-07 | 2027-05-05 | G-PRC-FAB MR-EL-004 | 2027-07-21
10 | ALP-E06-00XJA-EL-WIR-0001 | Emergency Diesel Generator - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-18 | 2027-05-07 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
10 | ALP-E06-00XJA-IC-DSH-0001 | Emergency Diesel Generator - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-03-18 | 2027-05-07
10 | ALP-E05-00BFA-EL-WIR-0001 | LV Switchboards and MCCs - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-03-30 | 2027-05-11 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
10 | ALP-E02-10BBT-ME-GAD-0001 | Unit Auxiliary Transformers - Supplier GA Drawings | NONE | IFR | A | no | 2027-04-01 | 2027-05-13 | G-PRC-FAB MR-EL-002 | 2027-07-26
10 | ALP-E07-00BRA-IC-IOL-0001 | UPS, Batteries and DC Systems - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-15 | 2027-05-13
10 | ALP-E07-00BRA-ME-CAL-0001 | UPS, Batteries and DC Systems - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-15 | 2027-05-13 | G-PRC-FAB MR-EL-007 | 2027-07-21
10 | ALP-E03-00BBA-ME-LST-0001 | MV Switchgear 10.5 kV - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-03-31 | 2027-05-20
10 | ALP-E05-00BFA-ME-LST-0001 | LV Switchboards and MCCs - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-08 | 2027-05-20
10 | ALP-E06-00XJA-ME-LST-0001 | Emergency Diesel Generator - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-03-31 | 2027-05-20
10 | ALP-E02-10BBT-IC-IOL-0001 | Unit Auxiliary Transformers - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-04-15 | 2027-05-27
10 | ALP-E02-10BBT-ME-CAL-0001 | Unit Auxiliary Transformers - Supplier Design Calculations | NONE | IFR | A | no | 2027-04-15 | 2027-05-27 | G-PRC-FAB MR-EL-002 | 2027-07-26
10 | ALP-E04-00BFT-ME-LST-0001 | LV Transformers - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-26 | 2027-06-01
10 | ALP-E07-00BRA-EL-WIR-0001 | UPS, Batteries and DC Systems - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-23 | 2027-06-01 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
10 | ALP-E07-00BRA-ME-LST-0001 | UPS, Batteries and DC Systems - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-05-04 | 2027-06-09
10 | ALP-E04-00BFT-ME-TST-0001 | LV Transformers - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-11 | 2027-06-22 | G-PRC-FAT MR-EL-004 | 2027-08-03
10 | ALP-E02-10BBT-EL-WIR-0001 | Unit Auxiliary Transformers - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-29 | 2027-06-24 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
10 | ALP-E02-10BBT-IC-DSH-0001 | Unit Auxiliary Transformers - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-04-29 | 2027-06-24
10 | ALP-E05-00BFA-ME-TST-0001 | LV Switchboards and MCCs - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-13 | 2027-06-24 | G-PRC-FAT MR-EL-005 | 2027-08-05
10 | ALP-E07-00BRA-ME-TST-0001 | UPS, Batteries and DC Systems - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-05-19 | 2027-06-30 | G-PRC-FAT MR-EL-007 | 2027-08-11
10 | ALP-E02-10BBT-ME-LST-0001 | Unit Auxiliary Transformers - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-05-13 | 2027-07-08
10 | ALP-E03-00BBA-ME-TST-0001 | MV Switchgear 10.5 kV - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-03 | 2027-07-15 | G-PRC-FAT MR-EL-003 | 2027-08-26
10 | ALP-E06-00XJA-ME-TST-0001 | Emergency Diesel Generator - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-06-03 | 2027-07-15 | G-PRC-FAT MR-EL-006 | 2027-08-26
10 | ALP-E04-00BFT-ME-PRC-0001 | LV Transformers - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-08 | 2027-07-20 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
10 | ALP-E05-00BFA-ME-PRC-0001 | LV Switchboards and MCCs - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-10 | 2027-07-22 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
10 | ALP-E07-00BRA-ME-PRC-0001 | UPS, Batteries and DC Systems - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-06-16 | 2027-07-28 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
10 | ALP-E03-00BBA-ME-PRC-0001 | MV Switchgear 10.5 kV - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-01 | 2027-08-12 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
10 | ALP-E06-00XJA-ME-PRC-0001 | Emergency Diesel Generator - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-07-01 | 2027-08-12 | G-CON-CWP CWP-03-EL-01 | 2027-10-25
10 | ALP-E04-00BFT-ME-TRP-0001 | LV Transformers - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-03 | 2027-08-17 | G-PRC-SHP MR-EL-004 | 2027-08-31
10 | ALP-E05-00BFA-ME-TRP-0001 | LV Switchboards and MCCs - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-05 | 2027-08-19 | G-PRC-SHP MR-EL-005 | 2027-09-02
10 | ALP-E07-00BRA-ME-TRP-0001 | UPS, Batteries and DC Systems - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-11 | 2027-08-25 | G-PRC-SHP MR-EL-007 | 2027-09-08
10 | ALP-E03-00BBA-ME-TRP-0001 | MV Switchgear 10.5 kV - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-26 | 2027-09-09 | G-PRC-SHP MR-EL-003 | 2027-09-23
10 | ALP-E06-00XJA-ME-TRP-0001 | Emergency Diesel Generator - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-08-26 | 2027-09-09 | G-PRC-SHP MR-EL-006 | 2027-09-23
10 | ALP-E02-10BBT-ME-TST-0001 | Unit Auxiliary Transformers - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-08-05 | 2027-09-16 | G-PRC-FAT MR-EL-002 | 2027-10-28
10 | ALP-E04-00BFT-ME-MDB-0001 | LV Transformers - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-17 | 2027-10-12 | G-PRC-SHP MR-EL-004 | 2027-08-31
10 | ALP-E02-10BBT-ME-PRC-0001 | Unit Auxiliary Transformers - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-09-02 | 2027-10-14 | G-CON-CWP CWP-01-EL-01 | 2028-01-10
10 | ALP-E05-00BFA-ME-MDB-0001 | LV Switchboards and MCCs - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-19 | 2027-10-14 | G-PRC-SHP MR-EL-005 | 2027-09-02
10 | ALP-E07-00BRA-ME-MDB-0001 | UPS, Batteries and DC Systems - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-08-25 | 2027-10-20 | G-PRC-SHP MR-EL-007 | 2027-09-08
10 | ALP-E03-00BBA-ME-MDB-0001 | MV Switchgear 10.5 kV - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-09 | 2027-11-04 | G-PRC-SHP MR-EL-003 | 2027-09-23
10 | ALP-E06-00XJA-ME-MDB-0001 | Emergency Diesel Generator - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-09-09 | 2027-11-04 | G-PRC-SHP MR-EL-006 | 2027-09-23
10 | ALP-E02-10BBT-ME-TRP-0001 | Unit Auxiliary Transformers - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-10-28 | 2027-11-11 | G-PRC-SHP MR-EL-002 | 2027-11-25
10 | ALP-E04-00BFT-ME-OMM-0001 | LV Transformers - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-06 | 2027-11-23 | G-COM-SC-EL 00BFT | 2028-05-09
10 | ALP-E05-00BFA-ME-OMM-0001 | LV Switchboards and MCCs - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-08 | 2027-11-25 | G-COM-SC-EL 00BFA | 2028-05-09
10 | ALP-E07-00BRA-ME-OMM-0001 | UPS, Batteries and DC Systems - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-14 | 2027-12-01 | G-COM-SC-EL 00BRA | 2028-05-09
10 | ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | NONE | IFR | A | no | 2027-11-03 | 2027-12-01 | G-OWN-TO 00000 | 2029-04-18
10 | ALP-E03-00BBA-ME-OMM-0001 | MV Switchgear 10.5 kV - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-29 | 2027-12-16 | G-COM-SC-EL 00BBA | 2028-05-09
10 | ALP-E06-00XJA-ME-OMM-0001 | Emergency Diesel Generator - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-07-29 | 2027-12-16 | G-COM-SC-EL 00XJA | 2028-05-09
10 | ALP-E02-10BBT-ME-MDB-0001 | Unit Auxiliary Transformers - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-11-11 | 2028-01-06 | G-PRC-SHP MR-EL-002 | 2027-11-25
10 | ALP-E02-10BBT-ME-OMM-0001 | Unit Auxiliary Transformers - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-09-30 | 2028-02-17 | G-COM-SC-EL 10BBT | 2028-05-09
10 | ALP-EPC-00000-PI-M3D-0004 | Plant 3D Model and IFC4 Export - As-Built | NONE | IFR | A | no | 2028-06-15 | 2028-07-06 | G-OPS-AB 00000 | 2029-07-18
11 | ALP-EPC-00ACA-GE-RPT-0001 | 380 kV GIS - Technical Bid Evaluation | NONE | IFR | A | no | 2026-11-26 | 2026-12-03 | G-PRC-PO MR-EL-001 | 2026-12-15
11 | ALP-EPC-00CJA-GE-RPT-0001 | Plant DCS - Technical Bid Evaluation | NONE | IFR | A | no | 2027-01-12 | 2027-01-19 | G-PRC-PO MR-IC-001 | 2027-02-15
11 | ALP-E01-00ACA-ME-ITP-0001 | 380 kV GIS - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-01-12 | 2027-02-09 | G-PRC-FAB MR-EL-001 | 2027-05-10
11 | ALP-E01-00ACA-CV-CAL-0001 | 380 kV GIS - Supplier Foundation Loads and Anchor Bolt Drawings | NONE | IFR | A | no | 2027-01-26 | 2027-02-23 | G-PRC-FAB MR-EL-001 | 2027-05-10
11 | ALP-E01-00ACA-ME-DSH-0001 | 380 kV GIS - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-01-12 | 2027-02-23 | G-PRC-FAB MR-EL-001 | 2027-05-10
11 | ALP-E01-00ACA-ME-GAD-0001 | 380 kV GIS - Supplier GA Drawings | NONE | IFR | A | no | 2027-01-26 | 2027-03-09 | G-PRC-FAB MR-EL-001 | 2027-05-10
11 | ALP-I01-00CJA-ME-ITP-0001 | Plant DCS - Supplier Inspection and Test Plan | NONE | IFR | A | no | 2027-02-18 | 2027-03-18 | G-PRC-FAB MR-IC-001 | 2027-06-07
11 | ALP-E01-00ACA-IC-IOL-0001 | 380 kV GIS - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-02-09 | 2027-03-23
11 | ALP-E01-00ACA-ME-CAL-0001 | 380 kV GIS - Supplier Design Calculations | NONE | IFR | A | no | 2027-02-09 | 2027-03-23 | G-PRC-FAB MR-EL-001 | 2027-05-10
11 | ALP-I01-00CJA-ME-DSH-0001 | Plant DCS - Supplier Certified Datasheets and Performance Curves | NONE | IFR | A | no | 2027-02-18 | 2027-04-01 | G-PRC-FAB MR-IC-001 | 2027-06-07
11 | ALP-I01-00CJA-ME-GAD-0001 | Plant DCS - Supplier GA Drawings | NONE | IFR | A | no | 2027-03-04 | 2027-04-15 | G-PRC-FAB MR-IC-001 | 2027-06-07
11 | ALP-E01-00ACA-EL-WIR-0001 | 380 kV GIS - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-02-23 | 2027-04-20 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
11 | ALP-E01-00ACA-IC-DSH-0001 | 380 kV GIS - Supplier Instrument List and Datasheets | NONE | IFR | A | no | 2027-02-23 | 2027-04-20
11 | ALP-EPC-00UBA-CV-EFD-0001 | Electrical Building - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-03-16 | 2027-04-20 | G-CON-CWP CWP-03-CV-01 | 2027-03-29
11 | ALP-I01-00CJA-IC-IOL-0001 | Plant DCS - Supplier I/O List, Control Philosophy and Interface Signals | NONE | IFR | A | no | 2027-03-18 | 2027-04-29
11 | ALP-I01-00CJA-ME-CAL-0001 | Plant DCS - Supplier Design Calculations | NONE | IFR | A | no | 2027-03-18 | 2027-04-29 | G-PRC-FAB MR-IC-001 | 2027-06-07
11 | ALP-E01-00ACA-ME-LST-0001 | 380 kV GIS - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-03-09 | 2027-05-04
11 | ALP-I01-00CJA-EL-WIR-0001 | Plant DCS - Supplier Electrical Schematics and Wiring Diagrams | NONE | IFR | A | no | 2027-04-01 | 2027-05-27 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
11 | ALP-I01-00CJA-ME-LST-0001 | Plant DCS - Spare Parts and Special Tools Lists | NONE | IFR | A | no | 2027-04-15 | 2027-06-10
11 | ALP-EPC-00UBF-CV-EFD-0001 | Transformer Bays - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-05-17 | 2027-06-21 | G-CON-CWP CWP-01-CV-02 | 2027-04-19
11 | ALP-I01-00CJA-ME-TST-0001 | Plant DCS - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-07-08 | 2027-08-19 | G-PRC-FAT MR-IC-001 | 2027-09-30
11 | ALP-I01-00CJA-ME-PRC-0001 | Plant DCS - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-08-05 | 2027-09-16 | G-CON-CWP CWP-11-IC-01 | 2027-11-22
11 | ALP-E01-00ACA-ME-TST-0001 | 380 kV GIS - Factory Acceptance Test Procedure | NONE | IFR | A | no | 2027-08-24 | 2027-10-05 | G-PRC-FAT MR-EL-001 | 2027-11-16
11 | ALP-I01-00CJA-ME-TRP-0001 | Plant DCS - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-09-30 | 2027-10-14 | G-PRC-SHP MR-IC-001 | 2027-10-28
11 | ALP-E01-00ACA-ME-PRC-0001 | 380 kV GIS - Supplier Installation and Erection Manual | NONE | IFR | A | no | 2027-09-21 | 2027-11-02 | G-CON-CWP CWP-04-EL-01 | 2028-01-04
11 | ALP-E01-00ACA-ME-TRP-0001 | 380 kV GIS - Factory Acceptance Test Report | NONE | IFR | A | no | 2027-11-16 | 2027-11-30 | G-PRC-SHP MR-EL-001 | 2027-12-14
11 | ALP-I01-00CJA-ME-MDB-0001 | Plant DCS - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-10-14 | 2027-12-09 | G-PRC-SHP MR-IC-001 | 2027-10-28
11 | ALP-EPC-00000-CM-LST-0004 | Special Tools List | NONE | IFR | A | no | 2027-11-24 | 2027-12-22 | G-OWN-TO 00000 | 2029-04-18
11 | ALP-I01-00CJA-ME-OMM-0001 | Plant DCS - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-09-02 | 2028-01-20 | G-COM-SC-FF 00CJA | 2028-07-24
11 | ALP-E01-00ACA-ME-MDB-0001 | 380 kV GIS - Manufacturing Record Book and Conformity Certificates | NONE | IFR | A | no | 2027-11-30 | 2028-01-25 | G-PRC-SHP MR-EL-001 | 2027-12-14
11 | ALP-E01-00ACA-ME-OMM-0001 | 380 kV GIS - Supplier Operation and Maintenance Manual | NONE | IFR | A | no | 2027-10-19 | 2028-03-07 | G-COM-SC-EL 00ACA | 2028-05-09
12 | ALP-EPC-00UAC-CV-EFD-0001 | GIS Building - Equipment Foundation Drawings | NONE | IFR | A | no | 2027-03-12 | 2027-04-16 | G-CON-CWP CWP-04-CV-01 | 2027-04-05

## Relations
Alpilla 600 MW Combined Cycle Power Plant - Document relations: input links with the maturity required
engine release_control v1.2.0 ¦ generated 2026-09-29T02:52:27Z by SETUP ¦ data 6d73bc5813f68e2b ¦ planned dates from the levelled workflow network and the CPM (working days)
Document | Title | Input | Input title | Input orig. | Needed for IFR | Needed for IFC | Input status now | Input planned at IFR level | Document start | Slack wd
ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00000-GE-LST-0001 | Codes, Standards and Regulations Register | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2027-03-23 | 91
ALP-EPC-00000-GE-LST-0002 | Permits and Authorities Register | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2027-03-24 | 92
ALP-EPC-00000-GE-LST-0004 | Variation and Change Register | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-20 | 4
ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-19 | 3
ALP-EPC-00000-HS-PLN-0001 | HSE in Design Plan and Safety-in-Design Register | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-12-24 | 28
ALP-EPC-00000-HS-RPT-0001 | EIA Conditions Compliance Matrix | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-12-09 | 17
ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00000-ME-RPT-0002 | Materials Selection and Corrosion Control Report | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-16 | 0
ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00000-ME-SPC-0002 | Painting and Coating Specification | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-16 | 0
ALP-EPC-00000-ME-SPC-0003 | Insulation Specification | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-17 | 1
ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-20 | 4
ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00000-GE-PLN-0001 | Engineering Execution Plan | ALP-EPC-00000-GE-PRC-0001 | KKS Identification Manual | EPC | IFR | IFC | IFR | 2026-11-20 | 2027-04-05 | 96
ALP-EPC-00000-GE-PLN-0001 | Engineering Execution Plan | ALP-EPC-00000-GE-PRC-0002 | Document Numbering and Document Control Procedure | EPC | IFR | IFC | IFR | 2026-11-13 | 2027-04-05 | 101
ALP-EPC-00000-GE-PLN-0003 | Project Quality Plan | ALP-EPC-00000-GE-PRC-0002 | Document Numbering and Document Control Procedure | EPC | IFR | IFC | IFR | 2026-11-13 | 2027-04-07 | 103
ALP-EPC-00000-GE-PRC-0003 | As-Built Documentation and Engineering Database Handover Procedure | ALP-EPC-00000-GE-PRC-0002 | Document Numbering and Document Control Procedure | EPC | IFR | IFC | IFR | 2026-11-13 | 2026-11-25 | 8
ALP-EPC-00000-PC-PRC-0001 | Progress Measurement and Reporting Procedure | ALP-EPC-00000-GE-PRC-0002 | Document Numbering and Document Control Procedure | EPC | IFR | IFC | IFR | 2026-11-13 | 2026-11-26 | 9
ALP-EPC-00000-GE-LST-0003 | Tie-in and Terminal Point Register | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2027-03-29 | 95
ALP-EPC-00000-GE-LST-0003 | Tie-in and Terminal Point Register | ALP-IEC-00000-GE-LST-0001 | Power Island - Terminal Points and Interface Data | IEC | IFR | ACCEPTED | ACCEPTED | 2026-09-28 | 2027-03-29 | 130
ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-28 | 40
ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2026-12-28 | 10
ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2026-12-28 | 10
ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | ALP-IEC-20MAA-CV-CAL-0001 | Steam Turbine and Condenser - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CV-SPC-0001 | Concrete and Civil Works Specification | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-EL-CAL-0004 | Lighting Calculation | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-29 | 237
ALP-EPC-00000-EL-RPT-0001 | Electrical Control and Interlock Philosophy | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-29 | 237
ALP-EPC-00000-EL-SPC-0001 | Power and Control Cable Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-06 | 4
ALP-EPC-00000-EL-SPC-0002 | LV and MV Motor Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-29 | 237
ALP-EPC-00000-EL-SPC-0005 | Cable Trays, Earthing and Lighting Materials - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-HS-PLN-0002 | Construction HSE Plan and Site Safety Plan | ALP-EPC-00000-HS-PLN-0001 | HSE in Design Plan and Safety-in-Design Register | EPC | IFR | IFC | NONE | 2027-03-09 | 2027-03-09 | 0
ALP-EPC-00000-HS-PLN-0003 | Construction Environmental and Social Management Plan | ALP-EPC-00000-HS-RPT-0001 | EIA Conditions Compliance Matrix | EPC | IFR | IFC | NONE | 2026-12-31 | 2027-02-22 | 37
ALP-EPC-00000-HS-PLN-0004 | Waste Management Plan | ALP-EPC-00000-HS-RPT-0001 | EIA Conditions Compliance Matrix | EPC | IFR | IFC | NONE | 2026-12-31 | 2027-03-05 | 46
ALP-EPC-00000-IC-CNR-0001 | Unit Coordination, Load Control, Export Limiter and Fuel Transfer | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-08 | 70
ALP-EPC-00000-IC-CNR-0001 | Unit Coordination, Load Control, Export Limiter and Fuel Transfer | ALP-IEC-10MBY-IC-CNR-0001 | Power Island Operating and Control Description | IEC | IFR | ACCEPTED | NONE | 2027-02-08 | 2027-02-08 | 0
ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-IC-SPC-0003 | Field Instruments - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-IC-SPC-0004 | Control Valves - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-IC-SPC-0005 | DCS Functional Design Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-03 | 1
ALP-EPC-00000-IC-TST-0001 | DCS Site Acceptance Test Procedure | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00CJA-IC-BLK-0001 | Plant DCS - System Architecture | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00CJA-IC-BLK-0001 | Plant DCS - System Architecture | ALP-IEC-10MBY-IC-BLK-0001 | TCS Architecture and DCS Integration | IEC | IFR | ACCEPTED | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00000-EL-CAL-0005 | Cathodic Protection Design | ALP-EPC-00000-ME-RPT-0002 | Materials Selection and Corrosion Control Report | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-12-07 | 0
ALP-EPC-00000-HS-STU-0002 | Stack Dispersion Confirmation | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2026-12-18 | 0
ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-18 | 34
ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-CAL-0001 | Performance Guarantee Calculation and Correction Curves | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-16 | 0
ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-PFD-0002 | Utility Flow Diagrams | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-STU-0001 | Plant Water Balance | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-STU-0003 | CW Thermal Plume and Outfall Dispersion Study | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-GE-MDL-0001 | Master Document List | ALP-EPC-00000-GE-PLN-0001 | Engineering Execution Plan | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00000-GE-PLN-0002 | Advanced Work Packaging Execution Plan | ALP-EPC-00000-GE-PLN-0001 | Engineering Execution Plan | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00000-GE-PLN-0005 | Project Execution Plan | ALP-EPC-00000-GE-PLN-0003 | Project Quality Plan | EPC | IFR | IFC | NONE | 2027-05-07 | 2027-05-13 | 4
ALP-EPC-00000-GE-LST-0005 | As-Built Documentation Index | ALP-EPC-00000-GE-PRC-0003 | As-Built Documentation and Engineering Database Handover Procedure | EPC | IFR | IFC | NONE | 2027-04-05 | 2027-04-05 | 0
ALP-EPC-00000-GE-PLN-0004 | Interface Management Plan | ALP-EPC-00000-GE-LST-0003 | Tie-in and Terminal Point Register | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-04-19 | 0
ALP-EPC-00000-CV-RPT-0002 | Dewatering Design and Discharge Plan | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00000-CV-SPC-0002 | Piling Specification | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00000-CV-STU-0001 | Site-Specific Seismic Hazard Study | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00000-HS-RPT-0003 | Soil and Groundwater Baseline Survey Report | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-23 | 86
ALP-EPC-00UAC-CV-CAL-0001 | GIS Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00UAC-CV-CAL-0001 | GIS Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00UBA-CV-CAL-0001 | Electrical Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-09 | 16
ALP-EPC-00UBA-CV-CAL-0001 | Electrical Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-09 | 56
ALP-EPC-00UBF-CV-CAL-0001 | Transformer Bays - Structural and Foundation Calculation | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-EPC-00UBF-CV-CAL-0001 | Transformer Bays - Structural and Foundation Calculation | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-EPC-00UBF-CV-CAL-0001 | Transformer Bays - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-04-09 | 59
ALP-EPC-00UBF-CV-CAL-0001 | Transformer Bays - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-09 | 99
ALP-EPC-00UCA-CV-CAL-0001 | Control Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-16 | 21
ALP-EPC-00UCA-CV-CAL-0001 | Control Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-16 | 61
ALP-EPC-00UEG-CV-CAL-0001 | LDO Tank Farm Structures - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-02 | 11
ALP-EPC-00UEG-CV-CAL-0001 | LDO Tank Farm Structures - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-02 | 51
ALP-EPC-00UEK-CV-CAL-0001 | Gas Station Structures - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-04-06 | 56
ALP-EPC-00UEK-CV-CAL-0001 | Gas Station Structures - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-06 | 96
ALP-EPC-00UGA-CV-CAL-0001 | Water Treatment Building and Basins - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-09 | 16
ALP-EPC-00UGA-CV-CAL-0001 | Water Treatment Building and Basins - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-09 | 56
ALP-EPC-00UPA-CV-CAL-0001 | CW Intake and Outfall Marine Structures - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-04-30 | 74
ALP-EPC-00UPA-CV-CAL-0001 | CW Intake and Outfall Marine Structures - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-30 | 114
ALP-EPC-00UPA-CV-RPT-0001 | Marine Route Survey for Intake and Outfall Pipelines | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00UPC-CV-CAL-0001 | CW Pump House - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00UPC-CV-CAL-0001 | CW Pump House - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00UQA-CV-CAL-0001 | Utility Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-15 | 20
ALP-EPC-00UQA-CV-CAL-0001 | Utility Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-15 | 60
ALP-EPC-00USA-CV-CAL-0001 | Workshop and Warehouse - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-15 | 20
ALP-EPC-00USA-CV-CAL-0001 | Workshop and Warehouse - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-15 | 60
ALP-EPC-00UYA-CV-CAL-0001 | Administration Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-12 | 39
ALP-EPC-00UYA-CV-CAL-0001 | Administration Building - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-12 | 79
ALP-EPC-00UZA-CV-CAL-0001 | Roads and Paving - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-05-05 | 77
ALP-EPC-00UZA-CV-CAL-0001 | Roads and Paving - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-05 | 117
ALP-EPC-00UZB-CV-CAL-0001 | Fencing and Gates - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-05-07 | 79
ALP-EPC-00UZB-CV-CAL-0001 | Fencing and Gates - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-07 | 119
ALP-EPC-00UZC-CV-CAL-0001 | Site Drainage and Culverts - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-05-11 | 81
ALP-EPC-00UZC-CV-CAL-0001 | Site Drainage and Culverts - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-11 | 121
ALP-EPC-00UZD-CV-CAL-0001 | Pipe Racks and Pipe Sleepers - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00UZD-CV-CAL-0001 | Pipe Racks and Pipe Sleepers - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00UZE-CV-CAL-0001 | Cable Trenches and Duct Banks - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-05-12 | 82
ALP-EPC-00UZE-CV-CAL-0001 | Cable Trenches and Duct Banks - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-12 | 122
ALP-EPC-00UZF-CV-CAL-0001 | Temporary Barge Landing - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-04-29 | 73
ALP-EPC-00UZF-CV-CAL-0001 | Temporary Barge Landing - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-29 | 113
ALP-EPC-10UHA-CV-CAL-0001 | HRSG Foundations and Structures - Structural and Foundation Calculation | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-10UHA-CV-CAL-0001 | HRSG Foundations and Structures - Structural and Foundation Calculation | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-10UHA-CV-CAL-0001 | HRSG Foundations and Structures - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-05-18 | 86
ALP-EPC-10UHA-CV-CAL-0001 | HRSG Foundations and Structures - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-18 | 126
ALP-EPC-10UHN-CV-CAL-0001 | Stack Foundation - Structural and Foundation Calculation | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-05-19 | 112
ALP-EPC-10UHN-CV-CAL-0001 | Stack Foundation - Structural and Foundation Calculation | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-05-19 | 112
ALP-EPC-10UHN-CV-CAL-0001 | Stack Foundation - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-05-19 | 87
ALP-EPC-10UHN-CV-CAL-0001 | Stack Foundation - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-19 | 127
ALP-EPC-10UMA-CV-CAL-0001 | Gas Turbine Hall - Structural and Foundation Calculation | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-03-11 | 63
ALP-EPC-10UMA-CV-CAL-0001 | Gas Turbine Hall - Structural and Foundation Calculation | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-03-11 | 63
ALP-EPC-10UMA-CV-CAL-0001 | Gas Turbine Hall - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-11 | 38
ALP-EPC-10UMA-CV-CAL-0001 | Gas Turbine Hall - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-11 | 78
ALP-EPC-20UMB-CV-CAL-0001 | Steam Turbine Hall - Structural and Foundation Calculation | ALP-IEC-20MAA-CV-CAL-0001 | Steam Turbine and Condenser - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-03-12 | 54
ALP-EPC-20UMB-CV-CAL-0001 | Steam Turbine Hall - Structural and Foundation Calculation | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-12 | 39
ALP-EPC-20UMB-CV-CAL-0001 | Steam Turbine Hall - Structural and Foundation Calculation | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-12 | 79
ALP-EPC-00000-CV-SPC-0004 | Civil and Building Works - Technical Specification | ALP-EPC-00000-CV-SPC-0001 | Concrete and Civil Works Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CV-SPC-0004 | Civil and Building Works - Technical Specification | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-SS-SPC-0002 | Structural Steel Supply and Fabrication - Technical Specification | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-EL-SPC-0004 | Power and Control Cables - Technical Specification | ALP-EPC-00000-EL-SPC-0001 | Power and Control Cable Specification | EPC | IFR | IFC | NONE | 2026-12-04 | 2026-12-04 | 0
ALP-EPC-00000-EL-SPC-0004 | Power and Control Cables - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-04 | 24
ALP-EPC-00000-EL-MRQ-0002 | Cable Trays, Earthing and Lighting Materials - Material Requisition | ALP-EPC-00000-EL-SPC-0005 | Cable Trays, Earthing and Lighting Materials - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00000-IC-LST-0002 | Alarm List | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00ACA-IC-LOG-0001 | 380 kV GIS Switchyard - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-30 | 5
ALP-EPC-00BLA-IC-LOG-0001 | Lighting and Small Power - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-02 | 7
ALP-EPC-00BMA-IC-LOG-0001 | Emergency LV Switchgear - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-07 | 10
ALP-EPC-00BRA-IC-LOG-0001 | UPS - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-07 | 10
ALP-EPC-00BTA-IC-LOG-0001 | Batteries and DC 220 V - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-08 | 11
ALP-EPC-00CJA-IC-LOG-0001 | Plant DCS - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-10 | 13
ALP-EPC-00CKA-IC-LOG-0001 | Historian, Performance Monitoring and Operator Training Simulator - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-24 | 1
ALP-EPC-00CQA-IC-LOG-0001 | Continuous Emission Monitoring - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-14 | 15
ALP-EPC-00CYA-IC-LOG-0001 | Telecom, CCTV, Access Control, Security - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-14 | 15
ALP-EPC-00SGY-IC-LOG-0001 | Fire Detection and Alarm - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-14 | 15
ALP-EPC-00SMA-IC-LOG-0001 | Cranes and Hoists - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-14 | 15
ALP-EPC-00XJA-IC-LOG-0001 | Emergency Diesel Generator - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-16 | 17
ALP-EPC-10BBT-IC-LOG-0001 | GT Unit Auxiliary Transformer - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-22 | 21
ALP-EPC-10HNE-IC-LOG-0001 | Stack 65 m with CEMS Platform and Silencer - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-28 | 25
ALP-EPC-20BBT-IC-LOG-0001 | ST Unit Auxiliary Transformer - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-29 | 26
ALP-EPC-00000-IC-TST-0002 | OT Cybersecurity Acceptance Test Procedure | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00CJG-IC-BLK-0001 | Safety Instrumented Systems - System Architecture | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00CJG-IC-BLK-0001 | Safety Instrumented Systems - System Architecture | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00CKA-IC-BLK-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Architecture | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00CKA-IC-BLK-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Architecture | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00CQA-IC-BLK-0001 | Continuous Emission Monitoring - System Architecture | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00CQA-IC-BLK-0001 | Continuous Emission Monitoring - System Architecture | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00CYA-IC-BLK-0001 | Telecom, CCTV, Access Control, Security - System Architecture | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00CYA-IC-BLK-0001 | Telecom, CCTV, Access Control, Security - System Architecture | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00SGY-IC-BLK-0001 | Fire Detection and Alarm - System Architecture | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00SGY-IC-BLK-0001 | Fire Detection and Alarm - System Architecture | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00000-GE-SPC-0003 | Instrument Installation Materials - Technical Specification | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00000-GE-SPC-0003 | Instrument Installation Materials - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-30 | 20
ALP-EPC-00ACA-IC-DSH-0001 | 380 kV GIS Switchyard - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00CQA-IC-DSH-0002 | Continuous Emission Monitoring - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-14 | 10
ALP-EPC-00XJA-IC-DSH-0001 | Emergency Diesel Generator - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-14 | 10
ALP-EPC-10BBT-IC-DSH-0001 | GT Unit Auxiliary Transformer - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-01 | 1
ALP-EPC-10HNE-IC-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-21 | 15
ALP-EPC-20BBT-IC-DSH-0001 | ST Unit Auxiliary Transformer - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-24 | 18
ALP-EPC-00000-IC-MRQ-0001 | Field Instruments - Material Requisition | ALP-EPC-00000-IC-SPC-0003 | Field Instruments - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00000-IC-MRQ-0002 | Control Valves - Material Requisition | ALP-EPC-00000-IC-SPC-0004 | Control Valves - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00BXA-GE-SPC-0001 | Cathodic Protection - Technical Specification | ALP-EPC-00000-EL-CAL-0005 | Cathodic Protection Design | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-01-28 | 23
ALP-EPC-00BXA-GE-SPC-0001 | Cathodic Protection - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-EPC-10HNE-SS-SPC-0001 | Stack 65 m with Silencer - Technical Specification | ALP-EPC-00000-HS-STU-0002 | Stack Dispersion Confirmation | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-11-02 | -25
ALP-EPC-10HNE-SS-SPC-0001 | Stack 65 m with Silencer - Technical Specification | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-GE-SPC-0006 | Pipe Supports, Spring Hangers and Snubbers - Technical Specification | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2027-02-22 | 46
ALP-EPC-00000-GE-SPC-0006 | Pipe Supports, Spring Hangers and Snubbers - Technical Specification | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-02-22 | 31
ALP-EPC-00000-GE-SPC-0007 | Piping Specialty Items - Technical Specification | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-GE-SPC-0008 | Safety and Relief Valves - Technical Specification | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-SPC-0003 | Welding, Heat Treatment and NDE Specification | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-01 | 21
ALP-EPC-00000-PI-SPC-0004 | Piping Bulk Materials - Technical Specification | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-SPC-0006 | Valves - Technical Specification | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-19 | 13
ALP-EPC-00000-CM-CMP-0002 | Performance Test Procedure | ALP-EPC-00000-PR-CAL-0001 | Performance Guarantee Calculation and Correction Curves | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00000-CM-CMP-0002 | Performance Test Procedure | ALP-IEC-10MBA-PR-HMB-0001 | Power Island Thermal Performance Data | IEC | IFR | ACCEPTED | ACCEPTED | 2026-09-28 | 2026-11-23 | 40
ALP-EPC-00000-PR-CAL-0002 | Degradation Curves | ALP-EPC-00000-PR-CAL-0001 | Performance Guarantee Calculation and Correction Curves | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-12-14 | 20
ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-PLT-0001 | Plot Plan | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00000-PI-PLT-0001 | Plot Plan | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-PLT-0001 | Plot Plan | ALP-IEC-10MBA-ME-LAY-0001 | Power Island Arrangement - Installation and Maintenance Spaces | IEC | IFR | ACCEPTED | ACCEPTED | 2026-09-28 | 2026-11-02 | 25
ALP-EPC-00000-PR-RPT-0001 | Cycle Chemistry Concept | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-RPT-0002 | Operating Philosophy | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-RPT-0003 | Isolation, Drainage and Venting Philosophy | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-05 | 3
ALP-EPC-00000-PR-STU-0002 | Reliability, Availability and Maintainability Study | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-10 | 6
ALP-EPC-00000-PR-STU-0004 | Carbon Capture Readiness Study | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00EGA-PR-SDS-0001 | LDO Unloading - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00EGA-PR-SDS-0001 | LDO Unloading - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGB-PR-SDS-0001 | LDO Storage - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00EGB-PR-SDS-0001 | LDO Storage - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGC-PR-SDS-0001 | LDO Forwarding and Treatment - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00EGC-PR-SDS-0001 | LDO Forwarding and Treatment - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EKA-PR-SDS-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00EKA-PR-SDS-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EKC-PR-SDS-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00EKC-PR-SDS-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GBA-PR-SDS-0001 | Seawater Reverse Osmosis - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00GBA-PR-SDS-0001 | Seawater Reverse Osmosis - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GCA-PR-SDS-0001 | Demineralisation - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00GCA-PR-SDS-0001 | Demineralisation - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-PR-SDS-0001 | Demineralised Water Storage and Distribution - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00GHA-PR-SDS-0001 | Demineralised Water Storage and Distribution - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-PR-SDS-0001 | Waste Water Treatment - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00GNA-PR-SDS-0001 | Waste Water Treatment - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GUA-PR-SDS-0001 | Sanitary Waste Water Treatment - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00GUA-PR-SDS-0001 | Sanitary Waste Water Treatment - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LBG-PR-SDS-0001 | Auxiliary Steam - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00LBG-PR-SDS-0001 | Auxiliary Steam - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-PR-SDS-0001 | Condensate Polishing - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00LDA-PR-SDS-0001 | Condensate Polishing - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAB-PR-SDS-0001 | CW Piping - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00PAB-PR-SDS-0001 | CW Piping - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAC-PR-SDS-0001 | CW Pumps - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00PAC-PR-SDS-0001 | CW Pumps - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAH-PR-SDS-0001 | Condenser Tube Cleaning - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00PAH-PR-SDS-0001 | Condenser Tube Cleaning - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PBA-PR-SDS-0001 | Electro-Chlorination - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00PBA-PR-SDS-0001 | Electro-Chlorination - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-PR-SDS-0001 | Closed Cooling Water - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00PGA-PR-SDS-0001 | Closed Cooling Water - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QCA-PR-SDS-0001 | Chemical Dosing - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00QCA-PR-SDS-0001 | Chemical Dosing - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-PR-SDS-0001 | Compressed Air - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00QEA-PR-SDS-0001 | Compressed Air - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QHA-PR-SDS-0001 | Auxiliary Boiler - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00QHA-PR-SDS-0001 | Auxiliary Boiler - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QJA-PR-SDS-0001 | Nitrogen Supply - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00QJA-PR-SDS-0001 | Nitrogen Supply - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QJB-PR-SDS-0001 | Hydrogen and CO2 Supply - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00QJB-PR-SDS-0001 | Hydrogen and CO2 Supply - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QUA-PR-SDS-0001 | Sampling and SWAS - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00QUA-PR-SDS-0001 | Sampling and SWAS - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SAA-HV-SDS-0001 | HVAC - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00SAA-HV-SDS-0001 | HVAC - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGC-PR-SDS-0001 | Deluge, Spray and Foam Systems - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00SGC-PR-SDS-0001 | Deluge, Spray and Foam Systems - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HAN-PR-SDS-0001 | HRSG Blowdown and Drains - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10HAN-PR-SDS-0001 | HRSG Blowdown and Drains - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HSB-PR-SDS-0001 | Ammonia Storage and Supply - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10HSB-PR-SDS-0001 | Ammonia Storage and Supply - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAB-PR-SDS-0001 | Feedwater Piping - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10LAB-PR-SDS-0001 | Feedwater Piping - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAC-PR-SDS-0001 | Boiler Feed Pumps - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10LAC-PR-SDS-0001 | Boiler Feed Pumps - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAE-PR-SDS-0001 | HP Attemperation Spray Water - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10LAE-PR-SDS-0001 | HP Attemperation Spray Water - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAF-PR-SDS-0001 | Reheat Attemperation Spray Water - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10LAF-PR-SDS-0001 | Reheat Attemperation Spray Water - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LBA-PR-SDS-0001 | Main Steam Piping - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10LBA-PR-SDS-0001 | Main Steam Piping - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LBB-PR-SDS-0001 | Hot Reheat Piping - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10LBB-PR-SDS-0001 | Hot Reheat Piping - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LBC-PR-SDS-0001 | Cold Reheat Piping - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10LBC-PR-SDS-0001 | Cold Reheat Piping - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LBD-PR-SDS-0001 | LP Steam Piping - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-10LBD-PR-SDS-0001 | LP Steam Piping - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20LCA-PR-SDS-0001 | Main Condensate Piping - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-20LCA-PR-SDS-0001 | Main Condensate Piping - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20LCB-PR-SDS-0001 | Condensate Extraction Pumps - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-20LCB-PR-SDS-0001 | Condensate Extraction Pumps - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20MAN-PR-SDS-0001 | Turbine Bypass Stations and Piping - System Design Description | ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | EPC | IFR | IFC | IFR | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-20MAN-PR-SDS-0001 | Turbine Bypass Stations and Piping - System Design Description | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-LST-0001 | Equipment List | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-LST-0001 | Equipment List | ALP-EPC-00000-PR-PFD-0002 | Utility Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-02 | -20
ALP-EPC-00000-PR-LST-0001 | Equipment List | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PR-LST-0003 | Chemical Consumption, Effluent and Emission Inventory | ALP-EPC-00000-PR-STU-0001 | Plant Water Balance | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-12-07 | 0
ALP-EPC-00000-CV-SPC-0005 | Marine Works - Technical Specification | ALP-EPC-00000-CV-SPC-0001 | Concrete and Civil Works Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CV-SPC-0005 | Marine Works - Technical Specification | ALP-EPC-00000-PR-STU-0003 | CW Thermal Plume and Outfall Dispersion Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-11-02 | -25
ALP-EPC-00000-CV-SPC-0005 | Marine Works - Technical Specification | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PC-SCH-0001 | Level 3 Project Schedule | ALP-EPC-00000-GE-MDL-0001 | Master Document List | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-31 | 10
ALP-EPC-00000-PC-SCH-0001 | Level 3 Project Schedule | ALP-EPC-00000-GE-PLN-0002 | Advanced Work Packaging Execution Plan | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-05-31 | 0
ALP-EPC-00000-CV-SPC-0003 | Piling Works - Technical Specification | ALP-EPC-00000-CV-SPC-0001 | Concrete and Civil Works Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CV-SPC-0003 | Piling Works - Technical Specification | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2026-11-02 | -35
ALP-EPC-00000-CV-SPC-0003 | Piling Works - Technical Specification | ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CV-TST-0001 | Pile Load Test Procedure | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2027-01-20 | 22
ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | ALP-EPC-00000-CV-SPC-0004 | Civil and Building Works - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | ALP-EPC-00000-SS-SPC-0002 | Structural Steel Supply and Fabrication - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-EL-MRQ-0001 | Power and Control Cables - Material Requisition | ALP-EPC-00000-EL-SPC-0004 | Power and Control Cables - Technical Specification | EPC | IFR | IFC | NONE | 2027-01-01 | 2027-01-01 | 0
ALP-EPC-00BLA-GE-RPT-0001 | Cable Trays, Earthing and Lighting Materials - Technical Bid Evaluation | ALP-EPC-00000-EL-MRQ-0002 | Cable Trays, Earthing and Lighting Materials - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-01-07 | 23
ALP-EPC-00000-IC-TRP-0001 | OT Cybersecurity Acceptance Test Report | ALP-EPC-00000-IC-TST-0002 | OT Cybersecurity Acceptance Test Procedure | EPC | IFR | IFC | NONE | 2026-12-14 | 2028-09-18 | 460
ALP-EPC-00CJG-GE-SPC-0001 | BOP Safety Instrumented System - Technical Specification | ALP-EPC-00CJG-IC-BLK-0001 | Safety Instrumented Systems - System Architecture | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00CJG-GE-SPC-0001 | BOP Safety Instrumented System - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00CKA-GE-SPC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Specification | ALP-EPC-00CKA-IC-BLK-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Architecture | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00CKA-GE-SPC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | ALP-EPC-00000-HS-RPT-0001 | EIA Conditions Compliance Matrix | EPC | IFR | IFC | NONE | 2026-12-31 | 2026-11-02 | -43
ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | ALP-EPC-00CQA-IC-BLK-0001 | Continuous Emission Monitoring - System Architecture | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-11-02 | -30
ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification | ALP-EPC-00CYA-IC-BLK-0001 | Telecom, CCTV, Access Control, Security - System Architecture | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification | ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-14 | 15
ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00000-GE-MRQ-0003 | Instrument Installation Materials - Material Requisition | ALP-EPC-00000-GE-SPC-0003 | Instrument Installation Materials - Technical Specification | EPC | IFR | IFC | NONE | 2027-04-02 | 2027-04-02 | 0
ALP-EPC-00000-GE-RPT-0006 | Field Instruments - Technical Bid Evaluation | ALP-EPC-00000-IC-MRQ-0001 | Field Instruments - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-03-03 | 62
ALP-EPC-00000-GE-RPT-0007 | Control Valves - Technical Bid Evaluation | ALP-EPC-00000-IC-MRQ-0002 | Control Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-02-22 | 55
ALP-EPC-00BXA-GE-ITP-0001 | Cathodic Protection - Inspection and Test Plan | ALP-EPC-00BXA-GE-SPC-0001 | Cathodic Protection - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-25 | 2027-02-25 | 0
ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | ALP-EPC-00BXA-GE-SPC-0001 | Cathodic Protection - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-25 | 2027-02-25 | 0
ALP-EPC-00000-GE-MRQ-0006 | Pipe Supports, Spring Hangers and Snubbers - Material Requisition | ALP-EPC-00000-GE-SPC-0006 | Pipe Supports, Spring Hangers and Snubbers - Technical Specification | EPC | IFR | IFC | NONE | 2027-03-22 | 2027-03-22 | 0
ALP-EPC-00000-GE-MRQ-0007 | Piping Specialty Items - Material Requisition | ALP-EPC-00000-GE-SPC-0007 | Piping Specialty Items - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00000-GE-MRQ-0008 | Safety and Relief Valves - Material Requisition | ALP-EPC-00000-GE-SPC-0008 | Safety and Relief Valves - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00000-HS-PLN-0006 | Radiation Protection Plan | ALP-EPC-00000-PI-SPC-0003 | Welding, Heat Treatment and NDE Specification | EPC | IFR | IFC | NONE | 2027-05-21 | 2027-06-02 | 8
ALP-EPC-00000-PI-MRQ-0001 | Piping Bulk Materials - Material Requisition | ALP-EPC-00000-PI-SPC-0004 | Piping Bulk Materials - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00000-PI-MRQ-0003 | Valves - Material Requisition | ALP-EPC-00000-PI-SPC-0006 | Valves - Technical Specification | EPC | IFR | IFC | NONE | 2026-12-17 | 2026-12-17 | 0
ALP-EPC-00000-CM-TRP-0002 | Performance Test Report incl. Uncertainty Analysis | ALP-EPC-00000-CM-CMP-0002 | Performance Test Procedure | EPC | IFR | IFC | NONE | 2027-07-14 | 2029-03-19 | 438
ALP-EPC-00000-GE-SPC-0004 | Painting and Insulation - Technical Specification | ALP-EPC-00000-ME-SPC-0002 | Painting and Coating Specification | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-19 | 69
ALP-EPC-00000-GE-SPC-0004 | Painting and Insulation - Technical Specification | ALP-EPC-00000-ME-SPC-0003 | Insulation Specification | EPC | IFR | IFC | NONE | 2027-02-11 | 2027-03-19 | 26
ALP-EPC-00000-GE-SPC-0004 | Painting and Insulation - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-03-19 | 49
ALP-EPC-00000-GE-SPC-0005 | Mechanical and Piping Erection - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-21 | 144
ALP-EPC-00000-GE-SPC-0005 | Mechanical and Piping Erection - Technical Specification | ALP-EPC-00000-PI-SPC-0003 | Welding, Heat Treatment and NDE Specification | EPC | IFR | IFC | NONE | 2027-05-21 | 2027-05-21 | 0
ALP-EPC-00000-GE-SPC-0005 | Mechanical and Piping Erection - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-05-21 | 94
ALP-EPC-00SMA-ME-SPC-0001 | EOT Cranes - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SMA-ME-SPC-0001 | EOT Cranes - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-10HNE-ME-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Datasheet | ALP-EPC-10HNE-SS-SPC-0001 | Stack 65 m with Silencer - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HNE-ME-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00000-CM-CMP-0004 | Operational Demonstration and Reliability Run Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-17 | 77
ALP-EPC-00000-CM-CMP-0004 | Operational Demonstration and Reliability Run Procedure | ALP-EPC-00000-IC-CNR-0001 | Unit Coordination, Load Control, Export Limiter and Fuel Transfer | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-03-17 | 12
ALP-EPC-00000-CM-PLN-0002 | Training Plan | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-28 | 238
ALP-EPC-00000-CM-PRC-0001 | Punch List and Completion Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-23 | 81
ALP-EPC-00000-CM-PRC-0002 | System Completion, Mechanical Completion and Turnover Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-11-02 | 241
ALP-EPC-00ACA-CM-CMP-0001 | 380 kV GIS Switchyard - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00BBA-CM-CMP-0001 | MV Switchgear 10.5 kV - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00BFA-CM-CMP-0001 | LV Switchgear 0.4 kV - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00BFT-CM-CMP-0001 | LV Transformers - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00BLA-CM-CMP-0001 | Lighting and Small Power - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00BMA-CM-CMP-0001 | Emergency LV Switchgear - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-00BRA-CM-CMP-0001 | UPS - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-10 | 8
ALP-EPC-00BTA-CM-CMP-0001 | Batteries and DC 220 V - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-22 | 16
ALP-EPC-00BXA-CM-CMP-0001 | Earthing and Lightning Protection - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-28 | 20
ALP-EPC-00CJA-CM-CMP-0001 | Plant DCS - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-08 | 29
ALP-EPC-00CJG-CM-CMP-0001 | Safety Instrumented Systems - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-19 | 36
ALP-EPC-00CKA-CM-CMP-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-25 | 40
ALP-EPC-00CQA-CM-CMP-0001 | Continuous Emission Monitoring - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-25 | 40
ALP-EPC-00CYA-CM-CMP-0001 | Telecom, CCTV, Access Control, Security - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-25 | 40
ALP-EPC-00SGY-CM-CMP-0001 | Fire Detection and Alarm - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-05 | 49
ALP-EPC-00SMA-CM-CMP-0001 | Cranes and Hoists - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-08 | 50
ALP-EPC-00XJA-CM-CMP-0001 | Emergency Diesel Generator - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-28 | 20
ALP-EPC-10BBT-CM-CMP-0001 | GT Unit Auxiliary Transformer - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-28 | 20
ALP-EPC-10HNE-CM-CMP-0001 | Stack 65 m with CEMS Platform and Silencer - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-08 | 50
ALP-EPC-20BBT-CM-CMP-0001 | ST Unit Auxiliary Transformer - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-12-28 | 20
ALP-EPC-00000-EL-STU-0003 | Earthing Study | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00000-EL-STU-0003 | Earthing Study | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00000-HS-HAZ-0001 | HAZID Report | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-25 | 39
ALP-EPC-00000-HS-HAZ-0001 | HAZID Report | ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-25 | 39
ALP-EPC-00000-HS-HAZ-0001 | HAZID Report | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2026-12-25 | 0
ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-25 | 39
ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2026-12-25 | 0
ALP-EPC-00000-HS-STU-0001 | Noise Study | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00000-HS-STU-0001 | Noise Study | ALP-IEC-10MBA-HS-RPT-0001 | Power Island Noise Data | IEC | IFR | ACCEPTED | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00000-HS-STU-0001 | Noise Study | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-01-11 | 11
ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-ME-STU-0002 | Mechanical Handling and Maintenance Access Study | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-19 | 13
ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-25 | 17
ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-24 | 16
ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-27 | 19
ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-10 | 6
ALP-EPC-00UPA-PI-LAY-0001 | Marine Works - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-30 | 20
ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-13 | 9
ALP-EPC-00UZA-CV-CVL-0001 | Temporary Facilities and Construction Site Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | ALP-IEC-10HAA-ME-GAD-0001 | HRSG incl. SCR - Supplier GA Drawings | IEC | IFR | ACCEPTED | ACCEPTED | 2026-09-28 | 2026-11-02 | 25
ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | ALP-IEC-10MBA-ME-GAD-0001 | Gas Turbine Package incl. Auxiliaries - Supplier GA Drawings | IEC | IFR | ACCEPTED | ACCEPTED | 2026-09-28 | 2026-11-02 | 25
ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-04 | 2
ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | ALP-IEC-20MAA-ME-GAD-0001 | Steam Turbine and Condenser - Supplier GA Drawings | IEC | IFR | ACCEPTED | ACCEPTED | 2026-09-28 | 2026-11-04 | 27
ALP-EPC-00000-PR-RPT-0004 | Equipment Sparing and Redundancy Philosophy | ALP-EPC-00000-PR-STU-0002 | Reliability, Availability and Maintainability Study | EPC | IFR | IFC | NONE | 2027-05-24 | 2027-05-24 | 0
ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation | ALP-EPC-00EGA-PR-SDS-0001 | LDO Unloading - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | ALP-EPC-00EGA-PR-SDS-0001 | LDO Unloading - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-00EGB-ME-CAL-0001 | LDO Storage - Sizing and Hydraulic Calculation | ALP-EPC-00EGB-PR-SDS-0001 | LDO Storage - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-10 | 72
ALP-EPC-00EGB-ME-CAL-0001 | LDO Storage - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-10 | 42
ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-26 | 84
ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | ALP-EPC-00EGB-PR-SDS-0001 | LDO Storage - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-26 | 84
ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-26 | 54
ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | ALP-EPC-00EGA-PR-SDS-0001 | LDO Unloading - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | ALP-EPC-00EGC-PR-SDS-0001 | LDO Forwarding and Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00EGC-ME-CAL-0001 | LDO Forwarding and Treatment - Sizing and Hydraulic Calculation | ALP-EPC-00EGC-PR-SDS-0001 | LDO Forwarding and Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00EGC-ME-CAL-0001 | LDO Forwarding and Treatment - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | ALP-EPC-00EGC-PR-SDS-0001 | LDO Forwarding and Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation | ALP-EPC-00EKA-PR-SDS-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | ALP-EPC-00EKA-PR-SDS-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | ALP-EPC-00EKA-PR-SDS-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00EKC-ME-CAL-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Sizing and Hydraulic Calculation | ALP-EPC-00EKC-PR-SDS-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-00EKC-ME-CAL-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | ALP-EPC-00EKC-PR-SDS-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-04 | 58
ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation | ALP-EPC-00GBA-PR-SDS-0001 | Seawater Reverse Osmosis - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-15 | 54
ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | ALP-EPC-00GBA-PR-SDS-0001 | Seawater Reverse Osmosis - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-15 | 54
ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-15 | 24
ALP-EPC-00GCA-ME-CAL-0001 | Demineralisation - Sizing and Hydraulic Calculation | ALP-EPC-00GCA-PR-SDS-0001 | Demineralisation - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00GCA-ME-CAL-0001 | Demineralisation - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | ALP-EPC-00GCA-PR-SDS-0001 | Demineralisation - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-04 | 58
ALP-EPC-00GHA-ME-CAL-0001 | Demineralised Water Storage and Distribution - Sizing and Hydraulic Calculation | ALP-EPC-00GHA-PR-SDS-0001 | Demineralised Water Storage and Distribution - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-08 | 49
ALP-EPC-00GHA-ME-CAL-0001 | Demineralised Water Storage and Distribution - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-08 | 19
ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | ALP-EPC-00GHA-PR-SDS-0001 | Demineralised Water Storage and Distribution - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-05 | 59
ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | ALP-EPC-00GHA-PR-SDS-0001 | Demineralised Water Storage and Distribution - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GKA-ME-CAL-0001 | Potable Water - Sizing and Hydraulic Calculation | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-07 | 48
ALP-EPC-00GKA-ME-CAL-0001 | Potable Water - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-07 | 18
ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-00GMA-ME-CAL-0001 | Process Drains and Waste Water Collection - Sizing and Hydraulic Calculation | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-21 | 35
ALP-EPC-00GMA-ME-CAL-0001 | Process Drains and Waste Water Collection - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-21 | 5
ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-25 | 30
ALP-EPC-00UZB-CV-CVL-0001 | Fencing and Gates - Civil Drawings | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00UZB-CV-CVL-0001 | Fencing and Gates - Civil Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00UZB-CV-CVL-0001 | Fencing and Gates - Civil Drawings | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00UZB-CV-CVL-0001 | Fencing and Gates - Civil Drawings | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-11-23 | 0
ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-EPC-00GNA-ME-CAL-0001 | Waste Water Treatment - Sizing and Hydraulic Calculation | ALP-EPC-00GNA-PR-SDS-0001 | Waste Water Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-25 | 39
ALP-EPC-00GNA-ME-CAL-0001 | Waste Water Treatment - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-25 | 9
ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | ALP-EPC-00GNA-PR-SDS-0001 | Waste Water Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-25 | 30
ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | ALP-EPC-00GNA-PR-SDS-0001 | Waste Water Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | ALP-EPC-00GUA-PR-SDS-0001 | Sanitary Waste Water Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GUA-ME-CAL-0001 | Sanitary Waste Water Treatment - Sizing and Hydraulic Calculation | ALP-EPC-00GUA-PR-SDS-0001 | Sanitary Waste Water Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-18 | 34
ALP-EPC-00GUA-ME-CAL-0001 | Sanitary Waste Water Treatment - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-18 | 4
ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | ALP-EPC-00GUA-PR-SDS-0001 | Sanitary Waste Water Treatment - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-00LBG-ME-CAL-0001 | Auxiliary Steam - Sizing and Hydraulic Calculation | ALP-EPC-00LBG-PR-SDS-0001 | Auxiliary Steam - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-00LBG-ME-CAL-0001 | Auxiliary Steam - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | ALP-EPC-00LBG-PR-SDS-0001 | Auxiliary Steam - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-05 | 59
ALP-EPC-00LDA-ME-CAL-0001 | Condensate Polishing - Sizing and Hydraulic Calculation | ALP-EPC-00LDA-PR-SDS-0001 | Condensate Polishing - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00LDA-ME-CAL-0001 | Condensate Polishing - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | ALP-EPC-00LDA-PR-SDS-0001 | Condensate Polishing - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | ALP-EPC-00GBA-PR-SDS-0001 | Seawater Reverse Osmosis - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | ALP-EPC-00GCA-PR-SDS-0001 | Demineralisation - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | ALP-EPC-00LDA-PR-SDS-0001 | Condensate Polishing - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-05 | 59
ALP-EPC-00PAA-ME-CAL-0001 | CW Intake, Screens and Outfall - Sizing and Hydraulic Calculation | ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-04 | 45
ALP-EPC-00PAA-ME-CAL-0001 | CW Intake, Screens and Outfall - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-04 | 15
ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-26 | 31
ALP-EPC-00PAA-PR-STU-0001 | CW Intake Hydraulic Model Study and Pump Sump Model Test | ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-27 | 19
ALP-EPC-00UPA-CV-CAL-0002 | Marine Structures Design: Hydrodynamics, Scour and Rock Protection | ALP-EPC-00000-PR-STU-0003 | CW Thermal Plume and Outfall Dispersion Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-12-07 | 0
ALP-EPC-00UPA-CV-CAL-0002 | Marine Structures Design: Hydrodynamics, Scour and Rock Protection | ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-07 | 25
ALP-EPC-00000-PI-SPC-0007 | GRP CW Pipes and Fittings - Technical Specification | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-SPC-0007 | GRP CW Pipes and Fittings - Technical Specification | ALP-EPC-00PAB-PR-SDS-0001 | CW Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAB-ME-CAL-0001 | CW Piping - Sizing and Hydraulic Calculation | ALP-EPC-00PAB-PR-SDS-0001 | CW Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00PAB-ME-CAL-0001 | CW Piping - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | ALP-EPC-00PAB-PR-SDS-0001 | CW Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-05 | 59
ALP-EPC-00PAC-ME-CAL-0001 | CW Pumps - Sizing and Hydraulic Calculation | ALP-EPC-00PAC-PR-SDS-0001 | CW Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00PAC-ME-CAL-0001 | CW Pumps - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification | ALP-EPC-00PAC-PR-SDS-0001 | CW Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | ALP-EPC-00PAC-PR-SDS-0001 | CW Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-05 | 59
ALP-EPC-00PAH-ME-CAL-0001 | Condenser Tube Cleaning - Sizing and Hydraulic Calculation | ALP-EPC-00PAH-PR-SDS-0001 | Condenser Tube Cleaning - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-27 | 62
ALP-EPC-00PAH-ME-CAL-0001 | Condenser Tube Cleaning - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-27 | 32
ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | ALP-EPC-00PAH-PR-SDS-0001 | Condenser Tube Cleaning - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | ALP-EPC-00PAH-PR-SDS-0001 | Condenser Tube Cleaning - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-05 | 59
ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | ALP-EPC-00PBA-PR-SDS-0001 | Electro-Chlorination - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-05 | 46
ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-05 | 16
ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | ALP-EPC-00PBA-PR-SDS-0001 | Electro-Chlorination - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | ALP-EPC-00PBA-PR-SDS-0001 | Electro-Chlorination - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-26 | 31
ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation | ALP-EPC-00PGA-PR-SDS-0001 | Closed Cooling Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-05 | 46
ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-05 | 16
ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | ALP-EPC-00PGA-PR-SDS-0001 | Closed Cooling Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-29 | 41
ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | ALP-EPC-00PGA-PR-SDS-0001 | Closed Cooling Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-29 | 41
ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-29 | 11
ALP-EPC-00QCA-ME-CAL-0001 | Chemical Dosing - Sizing and Hydraulic Calculation | ALP-EPC-00QCA-PR-SDS-0001 | Chemical Dosing - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-27 | 62
ALP-EPC-00QCA-ME-CAL-0001 | Chemical Dosing - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-27 | 32
ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | ALP-EPC-00QCA-PR-SDS-0001 | Chemical Dosing - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | ALP-EPC-00QCA-PR-SDS-0001 | Chemical Dosing - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-26 | 31
ALP-EPC-00QEA-ME-CAL-0001 | Compressed Air - Sizing and Hydraulic Calculation | ALP-EPC-00QEA-PR-SDS-0001 | Compressed Air - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-07 | 48
ALP-EPC-00QEA-ME-CAL-0001 | Compressed Air - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-07 | 18
ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | ALP-EPC-00QEA-PR-SDS-0001 | Compressed Air - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | ALP-EPC-00QEA-PR-SDS-0001 | Compressed Air - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-26 | 31
ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation | ALP-EPC-00QHA-PR-SDS-0001 | Auxiliary Boiler - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | ALP-EPC-00QHA-PR-SDS-0001 | Auxiliary Boiler - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-11 | 73
ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | ALP-EPC-00QHA-PR-SDS-0001 | Auxiliary Boiler - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-11 | 73
ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-11 | 43
ALP-EPC-00QJA-ME-CAL-0001 | Nitrogen Supply - Sizing and Hydraulic Calculation | ALP-EPC-00QJA-PR-SDS-0001 | Nitrogen Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-09 | 71
ALP-EPC-00QJA-ME-CAL-0001 | Nitrogen Supply - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-09 | 41
ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-23 | 101
ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | ALP-EPC-00QJA-PR-SDS-0001 | Nitrogen Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-23 | 101
ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-23 | 71
ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | ALP-EPC-00QJA-PR-SDS-0001 | Nitrogen Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | ALP-EPC-00QJB-PR-SDS-0001 | Hydrogen and CO2 Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QJB-ME-CAL-0001 | Hydrogen and CO2 Supply - Sizing and Hydraulic Calculation | ALP-EPC-00QJB-PR-SDS-0001 | Hydrogen and CO2 Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-09 | 71
ALP-EPC-00QJB-ME-CAL-0001 | Hydrogen and CO2 Supply - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-09 | 41
ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-24 | 102
ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | ALP-EPC-00QJB-PR-SDS-0001 | Hydrogen and CO2 Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-24 | 102
ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-24 | 72
ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification | ALP-EPC-00QUA-PR-SDS-0001 | Sampling and SWAS - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QUA-ME-CAL-0001 | Sampling and SWAS - Sizing and Hydraulic Calculation | ALP-EPC-00QUA-PR-SDS-0001 | Sampling and SWAS - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-08 | 70
ALP-EPC-00QUA-ME-CAL-0001 | Sampling and SWAS - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-08 | 40
ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-25 | 103
ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | ALP-EPC-00QUA-PR-SDS-0001 | Sampling and SWAS - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-25 | 103
ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-25 | 73
ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | ALP-EPC-00SAA-HV-SDS-0001 | HVAC - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | ALP-EPC-00SAA-HV-SDS-0001 | HVAC - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | ALP-EPC-00SAA-HV-SDS-0001 | HVAC - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | ALP-EPC-00EGB-PR-SDS-0001 | LDO Storage - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00SGA-ME-CAL-0001 | Fire Water System - Sizing and Hydraulic Calculation | ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SGA-ME-CAL-0001 | Fire Water System - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | ALP-EPC-00SGC-PR-SDS-0001 | Deluge, Spray and Foam Systems - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00SGC-ME-CAL-0001 | Deluge, Spray and Foam Systems - Sizing and Hydraulic Calculation | ALP-EPC-00SGC-PR-SDS-0001 | Deluge, Spray and Foam Systems - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SGC-ME-CAL-0001 | Deluge, Spray and Foam Systems - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | ALP-EPC-00SGC-PR-SDS-0001 | Deluge, Spray and Foam Systems - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-10HAN-ME-CAL-0001 | HRSG Blowdown and Drains - Sizing and Hydraulic Calculation | ALP-EPC-10HAN-PR-SDS-0001 | HRSG Blowdown and Drains - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-27 | 62
ALP-EPC-10HAN-ME-CAL-0001 | HRSG Blowdown and Drains - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-27 | 32
ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | ALP-EPC-10HAN-PR-SDS-0001 | HRSG Blowdown and Drains - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-06 | 111
ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | ALP-EPC-10HAN-PR-SDS-0001 | HRSG Blowdown and Drains - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-06 | 111
ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-06 | 81
ALP-EPC-10HSB-ME-CAL-0001 | Ammonia Storage and Supply - Sizing and Hydraulic Calculation | ALP-EPC-10HSB-PR-SDS-0001 | Ammonia Storage and Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-07 | 48
ALP-EPC-10HSB-ME-CAL-0001 | Ammonia Storage and Supply - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-07 | 18
ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | ALP-EPC-10HSB-PR-SDS-0001 | Ammonia Storage and Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | ALP-EPC-10HSB-PR-SDS-0001 | Ammonia Storage and Supply - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-EPC-10LAB-ME-CAL-0001 | Feedwater Piping - Sizing and Hydraulic Calculation | ALP-EPC-10LAB-PR-SDS-0001 | Feedwater Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-10LAB-ME-CAL-0001 | Feedwater Piping - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | ALP-EPC-10LAB-PR-SDS-0001 | Feedwater Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-EPC-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Sizing and Hydraulic Calculation | ALP-EPC-10LAC-PR-SDS-0001 | Boiler Feed Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-EPC-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2026-12-14 | 0
ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification | ALP-EPC-10LAC-PR-SDS-0001 | Boiler Feed Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | ALP-EPC-10LAC-PR-SDS-0001 | Boiler Feed Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-10LAE-ME-CAL-0001 | HP Attemperation Spray Water - Sizing and Hydraulic Calculation | ALP-EPC-10LAE-PR-SDS-0001 | HP Attemperation Spray Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-03 | 67
ALP-EPC-10LAE-ME-CAL-0001 | HP Attemperation Spray Water - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-03 | 37
ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | ALP-EPC-10LAE-PR-SDS-0001 | HP Attemperation Spray Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-10LAF-ME-CAL-0001 | Reheat Attemperation Spray Water - Sizing and Hydraulic Calculation | ALP-EPC-10LAF-PR-SDS-0001 | Reheat Attemperation Spray Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-10LAF-ME-CAL-0001 | Reheat Attemperation Spray Water - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | ALP-EPC-10LAF-PR-SDS-0001 | Reheat Attemperation Spray Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-10LBA-ME-CAL-0001 | Main Steam Piping - Sizing and Hydraulic Calculation | ALP-EPC-10LBA-PR-SDS-0001 | Main Steam Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-10LBA-ME-CAL-0001 | Main Steam Piping - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-28 | 127
ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | ALP-EPC-10LBA-PR-SDS-0001 | Main Steam Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-28 | 127
ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-28 | 97
ALP-EPC-10LBB-ME-CAL-0001 | Hot Reheat Piping - Sizing and Hydraulic Calculation | ALP-EPC-10LBB-PR-SDS-0001 | Hot Reheat Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-10LBB-ME-CAL-0001 | Hot Reheat Piping - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-28 | 127
ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | ALP-EPC-10LBB-PR-SDS-0001 | Hot Reheat Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-28 | 127
ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-28 | 97
ALP-EPC-10LBC-ME-CAL-0001 | Cold Reheat Piping - Sizing and Hydraulic Calculation | ALP-EPC-10LBC-PR-SDS-0001 | Cold Reheat Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-10LBC-ME-CAL-0001 | Cold Reheat Piping - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-29 | 128
ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | ALP-EPC-10LBC-PR-SDS-0001 | Cold Reheat Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-29 | 128
ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-29 | 98
ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | ALP-EPC-10LBA-PR-SDS-0001 | Main Steam Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | ALP-EPC-10LBB-PR-SDS-0001 | Hot Reheat Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | ALP-EPC-10LBC-PR-SDS-0001 | Cold Reheat Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | ALP-EPC-10LBD-PR-SDS-0001 | LP Steam Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LBD-ME-CAL-0001 | LP Steam Piping - Sizing and Hydraulic Calculation | ALP-EPC-10LBD-PR-SDS-0001 | LP Steam Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-10LBD-ME-CAL-0001 | LP Steam Piping - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-30 | 129
ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | ALP-EPC-10LBD-PR-SDS-0001 | LP Steam Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-30 | 129
ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-30 | 99
ALP-EPC-20LCA-ME-CAL-0001 | Main Condensate Piping - Sizing and Hydraulic Calculation | ALP-EPC-20LCA-PR-SDS-0001 | Main Condensate Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-15 | 75
ALP-EPC-20LCA-ME-CAL-0001 | Main Condensate Piping - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-15 | 45
ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | ALP-EPC-20LCA-PR-SDS-0001 | Main Condensate Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Sizing and Hydraulic Calculation | ALP-EPC-20LCB-PR-SDS-0001 | Condensate Extraction Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-07 | 48
ALP-EPC-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-07 | 18
ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification | ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification | ALP-EPC-20LCB-PR-SDS-0001 | Condensate Extraction Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-05 | 132
ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | ALP-EPC-20LCB-PR-SDS-0001 | Condensate Extraction Pumps - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-05 | 132
ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-05 | 102
ALP-EPC-20MAN-ME-CAL-0001 | Turbine Bypass Stations and Piping - Sizing and Hydraulic Calculation | ALP-EPC-20MAN-PR-SDS-0001 | Turbine Bypass Stations and Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-15 | 75
ALP-EPC-20MAN-ME-CAL-0001 | Turbine Bypass Stations and Piping - Sizing and Hydraulic Calculation | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-15 | 45
ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | ALP-EPC-20MAN-PR-SDS-0001 | Turbine Bypass Stations and Piping - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-00000-EL-LST-0001 | Electrical Load List | ALP-EPC-00000-PR-LST-0001 | Equipment List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-EL-LST-0001 | Electrical Load List | ALP-IEC-10MBA-EL-LST-0001 | Power Island Electrical Load List | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2026-11-02 | -40
ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | ALP-EPC-00000-CV-SPC-0005 | Marine Works - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | ALP-EPC-00000-CV-SPC-0003 | Piling Works - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CV-TRP-0001 | Pile Load Test Report and Pile Design Confirmation | ALP-EPC-00000-CV-TST-0001 | Pile Load Test Procedure | EPC | IFR | IFC | NONE | 2027-05-13 | 2027-05-13 | 0
ALP-EPC-00000-GE-RPT-0002 | Civil and Building Works - Technical Bid Evaluation | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-03 | 23
ALP-EPC-00000-GE-RPT-0016 | Structural Steel Supply and Fabrication - Technical Bid Evaluation | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-01-13 | 47
ALP-EPC-00000-GE-RPT-0003 | Power and Control Cables - Technical Bid Evaluation | ALP-EPC-00000-EL-MRQ-0001 | Power and Control Cables - Material Requisition | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-02-22 | 31
ALP-E09-00BLA-ME-DSH-0001 | Cable Trays, Earthing and Lighting Materials - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-EL-MRQ-0002 | Cable Trays, Earthing and Lighting Materials - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-01-28 | 38
ALP-E09-00BLA-ME-ITP-0001 | Cable Trays, Earthing and Lighting Materials - Supplier Inspection and Test Plan | ALP-EPC-00000-EL-MRQ-0002 | Cable Trays, Earthing and Lighting Materials - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-01-28 | 38
ALP-E09-00BLA-ME-MDB-0001 | Cable Trays, Earthing and Lighting Materials - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-EL-MRQ-0002 | Cable Trays, Earthing and Lighting Materials - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-04-22 | 98
ALP-EPC-00CJG-GE-ITP-0001 | BOP Safety Instrumented System - Inspection and Test Plan | ALP-EPC-00CJG-GE-SPC-0001 | BOP Safety Instrumented System - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-15 | 10
ALP-EPC-00CJG-IC-DSH-0001 | Safety Instrumented Systems: Control System - Datasheet | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-EPC-00CJG-IC-DSH-0001 | Safety Instrumented Systems: Control System - Datasheet | ALP-EPC-00CJG-GE-SPC-0001 | BOP Safety Instrumented System - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-00CKA-GE-ITP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Inspection and Test Plan | ALP-EPC-00CKA-GE-SPC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-22 | 15
ALP-EPC-00CKA-IC-DSH-0001 | Historian, Performance Monitoring and Operator Training Simulator: Control System - Datasheet | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-EPC-00CKA-IC-DSH-0001 | Historian, Performance Monitoring and Operator Training Simulator: Control System - Datasheet | ALP-EPC-00CKA-GE-SPC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-00CQA-IC-DSH-0001 | Continuous Emission Monitoring: Analyser - Datasheet | ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CQA-IC-DSH-0001 | Continuous Emission Monitoring: Analyser - Datasheet | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CQA-IC-ITP-0001 | Continuous Emission Monitoring System - Inspection and Test Plan | ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CQA-IC-TRP-0001 | CEMS Certification, QAL1 / QAL2 and AST Reports | ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2029-02-12 | 595
ALP-EPC-00CYA-GE-ITP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Inspection and Test Plan | ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-03-04 | 6
ALP-EPC-00CYA-IC-DSH-0001 | Telecom, CCTV, Access Control, Security - Datasheet | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-24 | 82
ALP-EPC-00CYA-IC-DSH-0001 | Telecom, CCTV, Access Control, Security - Datasheet | ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-02-24 | 0
ALP-EPC-00000-GE-RPT-0008 | Instrument Installation Materials - Technical Bid Evaluation | ALP-EPC-00000-GE-MRQ-0003 | Instrument Installation Materials - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-05-12 | 23
ALP-I04-00000-ME-DSH-0001 | Field Instruments - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-IC-MRQ-0001 | Field Instruments - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-03-29 | 80
ALP-I04-00000-ME-ITP-0001 | Field Instruments - Supplier Inspection and Test Plan | ALP-EPC-00000-IC-MRQ-0001 | Field Instruments - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-03-29 | 80
ALP-I04-00000-ME-MDB-0001 | Field Instruments - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-IC-MRQ-0001 | Field Instruments - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-08-25 | 187
ALP-I05-00000-ME-DSH-0001 | Control Valves - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-IC-MRQ-0002 | Control Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-03-22 | 75
ALP-I05-00000-ME-ITP-0001 | Control Valves - Supplier Inspection and Test Plan | ALP-EPC-00000-IC-MRQ-0002 | Control Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-03-22 | 75
ALP-I05-00000-ME-MDB-0001 | Control Valves - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-IC-MRQ-0002 | Control Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-09-13 | 200
ALP-EPC-00BXA-GE-RPT-0001 | Cathodic Protection - Technical Bid Evaluation | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-04-20 | 33
ALP-EPC-00000-GE-RPT-0013 | Pipe Supports, Spring Hangers and Snubbers - Technical Bid Evaluation | ALP-EPC-00000-GE-MRQ-0006 | Pipe Supports, Spring Hangers and Snubbers - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-29 | 2027-05-06 | 28
ALP-EPC-00000-GE-RPT-0014 | Piping Specialty Items - Technical Bid Evaluation | ALP-EPC-00000-GE-MRQ-0007 | Piping Specialty Items - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-03-15 | 70
ALP-EPC-00000-GE-RPT-0015 | Safety and Relief Valves - Technical Bid Evaluation | ALP-EPC-00000-GE-MRQ-0008 | Safety and Relief Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-03-11 | 68
ALP-EPC-00000-GE-RPT-0011 | Piping Bulk Materials - Technical Bid Evaluation | ALP-EPC-00000-PI-MRQ-0001 | Piping Bulk Materials - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-01-07 | 23
ALP-EPC-00000-GE-RPT-0012 | Valves - Technical Bid Evaluation | ALP-EPC-00000-PI-MRQ-0003 | Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-02-22 | 42
ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | ALP-EPC-00000-GE-SPC-0004 | Painting and Insulation - Technical Specification | EPC | IFR | IFC | NONE | 2027-04-16 | 2027-04-16 | 0
ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | ALP-EPC-00000-GE-SPC-0005 | Mechanical and Piping Erection - Technical Specification | EPC | IFR | IFC | NONE | 2027-06-18 | 2027-06-18 | 0
ALP-EPC-00SMA-ME-DSH-0001 | Cranes and Hoists - Datasheet | ALP-EPC-00SMA-ME-SPC-0001 | EOT Cranes - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SMA-ME-DSH-0001 | Cranes and Hoists - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00SMA-ME-ITP-0001 | EOT Cranes - Inspection and Test Plan | ALP-EPC-00SMA-ME-SPC-0001 | EOT Cranes - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | ALP-EPC-10HNE-ME-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | ALP-EPC-10HNE-SS-SPC-0001 | Stack 65 m with Silencer - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CM-TRP-0004 | Operational Demonstration and Reliability Run Report | ALP-EPC-00000-CM-CMP-0004 | Operational Demonstration and Reliability Run Procedure | EPC | IFR | IFC | NONE | 2027-08-04 | 2029-03-28 | 430
ALP-EPC-00000-CM-OMM-0002 | Training Manuals and Courseware | ALP-EPC-00000-CM-PLN-0002 | Training Plan | EPC | IFR | IFC | NONE | 2027-11-25 | 2027-11-25 | 0
ALP-EPC-00000-CM-LST-0003 | Punch List at Taking-Over | ALP-EPC-00000-CM-PRC-0001 | Punch List and Completion Procedure | EPC | IFR | IFC | NONE | 2027-11-11 | 2027-11-11 | 0
ALP-EPC-00ACA-CM-MDB-0001 | 380 kV GIS Switchyard - System Turnover Dossier | ALP-EPC-00ACA-CM-CMP-0001 | 380 kV GIS Switchyard - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2028-01-04 | 266
ALP-EPC-00ACA-CM-OMM-0001 | 380 kV GIS Switchyard - Operating Procedures | ALP-EPC-00ACA-CM-CMP-0001 | 380 kV GIS Switchyard - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00BBA-CM-MDB-0001 | MV Switchgear 10.5 kV - System Turnover Dossier | ALP-EPC-00BBA-CM-CMP-0001 | MV Switchgear 10.5 kV - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2028-01-04 | 266
ALP-EPC-00BBA-CM-OMM-0001 | MV Switchgear 10.5 kV - Operating Procedures | ALP-EPC-00BBA-CM-CMP-0001 | MV Switchgear 10.5 kV - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00BFA-CM-MDB-0001 | LV Switchgear 0.4 kV - System Turnover Dossier | ALP-EPC-00BFA-CM-CMP-0001 | LV Switchgear 0.4 kV - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2028-01-04 | 266
ALP-EPC-00BFA-CM-OMM-0001 | LV Switchgear 0.4 kV - Operating Procedures | ALP-EPC-00BFA-CM-CMP-0001 | LV Switchgear 0.4 kV - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00BFT-CM-MDB-0001 | LV Transformers - System Turnover Dossier | ALP-EPC-00BFT-CM-CMP-0001 | LV Transformers - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2028-01-04 | 266
ALP-EPC-00BFT-CM-OMM-0001 | LV Transformers - Operating Procedures | ALP-EPC-00BFT-CM-CMP-0001 | LV Transformers - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00BLA-CM-MDB-0001 | Lighting and Small Power - System Turnover Dossier | ALP-EPC-00BLA-CM-CMP-0001 | Lighting and Small Power - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2028-01-04 | 266
ALP-EPC-00BLA-CM-OMM-0001 | Lighting and Small Power - Operating Procedures | ALP-EPC-00BLA-CM-CMP-0001 | Lighting and Small Power - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-29 | 1
ALP-EPC-00BMA-CM-MDB-0001 | Emergency LV Switchgear - System Turnover Dossier | ALP-EPC-00BMA-CM-CMP-0001 | Emergency LV Switchgear - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2028-01-04 | 266
ALP-EPC-00BMA-CM-OMM-0001 | Emergency LV Switchgear - Operating Procedures | ALP-EPC-00BMA-CM-CMP-0001 | Emergency LV Switchgear - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-01-04 | 5
ALP-EPC-00BRA-CM-MDB-0001 | UPS - System Turnover Dossier | ALP-EPC-00BRA-CM-CMP-0001 | UPS - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-07 | 2028-01-04 | 258
ALP-EPC-00BRA-CM-OMM-0001 | UPS - Operating Procedures | ALP-EPC-00BRA-CM-CMP-0001 | UPS - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-07 | 0
ALP-EPC-00BTA-CM-MDB-0001 | Batteries and DC 220 V - System Turnover Dossier | ALP-EPC-00BTA-CM-CMP-0001 | Batteries and DC 220 V - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-19 | 2028-01-04 | 250
ALP-EPC-00BTA-CM-OMM-0001 | Batteries and DC 220 V - Operating Procedures | ALP-EPC-00BTA-CM-CMP-0001 | Batteries and DC 220 V - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-19 | 2027-01-19 | 0
ALP-EPC-00BXA-CM-MDB-0001 | Earthing and Lightning Protection - System Turnover Dossier | ALP-EPC-00BXA-CM-CMP-0001 | Earthing and Lightning Protection - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-25 | 2028-01-04 | 246
ALP-EPC-00CJA-CM-MDB-0001 | Plant DCS - System Turnover Dossier | ALP-EPC-00CJA-CM-CMP-0001 | Plant DCS - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-05 | 2028-03-20 | 291
ALP-EPC-00CJA-CM-OMM-0001 | Plant DCS - Operating Procedures | ALP-EPC-00CJA-CM-CMP-0001 | Plant DCS - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-05 | 2027-02-09 | 2
ALP-EPC-00CJG-CM-MDB-0001 | Safety Instrumented Systems - System Turnover Dossier | ALP-EPC-00CJG-CM-CMP-0001 | Safety Instrumented Systems - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-16 | 2028-03-20 | 284
ALP-EPC-00CJG-CM-OMM-0001 | Safety Instrumented Systems - Operating Procedures | ALP-EPC-00CJG-CM-CMP-0001 | Safety Instrumented Systems - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-02-16 | 0
ALP-EPC-00CKA-CM-MDB-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Turnover Dossier | ALP-EPC-00CKA-CM-CMP-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-22 | 2028-03-20 | 280
ALP-EPC-00CKA-CM-OMM-0001 | Historian, Performance Monitoring and Operator Training Simulator - Operating Procedures | ALP-EPC-00CKA-CM-CMP-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-02-22 | 0
ALP-EPC-00CQA-CM-MDB-0001 | Continuous Emission Monitoring - System Turnover Dossier | ALP-EPC-00CQA-CM-CMP-0001 | Continuous Emission Monitoring - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-22 | 2028-03-20 | 280
ALP-EPC-00CQA-CM-OMM-0001 | Continuous Emission Monitoring - Operating Procedures | ALP-EPC-00CQA-CM-CMP-0001 | Continuous Emission Monitoring - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-03-05 | 9
ALP-EPC-00CYA-CM-MDB-0001 | Telecom, CCTV, Access Control, Security - System Turnover Dossier | ALP-EPC-00CYA-CM-CMP-0001 | Telecom, CCTV, Access Control, Security - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-22 | 2028-03-20 | 280
ALP-EPC-00CYA-CM-OMM-0001 | Telecom, CCTV, Access Control, Security - Operating Procedures | ALP-EPC-00CYA-CM-CMP-0001 | Telecom, CCTV, Access Control, Security - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-03-08 | 10
ALP-EPC-00SGY-CM-MDB-0001 | Fire Detection and Alarm - System Turnover Dossier | ALP-EPC-00SGY-CM-CMP-0001 | Fire Detection and Alarm - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-05 | 2028-04-17 | 291
ALP-EPC-00SGY-CM-OMM-0001 | Fire Detection and Alarm - Operating Procedures | ALP-EPC-00SGY-CM-CMP-0001 | Fire Detection and Alarm - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-08 | 1
ALP-EPC-00SMA-CM-MDB-0001 | Cranes and Hoists - System Turnover Dossier | ALP-EPC-00SMA-CM-CMP-0001 | Cranes and Hoists - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-08 | 2028-04-17 | 290
ALP-EPC-00XJA-CM-MDB-0001 | Emergency Diesel Generator - System Turnover Dossier | ALP-EPC-00XJA-CM-CMP-0001 | Emergency Diesel Generator - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-25 | 2028-01-04 | 246
ALP-EPC-00XJA-CM-OMM-0001 | Emergency Diesel Generator - Operating Procedures | ALP-EPC-00XJA-CM-CMP-0001 | Emergency Diesel Generator - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-10BBT-CM-MDB-0001 | GT Unit Auxiliary Transformer - System Turnover Dossier | ALP-EPC-10BBT-CM-CMP-0001 | GT Unit Auxiliary Transformer - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-25 | 2028-01-04 | 246
ALP-EPC-10BBT-CM-OMM-0001 | GT Unit Auxiliary Transformer - Operating Procedures | ALP-EPC-10BBT-CM-CMP-0001 | GT Unit Auxiliary Transformer - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-10HNE-CM-MDB-0001 | Stack 65 m with CEMS Platform and Silencer - System Turnover Dossier | ALP-EPC-10HNE-CM-CMP-0001 | Stack 65 m with CEMS Platform and Silencer - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-11 | 2028-04-17 | 287
ALP-EPC-20BBT-CM-MDB-0001 | ST Unit Auxiliary Transformer - System Turnover Dossier | ALP-EPC-20BBT-CM-CMP-0001 | ST Unit Auxiliary Transformer - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-25 | 2028-01-18 | 256
ALP-EPC-20BBT-CM-OMM-0001 | ST Unit Auxiliary Transformer - Operating Procedures | ALP-EPC-20BBT-CM-CMP-0001 | ST Unit Auxiliary Transformer - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00000-HS-RPT-0006 | Occupational Health and Safety Risk Assessment | ALP-EPC-00000-HS-HAZ-0001 | HAZID Report | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-04-02 | 47
ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification | ALP-EPC-00SGY-IC-BLK-0001 | Fire Detection and Alarm - System Architecture | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-03 | 37
ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-03 | 8
ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-03 | 67
ALP-EPC-00000-CM-CMP-0006 | Emission and Noise Test Procedure | ALP-EPC-00000-HS-STU-0001 | Noise Study | EPC | IFR | IFC | NONE | 2027-02-15 | 2027-07-22 | 113
ALP-EPC-00000-CM-CMP-0006 | Emission and Noise Test Procedure | ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-22 | 188
ALP-EPC-00000-HS-RPT-0002 | Constructability and Maintainability Review | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-03-08 | 65
ALP-EPC-00000-HS-RPT-0002 | Constructability and Maintainability Review | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-08 | 90
ALP-EPC-00000-ME-LST-0001 | Heavy and Oversized Piece List | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-12-07 | 0
ALP-EPC-00000-ME-PLN-0001 | Marine Operations Plan | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-12-07 | 0
ALP-EPC-00000-ME-RPT-0001 | Abnormal Load Route Survey and Transport Drawings | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-12-07 | 0
ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-12-07 | 0
ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-07 | 25
ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-07 | 10
ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings | ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-07 | 25
ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings | ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-07 | 25
ALP-EPC-00UZF-CV-RPT-0001 | Temporary Barge Landing Design Report and Removal Plan | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-12-07 | 0
ALP-EPC-00UZF-CV-RPT-0001 | Temporary Barge Landing Design Report and Removal Plan | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-07 | 10
ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-01 | 21
ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings | ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2026-12-01 | 0
ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings | ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2027-01-18 | 34
ALP-EPC-00UAC-SS-STL-0002 | GIS Building - Steel Structure Drawings | ALP-EPC-00UAC-CV-CAL-0001 | GIS Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-02-08 | 2027-02-08 | 0
ALP-EPC-00UAC-SS-STL-0002 | GIS Building - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-08 | 70
ALP-EPC-00UAC-SS-STL-0002 | GIS Building - Steel Structure Drawings | ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2027-02-08 | 49
ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-09 | 27
ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-09 | 2026-12-09 | 0
ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-09 | 2027-01-18 | 28
ALP-EPC-00UBA-PI-PPL-0001 | Electrical Building and Emergency Power - Piping General Arrangement | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-09 | 2027-05-12 | 110
ALP-EPC-00UBA-PI-PPL-0001 | Electrical Building and Emergency Power - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2027-05-12 | 103
ALP-EPC-00UBA-PI-PPL-0001 | Electrical Building and Emergency Power - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2027-05-12 | 105
ALP-EPC-00UBA-SS-STL-0002 | Electrical Building - Steel Structure Drawings | ALP-EPC-00UBA-CV-CAL-0001 | Electrical Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-02 | 2027-03-02 | 0
ALP-EPC-00UBA-SS-STL-0002 | Electrical Building - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-02 | 86
ALP-EPC-00UBA-SS-STL-0002 | Electrical Building - Steel Structure Drawings | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-09 | 2027-03-02 | 59
ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-15 | 31
ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2026-12-15 | 0
ALP-EPC-00UCA-CV-FND-0001 | Control Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00UCA-CV-FND-0001 | Control Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00UCA-CV-FND-0001 | Control Building - Foundation and Underground Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-01-18 | 24
ALP-EPC-00UCA-PI-PPL-0001 | Control, Administration and Workshop Buildings - Piping General Arrangement | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-05-12 | 106
ALP-EPC-00UCA-PI-PPL-0001 | Control, Administration and Workshop Buildings - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2027-05-12 | 103
ALP-EPC-00UCA-PI-PPL-0001 | Control, Administration and Workshop Buildings - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2027-05-12 | 105
ALP-EPC-00UCA-SS-STL-0002 | Control Building - Steel Structure Drawings | ALP-EPC-00UCA-CV-CAL-0001 | Control Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-31 | 2027-03-31 | 0
ALP-EPC-00UCA-SS-STL-0002 | Control Building - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-31 | 107
ALP-EPC-00UCA-SS-STL-0002 | Control Building - Steel Structure Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-03-31 | 76
ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-15 | 31
ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2026-12-15 | 0
ALP-EPC-00USA-CV-FND-0001 | Workshop and Warehouse - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00USA-CV-FND-0001 | Workshop and Warehouse - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00USA-CV-FND-0001 | Workshop and Warehouse - Foundation and Underground Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-01-18 | 24
ALP-EPC-00USA-SS-STL-0002 | Workshop and Warehouse - Steel Structure Drawings | ALP-EPC-00USA-CV-CAL-0001 | Workshop and Warehouse - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-31 | 2027-03-31 | 0
ALP-EPC-00USA-SS-STL-0002 | Workshop and Warehouse - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-31 | 107
ALP-EPC-00USA-SS-STL-0002 | Workshop and Warehouse - Steel Structure Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-03-31 | 76
ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-15 | 31
ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2026-12-15 | 0
ALP-EPC-00UYA-CV-FND-0001 | Administration Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00UYA-CV-FND-0001 | Administration Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00UYA-CV-FND-0001 | Administration Building - Foundation and Underground Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-01-18 | 24
ALP-EPC-00UYA-SS-STL-0002 | Administration Building - Steel Structure Drawings | ALP-EPC-00UYA-CV-CAL-0001 | Administration Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-04-02 | 2027-04-02 | 0
ALP-EPC-00UYA-SS-STL-0002 | Administration Building - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-02 | 109
ALP-EPC-00UYA-SS-STL-0002 | Administration Building - Steel Structure Drawings | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-04-02 | 78
ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-18 | 43
ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-18 | 83
ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings | ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-23 | 2027-03-18 | 61
ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2026-12-23 | 5
ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2026-12-23 | 3
ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-23 | 2026-12-23 | 0
ALP-EPC-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Structure Drawings | ALP-EPC-00UEG-CV-CAL-0001 | LDO Tank Farm Structures - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-02-25 | 2027-02-25 | 0
ALP-EPC-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-EPC-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Structure Drawings | ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-23 | 2027-02-25 | 46
ALP-EPC-00UEK-CV-ARC-0001 | Gas Station Structures - Architectural Drawings | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-01-13 | 12
ALP-EPC-00UEK-CV-ARC-0001 | Gas Station Structures - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-13 | 52
ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-04-28 | 72
ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-28 | 112
ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-04-28 | 87
ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2026-12-28 | 8
ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2026-12-28 | 6
ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00UEK-SS-STL-0001 | Gas Station Structures - Steel Structure Drawings | ALP-EPC-00UEK-CV-CAL-0001 | Gas Station Structures - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-04-27 | 2027-04-27 | 0
ALP-EPC-00UEK-SS-STL-0001 | Gas Station Structures - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-27 | 126
ALP-EPC-00UEK-SS-STL-0001 | Gas Station Structures - Steel Structure Drawings | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-04-27 | 86
ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-15 | 31
ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings | ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2026-12-15 | 0
ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-18 | 40
ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings | ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-01-18 | 24
ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2026-12-18 | 2
ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2026-12-18 | 0
ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2026-12-18 | 3
ALP-EPC-00UGA-SS-STL-0002 | Water Treatment Building and Basins - Steel Structure Drawings | ALP-EPC-00UGA-CV-CAL-0001 | Water Treatment Building and Basins - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-03-03 | 0
ALP-EPC-00UGA-SS-STL-0002 | Water Treatment Building and Basins - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-03 | 87
ALP-EPC-00UGA-SS-STL-0002 | Water Treatment Building and Basins - Steel Structure Drawings | ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-03-03 | 56
ALP-EPC-00UZF-CV-FND-0002 | Temporary Barge Landing - Piling Layout and Pile Schedule | ALP-EPC-00UPA-PI-LAY-0001 | Marine Works - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-04-27 | 85
ALP-EPC-00UZF-CV-FND-0002 | Temporary Barge Landing - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-27 | 111
ALP-EPC-00UZF-CV-FND-0002 | Temporary Barge Landing - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2027-04-27 | 91
ALP-EPC-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Structure Drawings | ALP-EPC-00UZF-CV-CAL-0001 | Temporary Barge Landing - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-05-21 | 2027-05-21 | 0
ALP-EPC-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-21 | 144
ALP-EPC-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Structure Drawings | ALP-EPC-00UPA-PI-LAY-0001 | Marine Works - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-05-21 | 103
ALP-EPC-00UPC-CV-ARC-0001 | CW Pump House - Architectural Drawings | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-03 | 2026-12-03 | 0
ALP-EPC-00UPC-CV-ARC-0001 | CW Pump House - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-03 | 23
ALP-EPC-00UPC-CV-FND-0002 | CW Pump House - Piling Layout and Pile Schedule | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-03 | 2026-12-21 | 12
ALP-EPC-00UPC-CV-FND-0002 | CW Pump House - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-21 | 20
ALP-EPC-00UPC-CV-FND-0002 | CW Pump House - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2026-12-21 | 0
ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2027-03-08 | 58
ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2027-03-08 | 56
ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-03 | 2027-03-08 | 67
ALP-EPC-00UPC-SS-STL-0001 | CW Pump House - Steel Structure Drawings | ALP-EPC-00UPC-CV-CAL-0001 | CW Pump House - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-02-09 | 2027-02-09 | 0
ALP-EPC-00UPC-SS-STL-0001 | CW Pump House - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-09 | 71
ALP-EPC-00UPC-SS-STL-0001 | CW Pump House - Steel Structure Drawings | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-03 | 2027-02-09 | 48
ALP-EPC-00UQA-CV-ARC-0001 | Utility Building - Architectural Drawings | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-22 | 2026-12-22 | 0
ALP-EPC-00UQA-CV-ARC-0001 | Utility Building - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-22 | 36
ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-09 | 16
ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-09 | 56
ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-22 | 2027-02-09 | 35
ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2026-12-22 | 4
ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2026-12-22 | 2
ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-22 | 2026-12-22 | 0
ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-22 | 2027-04-16 | 83
ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2027-04-16 | 85
ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2027-04-16 | 87
ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-22 | 2027-05-10 | 99
ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2027-05-10 | 101
ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2027-05-10 | 103
ALP-EPC-00UQA-SS-STL-0001 | Utility Building - Steel Structure Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-29 | 50
ALP-EPC-00UQA-SS-STL-0001 | Utility Building - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-29 | 105
ALP-EPC-00UQA-SS-STL-0001 | Utility Building - Steel Structure Drawings | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-22 | 2027-03-29 | 69
ALP-EPC-00UQA-SS-STL-0001 | Utility Building - Steel Structure Drawings | ALP-EPC-00UQA-CV-CAL-0001 | Utility Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-29 | 2027-03-29 | 0
ALP-EPC-00000-EL-LST-0002 | Construction Power Load List | ALP-EPC-00UZA-CV-CVL-0001 | Temporary Facilities and Construction Site Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2026-11-02 | -21
ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2026-12-18 | 2
ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2026-12-18 | 0
ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2026-12-18 | 13
ALP-EPC-00UZD-CV-FND-0001 | Pipe Racks and Pipe Sleepers - Foundation and Underground Drawings | ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2027-02-10 | 51
ALP-EPC-00UZD-CV-FND-0001 | Pipe Racks and Pipe Sleepers - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-10 | 17
ALP-EPC-00UZD-CV-FND-0001 | Pipe Racks and Pipe Sleepers - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-10 | 57
ALP-EPC-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Structure Drawings | ALP-EPC-00UZD-CV-CAL-0001 | Pipe Racks and Pipe Sleepers - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-02-10 | 2027-02-10 | 0
ALP-EPC-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-10 | 72
ALP-EPC-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Structure Drawings | ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2027-02-10 | 51
ALP-EPC-00UBF-CV-FND-0002 | Transformer Bays - Piling Layout and Pile Schedule | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2026-12-24 | 0
ALP-EPC-00UBF-CV-FND-0002 | Transformer Bays - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-24 | 23
ALP-EPC-00UBF-CV-FND-0002 | Transformer Bays - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2026-12-24 | 3
ALP-EPC-00UBF-SS-STL-0001 | Transformer Bays - Steel Structure Drawings | ALP-EPC-00UBF-CV-CAL-0001 | Transformer Bays - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00UBF-SS-STL-0001 | Transformer Bays - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-03 | 130
ALP-EPC-00UBF-SS-STL-0001 | Transformer Bays - Steel Structure Drawings | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-05-03 | 92
ALP-EPC-10UHA-CV-FND-0002 | HRSG Foundations and Structures - Piling Layout and Pile Schedule | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2026-12-24 | 0
ALP-EPC-10UHA-CV-FND-0002 | HRSG Foundations and Structures - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-24 | 23
ALP-EPC-10UHA-CV-FND-0002 | HRSG Foundations and Structures - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2026-12-24 | 3
ALP-EPC-10UHN-CV-FND-0002 | Stack Foundation - Piling Layout and Pile Schedule | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2026-12-24 | 0
ALP-EPC-10UHN-CV-FND-0002 | Stack Foundation - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-24 | 23
ALP-EPC-10UHN-CV-FND-0002 | Stack Foundation - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2026-12-24 | 3
ALP-EPC-10UMA-CV-ARC-0001 | Gas Turbine Hall - Architectural Drawings | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2026-12-24 | 0
ALP-EPC-10UMA-CV-ARC-0001 | Gas Turbine Hall - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-EPC-10UMA-CV-FND-0001 | Gas Turbine Hall - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-24 | 23
ALP-EPC-10UMA-CV-FND-0001 | Gas Turbine Hall - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2026-12-24 | 3
ALP-EPC-10UMA-CV-FND-0001 | Gas Turbine Hall - Piling Layout and Pile Schedule | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2026-12-24 | 0
ALP-EPC-10UMA-CV-FND-0001 | Gas Turbine Hall - Piling Layout and Pile Schedule | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2026-12-24 | 8
ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2027-03-02 | 54
ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2027-03-02 | 52
ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-03-02 | 48
ALP-EPC-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Structure Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-04-05 | 55
ALP-EPC-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-05 | 110
ALP-EPC-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Structure Drawings | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-04-05 | 72
ALP-EPC-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Structure Drawings | ALP-EPC-10UMA-CV-CAL-0001 | Gas Turbine Hall - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-04-05 | 2027-04-05 | 0
ALP-EPC-20UMB-CV-ARC-0001 | Steam Turbine Hall - Architectural Drawings | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-11 | 2026-12-11 | 0
ALP-EPC-20UMB-CV-ARC-0001 | Steam Turbine Hall - Architectural Drawings | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-11 | 29
ALP-EPC-20UMB-CV-FND-0001 | Steam Turbine Hall - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2026-12-28 | 25
ALP-EPC-20UMB-CV-FND-0001 | Steam Turbine Hall - Piling Layout and Pile Schedule | ALP-EPC-00000-CV-SPC-0002 | Piling Specification | EPC | IFR | IFC | NONE | 2026-12-21 | 2026-12-28 | 5
ALP-EPC-20UMB-CV-FND-0001 | Steam Turbine Hall - Piling Layout and Pile Schedule | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-11 | 2026-12-28 | 11
ALP-EPC-20UMB-CV-FND-0001 | Steam Turbine Hall - Piling Layout and Pile Schedule | ALP-IEC-20MAA-CV-CAL-0001 | Steam Turbine and Condenser - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2026-12-16 | 2027-03-03 | 55
ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | EPC | IFR | IFC | NONE | 2026-12-18 | 2027-03-03 | 53
ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-11 | 2027-03-03 | 58
ALP-EPC-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Structure Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-04-05 | 55
ALP-EPC-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Structure Drawings | ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-05 | 110
ALP-EPC-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Structure Drawings | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-11 | 2027-04-05 | 81
ALP-EPC-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Structure Drawings | ALP-EPC-20UMB-CV-CAL-0001 | Steam Turbine Hall - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-04-05 | 2027-04-05 | 0
ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-25 | 103
ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-03-25 | 0
ALP-EPC-00EGA-IC-DSH-0001 | LDO Unloading - Instrument Datasheets | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-03-25 | 0
ALP-EPC-00EGA-IC-DSH-0001 | LDO Unloading - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-25 | 83
ALP-EPC-00EGA-IC-DSH-0002 | LDO Unloading - Control Valve Sizing and Datasheets | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-03-25 | 0
ALP-EPC-00EGA-IC-DSH-0002 | LDO Unloading - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-25 | 83
ALP-EPC-00EGA-IC-DSH-0002 | LDO Unloading - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-25 | 73
ALP-EPC-00EGA-PR-DSH-0001 | LDO Unloading - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-04-05 | 7
ALP-EPC-00EGA-PR-DSH-0001 | LDO Unloading - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-05 | 80
ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-06 | 111
ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-04-06 | 0
ALP-EPC-00EGB-IC-DSH-0001 | LDO Storage - Instrument Datasheets | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-04-06 | 0
ALP-EPC-00EGB-IC-DSH-0001 | LDO Storage - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-06 | 91
ALP-EPC-00EGB-PR-DSH-0001 | LDO Storage - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-05-06 | 22
ALP-EPC-00EGB-PR-DSH-0001 | LDO Storage - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-06 | 103
ALP-EPC-00EGA-ME-DSH-0001 | LDO Unloading: Package - Datasheet | ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2026-11-02 | -48
ALP-EPC-00EGA-ME-DSH-0001 | LDO Unloading: Package - Datasheet | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGA-ME-DSH-0001 | LDO Unloading: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00EGA-ME-DSH-0002 | LDO Unloading: Filters - Datasheet | ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-11 | 2
ALP-EPC-00EGA-ME-DSH-0002 | LDO Unloading: Filters - Datasheet | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00EGA-ME-DSH-0002 | LDO Unloading: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00EGA-ME-DSH-0003 | LDO Unloading: Pumps - Datasheet | ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-11 | 2
ALP-EPC-00EGA-ME-DSH-0003 | LDO Unloading: Pumps - Datasheet | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00EGA-ME-DSH-0003 | LDO Unloading: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00EGA-ME-DSH-0004 | LDO Unloading: Tank - Datasheet | ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-11 | 2
ALP-EPC-00EGA-ME-DSH-0004 | LDO Unloading: Tank - Datasheet | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00EGA-ME-DSH-0004 | LDO Unloading: Tank - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00EGA-ME-ITP-0001 | LDO Unloading and Forwarding / Treatment Skids - Inspection and Test Plan | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGC-ME-DSH-0001 | LDO Forwarding and Treatment: Package - Datasheet | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGC-ME-DSH-0001 | LDO Forwarding and Treatment: Package - Datasheet | ALP-EPC-00EGC-ME-CAL-0001 | LDO Forwarding and Treatment - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-12 | 2026-11-02 | -51
ALP-EPC-00EGC-ME-DSH-0001 | LDO Forwarding and Treatment: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00EGC-ME-DSH-0002 | LDO Forwarding and Treatment: Filters - Datasheet | ALP-EPC-00EGC-ME-CAL-0001 | LDO Forwarding and Treatment - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-12 | 2027-01-12 | 0
ALP-EPC-00EGC-ME-DSH-0002 | LDO Forwarding and Treatment: Filters - Datasheet | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-12 | 51
ALP-EPC-00EGC-ME-DSH-0002 | LDO Forwarding and Treatment: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-12 | 1
ALP-EPC-00EGC-ME-DSH-0003 | LDO Forwarding and Treatment: Pumps - Datasheet | ALP-EPC-00EGC-ME-CAL-0001 | LDO Forwarding and Treatment - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-12 | 2027-01-12 | 0
ALP-EPC-00EGC-ME-DSH-0003 | LDO Forwarding and Treatment: Pumps - Datasheet | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-12 | 51
ALP-EPC-00EGC-ME-DSH-0003 | LDO Forwarding and Treatment: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-12 | 1
ALP-EPC-00000-CM-CMP-0005 | Tests on LDO Procedure | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-07-20 | 124
ALP-EPC-00000-CM-CMP-0005 | Tests on LDO Procedure | ALP-IEC-10MBA-PR-PID-0001 | Gas Turbine Package incl. Auxiliaries - Supplier P&IDs | IEC | IFR | ACCEPTED | NONE | 2027-01-11 | 2027-07-20 | 136
ALP-EPC-00000-CM-CMP-0005 | Tests on LDO Procedure | ALP-IEC-10MBY-IC-CNR-0001 | Power Island Operating and Control Description | IEC | IFR | ACCEPTED | NONE | 2027-02-08 | 2027-07-20 | 116
ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-27 | 62
ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-01-27 | 0
ALP-EPC-00EGC-IC-DSH-0001 | LDO Forwarding and Treatment - Instrument Datasheets | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-01-27 | 0
ALP-EPC-00EGC-IC-DSH-0001 | LDO Forwarding and Treatment - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-27 | 42
ALP-EPC-00EGC-IC-DSH-0002 | LDO Forwarding and Treatment - Control Valve Sizing and Datasheets | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-01-27 | 0
ALP-EPC-00EGC-IC-DSH-0002 | LDO Forwarding and Treatment - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-27 | 42
ALP-EPC-00EGC-IC-DSH-0002 | LDO Forwarding and Treatment - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-27 | 32
ALP-EPC-00EGC-PR-DSH-0001 | LDO Forwarding and Treatment - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-01-27 | 0
ALP-EPC-00EGC-PR-DSH-0001 | LDO Forwarding and Treatment - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-27 | 32
ALP-EPC-00EKA-ME-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station: Package - Datasheet | ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-13 | 2026-11-02 | -52
ALP-EPC-00EKA-ME-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station: Package - Datasheet | ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EKA-ME-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00EKA-ME-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station: Filters - Datasheet | ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-13 | 2027-01-13 | 0
ALP-EPC-00EKA-ME-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station: Filters - Datasheet | ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-13 | 52
ALP-EPC-00EKA-ME-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-13 | 2
ALP-EPC-00EKA-ME-DSH-0003 | Gas Receiving, Filtration and Fiscal Metering Station: Heat Exchangers - Datasheet | ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-13 | 2027-01-13 | 0
ALP-EPC-00EKA-ME-DSH-0003 | Gas Receiving, Filtration and Fiscal Metering Station: Heat Exchangers - Datasheet | ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-13 | 52
ALP-EPC-00EKA-ME-DSH-0003 | Gas Receiving, Filtration and Fiscal Metering Station: Heat Exchangers - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-13 | 2
ALP-EPC-00EKA-ME-DSH-0004 | Gas Receiving, Filtration and Fiscal Metering Station: Tank - Datasheet | ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-13 | 2027-01-13 | 0
ALP-EPC-00EKA-ME-DSH-0004 | Gas Receiving, Filtration and Fiscal Metering Station: Tank - Datasheet | ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-13 | 52
ALP-EPC-00EKA-ME-DSH-0004 | Gas Receiving, Filtration and Fiscal Metering Station: Tank - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-13 | 2
ALP-EPC-00EKA-ME-ITP-0001 | Gas Receiving and Metering Station - Inspection and Test Plan | ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00EKA-IC-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Instrument Datasheets | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00EKA-IC-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-25 | 40
ALP-EPC-00EKA-IC-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station - Control Valve Sizing and Datasheets | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00EKA-IC-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-25 | 40
ALP-EPC-00EKA-IC-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-01-25 | 30
ALP-EPC-00EKA-PR-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-05-17 | 80
ALP-EPC-00EKA-PR-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-17 | 110
ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-04-09 | 54
ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-09 | 0
ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | ALP-IEC-10MBA-PR-PID-0001 | Gas Turbine Package incl. Auxiliaries - Supplier P&IDs | IEC | IFR | ACCEPTED | NONE | 2027-01-11 | 2027-04-09 | 64
ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-09 | 0
ALP-EPC-00EKC-IC-DSH-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Instrument Datasheets | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-09 | 0
ALP-EPC-00EKC-IC-DSH-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-09 | 94
ALP-EPC-00EKC-IC-DSH-0002 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Valve Sizing and Datasheets | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-09 | 0
ALP-EPC-00EKC-IC-DSH-0002 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-09 | 94
ALP-EPC-00EKC-IC-DSH-0002 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-EPC-00EKC-PR-DSH-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-26 | 11
ALP-EPC-00EKC-PR-DSH-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-26 | 95
ALP-EPC-00GBA-IC-CNR-0001 | Seawater Reverse Osmosis - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-01 | 85
ALP-EPC-00GBA-IC-CNR-0001 | Seawater Reverse Osmosis - Control Narrative | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-03-01 | 0
ALP-EPC-00GBA-IC-DSH-0001 | Seawater Reverse Osmosis - Instrument Datasheets | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-03-01 | 0
ALP-EPC-00GBA-IC-DSH-0001 | Seawater Reverse Osmosis - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-01 | 65
ALP-EPC-00GBA-IC-DSH-0002 | Seawater Reverse Osmosis - Control Valve Sizing and Datasheets | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-03-01 | 0
ALP-EPC-00GBA-IC-DSH-0002 | Seawater Reverse Osmosis - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-01 | 65
ALP-EPC-00GBA-IC-DSH-0002 | Seawater Reverse Osmosis - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-01 | 55
ALP-EPC-00GBA-PR-DSH-0001 | Seawater Reverse Osmosis - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-05-17 | 55
ALP-EPC-00GBA-PR-DSH-0001 | Seawater Reverse Osmosis - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-17 | 110
ALP-EPC-00GCA-IC-CNR-0001 | Demineralisation - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-EPC-00GCA-IC-CNR-0001 | Demineralisation - Control Narrative | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-09 | 0
ALP-EPC-00GCA-IC-DSH-0001 | Demineralisation - Instrument Datasheets | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-09 | 0
ALP-EPC-00GCA-IC-DSH-0001 | Demineralisation - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-09 | 94
ALP-EPC-00GCA-IC-DSH-0002 | Demineralisation - Control Valve Sizing and Datasheets | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-09 | 0
ALP-EPC-00GCA-IC-DSH-0002 | Demineralisation - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-09 | 94
ALP-EPC-00GCA-IC-DSH-0002 | Demineralisation - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-EPC-00GCA-PR-DSH-0001 | Demineralisation - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-05-14 | 25
ALP-EPC-00GCA-PR-DSH-0001 | Demineralisation - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-14 | 109
ALP-EPC-00GHA-IC-CNR-0001 | Demineralised Water Storage and Distribution - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00GHA-IC-CNR-0001 | Demineralised Water Storage and Distribution - Control Narrative | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00GHA-IC-DSH-0001 | Demineralised Water Storage and Distribution - Instrument Datasheets | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00GHA-IC-DSH-0001 | Demineralised Water Storage and Distribution - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-12 | 95
ALP-EPC-00GHA-IC-DSH-0002 | Demineralised Water Storage and Distribution - Control Valve Sizing and Datasheets | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00GHA-IC-DSH-0002 | Demineralised Water Storage and Distribution - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-12 | 95
ALP-EPC-00GHA-IC-DSH-0002 | Demineralised Water Storage and Distribution - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-00GHA-PR-DSH-0001 | Demineralised Water Storage and Distribution - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-17 | 25
ALP-EPC-00GHA-PR-DSH-0001 | Demineralised Water Storage and Distribution - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-17 | 110
ALP-EPC-00GHA-ME-DSH-0001 | Demineralised Water Storage and Distribution: Tanks - Datasheet | ALP-EPC-00GHA-ME-CAL-0001 | Demineralised Water Storage and Distribution - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-18 | 2026-11-02 | -78
ALP-EPC-00GHA-ME-DSH-0001 | Demineralised Water Storage and Distribution: Tanks - Datasheet | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-DSH-0001 | Demineralised Water Storage and Distribution: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GHA-ME-DSH-0002 | Demineralised Water Storage and Distribution: Pumps - Datasheet | ALP-EPC-00GHA-ME-CAL-0001 | Demineralised Water Storage and Distribution - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-18 | 2026-11-02 | -78
ALP-EPC-00GHA-ME-DSH-0002 | Demineralised Water Storage and Distribution: Pumps - Datasheet | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-DSH-0002 | Demineralised Water Storage and Distribution: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GHA-ME-ITP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Inspection and Test Plan | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GKA-ME-DSH-0001 | Potable Water: Tank - Datasheet | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GKA-ME-DSH-0001 | Potable Water: Tank - Datasheet | ALP-EPC-00GKA-ME-CAL-0001 | Potable Water - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-16 | 2026-11-02 | -76
ALP-EPC-00GKA-ME-DSH-0001 | Potable Water: Tank - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GKA-ME-DSH-0002 | Potable Water: Filters - Datasheet | ALP-EPC-00GKA-ME-CAL-0001 | Potable Water - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-02-16 | 0
ALP-EPC-00GKA-ME-DSH-0002 | Potable Water: Filters - Datasheet | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-16 | 76
ALP-EPC-00GKA-ME-DSH-0002 | Potable Water: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-02-16 | 26
ALP-EPC-00GKA-ME-DSH-0003 | Potable Water: Pumps - Datasheet | ALP-EPC-00GKA-ME-CAL-0001 | Potable Water - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-02-16 | 0
ALP-EPC-00GKA-ME-DSH-0003 | Potable Water: Pumps - Datasheet | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-16 | 76
ALP-EPC-00GKA-ME-DSH-0003 | Potable Water: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-02-16 | 26
ALP-EPC-00GKA-IC-CNR-0001 | Potable Water - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-17 | 140
ALP-EPC-00GKA-IC-CNR-0001 | Potable Water - Control Narrative | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-00GKA-IC-DSH-0001 | Potable Water - Instrument Datasheets | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-00GKA-IC-DSH-0001 | Potable Water - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-17 | 120
ALP-EPC-00GMA-IC-CNR-0001 | Process Drains and Waste Water Collection - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-EPC-00GMA-IC-CNR-0001 | Process Drains and Waste Water Collection - Control Narrative | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-03-04 | 0
ALP-EPC-00GMA-IC-DSH-0001 | Process Drains and Waste Water Collection - Instrument Datasheets | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-03-04 | 0
ALP-EPC-00GMA-IC-DSH-0001 | Process Drains and Waste Water Collection - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-04 | 68
ALP-EPC-00UZB-EL-ELY-0001 | Fencing and Gates - Earthing and Lightning Protection Layouts | ALP-EPC-00UZB-CV-CVL-0001 | Fencing and Gates - Civil Drawings | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-29 | 1
ALP-EPC-00UZB-EL-ELY-0001 | Fencing and Gates - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-29 | 1
ALP-EPC-00UZB-EL-ELY-0001 | Fencing and Gates - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2026-12-29 | 0
ALP-EPC-00GKA-PI-PPL-0001 | Potable Water - Underground Piping Drawings | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-00GKA-PI-PPL-0001 | Potable Water - Underground Piping Drawings | ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-05-17 | 64
ALP-EPC-00GMA-PI-PPL-0001 | Process Drains and Waste Water Collection - Underground Piping Drawings | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-05-12 | 49
ALP-EPC-00GMA-PI-PPL-0001 | Process Drains and Waste Water Collection - Underground Piping Drawings | ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-05-12 | 61
ALP-EPC-00UZC-CV-RBR-0001 | Site Drainage and Culverts - Reinforcement Drawings | ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-04-27 | 50
ALP-EPC-00UZC-EL-ELY-0001 | Site Drainage and Culverts - Earthing and Lightning Protection Layouts | ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-02-16 | 0
ALP-EPC-00UZC-EL-ELY-0001 | Site Drainage and Culverts - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-02-16 | 36
ALP-EPC-00UZC-EL-ELY-0001 | Site Drainage and Culverts - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-02-16 | 35
ALP-EPC-00UZE-CV-RBR-0001 | Cable Trenches and Duct Banks - Reinforcement Drawings | ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings | EPC | IFR | IFC | NONE | 2027-03-11 | 2027-04-27 | 33
ALP-EPC-00UZE-EL-ELY-0001 | Cable Trenches and Duct Banks - Earthing and Lightning Protection Layouts | ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings | EPC | IFR | IFC | NONE | 2027-03-11 | 2027-03-11 | 0
ALP-EPC-00UZE-EL-ELY-0001 | Cable Trenches and Duct Banks - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-03-11 | 53
ALP-EPC-00UZE-EL-ELY-0001 | Cable Trenches and Duct Banks - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-03-11 | 52
ALP-EPC-00GNA-IC-CNR-0001 | Waste Water Treatment - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00GNA-IC-CNR-0001 | Waste Water Treatment - Control Narrative | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00GNA-IC-DSH-0001 | Waste Water Treatment - Instrument Datasheets | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00GNA-IC-DSH-0001 | Waste Water Treatment - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-05 | 69
ALP-EPC-00GNA-IC-DSH-0002 | Waste Water Treatment - Control Valve Sizing and Datasheets | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00GNA-IC-DSH-0002 | Waste Water Treatment - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-05 | 69
ALP-EPC-00GNA-IC-DSH-0002 | Waste Water Treatment - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-05 | 59
ALP-EPC-00GMA-ME-DSH-0004 | Process Drains and Waste Water Collection: Filter - Datasheet | ALP-EPC-00GMA-ME-CAL-0001 | Process Drains and Waste Water Collection - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-18 | 0
ALP-EPC-00GMA-ME-DSH-0004 | Process Drains and Waste Water Collection: Filter - Datasheet | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-18 | 55
ALP-EPC-00GMA-ME-DSH-0004 | Process Drains and Waste Water Collection: Filter - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-18 | 5
ALP-EPC-00GMA-ME-DSH-0005 | Process Drains and Waste Water Collection: Pumps - Datasheet | ALP-EPC-00GMA-ME-CAL-0001 | Process Drains and Waste Water Collection - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-25 | 5
ALP-EPC-00GMA-ME-DSH-0005 | Process Drains and Waste Water Collection: Pumps - Datasheet | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00GMA-ME-DSH-0005 | Process Drains and Waste Water Collection: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-25 | 10
ALP-EPC-00GMA-ME-DSH-0006 | Process Drains and Waste Water Collection: Tank - Datasheet | ALP-EPC-00GMA-ME-CAL-0001 | Process Drains and Waste Water Collection - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-25 | 5
ALP-EPC-00GMA-ME-DSH-0006 | Process Drains and Waste Water Collection: Tank - Datasheet | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00GMA-ME-DSH-0006 | Process Drains and Waste Water Collection: Tank - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-25 | 10
ALP-EPC-00GNA-ME-DSH-0001 | Waste Water Treatment: Package - Datasheet | ALP-EPC-00GNA-ME-CAL-0001 | Waste Water Treatment - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-22 | 2026-11-02 | -59
ALP-EPC-00GNA-ME-DSH-0001 | Waste Water Treatment: Package - Datasheet | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-ME-DSH-0001 | Waste Water Treatment: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GNA-ME-DSH-0002 | Waste Water Treatment: Pumps - Datasheet | ALP-EPC-00GNA-ME-CAL-0001 | Waste Water Treatment - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-25 | 1
ALP-EPC-00GNA-ME-DSH-0002 | Waste Water Treatment: Pumps - Datasheet | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00GNA-ME-DSH-0002 | Waste Water Treatment: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-25 | 10
ALP-EPC-00GNA-ME-DSH-0003 | Waste Water Treatment: Tanks - Datasheet | ALP-EPC-00GNA-ME-CAL-0001 | Waste Water Treatment - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-27 | 3
ALP-EPC-00GNA-ME-DSH-0003 | Waste Water Treatment: Tanks - Datasheet | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-27 | 62
ALP-EPC-00GNA-ME-DSH-0003 | Waste Water Treatment: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-27 | 12
ALP-EPC-00GNA-ME-ITP-0001 | Waste Water and Sanitary Treatment Packages - Inspection and Test Plan | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GUA-ME-DSH-0001 | Sanitary Waste Water Treatment: Package - Datasheet | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GUA-ME-DSH-0001 | Sanitary Waste Water Treatment: Package - Datasheet | ALP-EPC-00GUA-ME-CAL-0001 | Sanitary Waste Water Treatment - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-19 | 2026-11-02 | -56
ALP-EPC-00GUA-ME-DSH-0001 | Sanitary Waste Water Treatment: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GUA-ME-DSH-0002 | Sanitary Waste Water Treatment: Pumps - Datasheet | ALP-EPC-00GUA-ME-CAL-0001 | Sanitary Waste Water Treatment - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-19 | 2027-01-27 | 6
ALP-EPC-00GUA-ME-DSH-0002 | Sanitary Waste Water Treatment: Pumps - Datasheet | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-27 | 62
ALP-EPC-00GUA-ME-DSH-0002 | Sanitary Waste Water Treatment: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-27 | 12
ALP-EPC-00GUA-IC-CNR-0001 | Sanitary Waste Water Treatment - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-17 | 140
ALP-EPC-00GUA-IC-CNR-0001 | Sanitary Waste Water Treatment - Control Narrative | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-00GUA-IC-DSH-0001 | Sanitary Waste Water Treatment - Instrument Datasheets | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-00GUA-IC-DSH-0001 | Sanitary Waste Water Treatment - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-17 | 120
ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00LBG-IC-DSH-0001 | Auxiliary Steam - Instrument Datasheets | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00LBG-IC-DSH-0001 | Auxiliary Steam - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-12 | 95
ALP-EPC-00LBG-IC-DSH-0002 | Auxiliary Steam - Control Valve Sizing and Datasheets | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00LBG-IC-DSH-0002 | Auxiliary Steam - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-12 | 95
ALP-EPC-00LBG-IC-DSH-0002 | Auxiliary Steam - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-12 | 85
ALP-EPC-00LBG-PR-DSH-0001 | Auxiliary Steam - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-17 | 25
ALP-EPC-00LBG-PR-DSH-0001 | Auxiliary Steam - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-17 | 110
ALP-EPC-00GBA-ME-DSH-0001 | Seawater Reverse Osmosis: Package - Datasheet | ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GBA-ME-DSH-0001 | Seawater Reverse Osmosis: Package - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GBA-ME-DSH-0001 | Seawater Reverse Osmosis: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GBA-ME-DSH-0002 | Seawater Reverse Osmosis: Filters - Datasheet | ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00GBA-ME-DSH-0002 | Seawater Reverse Osmosis: Filters - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00GBA-ME-DSH-0002 | Seawater Reverse Osmosis: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00GBA-ME-DSH-0003 | Seawater Reverse Osmosis: Pumps - Datasheet | ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00GBA-ME-DSH-0003 | Seawater Reverse Osmosis: Pumps - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00GBA-ME-DSH-0003 | Seawater Reverse Osmosis: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00GBA-ME-DSH-0004 | Seawater Reverse Osmosis: Tank - Datasheet | ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00GBA-ME-DSH-0004 | Seawater Reverse Osmosis: Tank - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00GBA-ME-DSH-0004 | Seawater Reverse Osmosis: Tank - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00GCA-ME-DSH-0001 | Demineralisation: Package - Datasheet | ALP-EPC-00GCA-ME-CAL-0001 | Demineralisation - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2026-11-02 | -48
ALP-EPC-00GCA-ME-DSH-0001 | Demineralisation: Package - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GCA-ME-DSH-0001 | Demineralisation: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00GCA-ME-DSH-0002 | Demineralisation: Filters - Datasheet | ALP-EPC-00GCA-ME-CAL-0001 | Demineralisation - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-11 | 2
ALP-EPC-00GCA-ME-DSH-0002 | Demineralisation: Filters - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00GCA-ME-DSH-0002 | Demineralisation: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00GCA-ME-DSH-0003 | Demineralisation: Pumps - Datasheet | ALP-EPC-00GCA-ME-CAL-0001 | Demineralisation - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-11 | 2
ALP-EPC-00GCA-ME-DSH-0003 | Demineralisation: Pumps - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00GCA-ME-DSH-0003 | Demineralisation: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00LDA-ME-DSH-0001 | Condensate Polishing: Package - Datasheet | ALP-EPC-00LDA-ME-CAL-0001 | Condensate Polishing - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2026-11-02 | -48
ALP-EPC-00LDA-ME-DSH-0001 | Condensate Polishing: Package - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-DSH-0001 | Condensate Polishing: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00LDA-ME-DSH-0002 | Condensate Polishing: Filters - Datasheet | ALP-EPC-00LDA-ME-CAL-0001 | Condensate Polishing - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-11 | 2
ALP-EPC-00LDA-ME-DSH-0002 | Condensate Polishing: Filters - Datasheet | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00LDA-ME-DSH-0002 | Condensate Polishing: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00LDA-ME-ITP-0001 | Water Treatment Package - Inspection and Test Plan | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-IC-CNR-0001 | Condensate Polishing - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00LDA-IC-CNR-0001 | Condensate Polishing - Control Narrative | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00LDA-IC-DSH-0001 | Condensate Polishing - Instrument Datasheets | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-13 | 1
ALP-EPC-00LDA-IC-DSH-0001 | Condensate Polishing - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-13 | 96
ALP-EPC-00LDA-IC-DSH-0002 | Condensate Polishing - Control Valve Sizing and Datasheets | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-13 | 1
ALP-EPC-00LDA-IC-DSH-0002 | Condensate Polishing - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-13 | 96
ALP-EPC-00LDA-IC-DSH-0002 | Condensate Polishing - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-04-13 | 86
ALP-EPC-00LDA-PR-DSH-0001 | Condensate Polishing - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-17 | 25
ALP-EPC-00LDA-PR-DSH-0001 | Condensate Polishing - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-17 | 110
ALP-EPC-00PAA-ME-DSH-0001 | CW Intake, Screens and Outfall: Filters - Datasheet | ALP-EPC-00PAA-ME-CAL-0001 | CW Intake, Screens and Outfall - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2026-11-02 | -65
ALP-EPC-00PAA-ME-DSH-0001 | CW Intake, Screens and Outfall: Filters - Datasheet | ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAA-ME-DSH-0001 | CW Intake, Screens and Outfall: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PAA-ME-DSH-0002 | CW Intake, Screens and Outfall: Pumps - Datasheet | ALP-EPC-00PAA-ME-CAL-0001 | CW Intake, Screens and Outfall - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-00PAA-ME-DSH-0002 | CW Intake, Screens and Outfall: Pumps - Datasheet | ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-EPC-00PAA-ME-DSH-0002 | CW Intake, Screens and Outfall: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-02-01 | 15
ALP-EPC-00PAA-ME-DSH-0003 | CW Intake, Screens and Outfall: Valves - Datasheet | ALP-EPC-00PAA-ME-CAL-0001 | CW Intake, Screens and Outfall - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-00PAA-ME-DSH-0003 | CW Intake, Screens and Outfall: Valves - Datasheet | ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-EPC-00PAA-ME-DSH-0003 | CW Intake, Screens and Outfall: Valves - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-02-01 | 15
ALP-EPC-00PAA-ME-ITP-0001 | Travelling Band Screens and Trash Rakes - Inspection and Test Plan | ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAA-IC-CNR-0001 | CW Intake, Screens and Outfall - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00PAA-IC-CNR-0001 | CW Intake, Screens and Outfall - Control Narrative | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00PAA-IC-DSH-0001 | CW Intake, Screens and Outfall - Instrument Datasheets | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00PAA-IC-DSH-0001 | CW Intake, Screens and Outfall - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-05 | 69
ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings | ALP-EPC-00000-PI-PLT-0001 | Plot Plan | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-10 | 135
ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-10 | 120
ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings | ALP-EPC-00UPA-CV-CAL-0002 | Marine Structures Design: Hydrodynamics, Scour and Rock Protection | EPC | IFR | IFC | NONE | 2027-05-10 | 2027-05-10 | 0
ALP-EPC-00PAB-ME-DSH-0001 | CW Piping: Valves - Datasheet | ALP-EPC-00PAB-ME-CAL-0001 | CW Piping - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-05 | 2027-01-11 | 4
ALP-EPC-00PAB-ME-DSH-0001 | CW Piping: Valves - Datasheet | ALP-EPC-00000-PI-SPC-0007 | GRP CW Pipes and Fittings - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-11 | 30
ALP-EPC-00PAB-ME-DSH-0001 | CW Piping: Valves - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00PAB-IC-CNR-0001 | CW Piping - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00PAB-IC-CNR-0001 | CW Piping - Control Narrative | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00PAB-IC-DSH-0001 | CW Piping - Instrument Datasheets | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00PAB-IC-DSH-0001 | CW Piping - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-12 | 95
ALP-EPC-00PAB-PI-PPL-0001 | CW Piping - Underground Piping Drawings | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-14 | 24
ALP-EPC-00PAB-PI-PPL-0001 | CW Piping - Underground Piping Drawings | ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-05-14 | 63
ALP-EPC-00PAB-PR-STU-0001 | CW System Hydraulic Transient Analysis | ALP-EPC-00PAB-ME-CAL-0001 | CW Piping - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-05 | 2027-05-18 | 95
ALP-EPC-00PAB-PR-STU-0001 | CW System Hydraulic Transient Analysis | ALP-EPC-00PAC-ME-CAL-0001 | CW Pumps - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-05 | 2027-05-18 | 95
ALP-EPC-00PAC-ME-DSH-0001 | CW Pumps - Datasheet | ALP-EPC-00PAC-ME-CAL-0001 | CW Pumps - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-05 | 2026-11-02 | -46
ALP-EPC-00PAC-ME-DSH-0001 | CW Pumps - Datasheet | ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAC-ME-DSH-0001 | CW Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PAC-ME-ITP-0001 | CW Pumps - Inspection and Test Plan | ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAC-IC-CNR-0001 | CW Pumps - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-EPC-00PAC-IC-CNR-0001 | CW Pumps - Control Narrative | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-12 | 0
ALP-EPC-00PAC-IC-DSH-0001 | CW Pumps - Instrument Datasheets | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-04-15 | 3
ALP-EPC-00PAC-IC-DSH-0001 | CW Pumps - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-15 | 98
ALP-EPC-00PAH-ME-DSH-0001 | Condenser Tube Cleaning: Package - Datasheet | ALP-EPC-00PAH-ME-CAL-0001 | Condenser Tube Cleaning - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-26 | 2026-11-02 | -84
ALP-EPC-00PAH-ME-DSH-0001 | Condenser Tube Cleaning: Package - Datasheet | ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAH-ME-DSH-0001 | Condenser Tube Cleaning: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PAH-ME-DSH-0002 | Condenser Tube Cleaning: Filters - Datasheet | ALP-EPC-00PAH-ME-CAL-0001 | Condenser Tube Cleaning - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-26 | 2027-02-26 | 0
ALP-EPC-00PAH-ME-DSH-0002 | Condenser Tube Cleaning: Filters - Datasheet | ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-26 | 84
ALP-EPC-00PAH-ME-DSH-0002 | Condenser Tube Cleaning: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-02-26 | 34
ALP-EPC-00PAH-ME-DSH-0003 | Condenser Tube Cleaning: Pumps - Datasheet | ALP-EPC-00PAH-ME-CAL-0001 | Condenser Tube Cleaning - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-26 | 2027-02-26 | 0
ALP-EPC-00PAH-ME-DSH-0003 | Condenser Tube Cleaning: Pumps - Datasheet | ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-26 | 84
ALP-EPC-00PAH-ME-DSH-0003 | Condenser Tube Cleaning: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-02-26 | 34
ALP-EPC-00PAH-ME-ITP-0001 | Condenser Tube Cleaning System - Inspection and Test Plan | ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00PAH-IC-CNR-0001 | Condenser Tube Cleaning - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-13 | 116
ALP-EPC-00PAH-IC-CNR-0001 | Condenser Tube Cleaning - Control Narrative | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-04-13 | 0
ALP-EPC-00PAH-IC-DSH-0001 | Condenser Tube Cleaning - Instrument Datasheets | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-04-16 | 3
ALP-EPC-00PAH-IC-DSH-0001 | Condenser Tube Cleaning - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-16 | 99
ALP-EPC-00PBA-ME-DSH-0001 | Electro-Chlorination: Package - Datasheet | ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-29 | 2026-11-02 | -64
ALP-EPC-00PBA-ME-DSH-0001 | Electro-Chlorination: Package - Datasheet | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PBA-ME-DSH-0001 | Electro-Chlorination: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PBA-ME-DSH-0002 | Electro-Chlorination: Fans - Datasheet | ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-29 | 2027-01-29 | 0
ALP-EPC-00PBA-ME-DSH-0002 | Electro-Chlorination: Fans - Datasheet | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-29 | 64
ALP-EPC-00PBA-ME-DSH-0002 | Electro-Chlorination: Fans - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-29 | 14
ALP-EPC-00PBA-ME-DSH-0003 | Electro-Chlorination: Filters - Datasheet | ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-29 | 2027-01-29 | 0
ALP-EPC-00PBA-ME-DSH-0003 | Electro-Chlorination: Filters - Datasheet | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-29 | 64
ALP-EPC-00PBA-ME-DSH-0003 | Electro-Chlorination: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-29 | 14
ALP-EPC-00PBA-ME-DSH-0004 | Electro-Chlorination: Pumps - Datasheet | ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-29 | 2027-01-29 | 0
ALP-EPC-00PBA-ME-DSH-0004 | Electro-Chlorination: Pumps - Datasheet | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-29 | 64
ALP-EPC-00PBA-ME-DSH-0004 | Electro-Chlorination: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-29 | 14
ALP-EPC-00PBA-ME-DSH-0005 | Electro-Chlorination: Tanks - Datasheet | ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-29 | 2027-01-29 | 0
ALP-EPC-00PBA-ME-DSH-0005 | Electro-Chlorination: Tanks - Datasheet | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-29 | 64
ALP-EPC-00PBA-ME-DSH-0005 | Electro-Chlorination: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-29 | 14
ALP-EPC-00PBA-ME-ITP-0001 | Electro-Chlorination Package - Inspection and Test Plan | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PBA-IC-CNR-0001 | Electro-Chlorination - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00PBA-IC-CNR-0001 | Electro-Chlorination - Control Narrative | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00PBA-IC-DSH-0001 | Electro-Chlorination - Instrument Datasheets | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00PBA-IC-DSH-0001 | Electro-Chlorination - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-05 | 69
ALP-EPC-00PBA-IC-DSH-0002 | Electro-Chlorination - Control Valve Sizing and Datasheets | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00PBA-IC-DSH-0002 | Electro-Chlorination - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-05 | 69
ALP-EPC-00PBA-IC-DSH-0002 | Electro-Chlorination - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-05 | 59
ALP-EPC-00PGA-ME-DSH-0001 | Closed Cooling Water: Heat Exchangers - Datasheet | ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-09 | 2026-11-02 | -71
ALP-EPC-00PGA-ME-DSH-0001 | Closed Cooling Water: Heat Exchangers - Datasheet | ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-DSH-0001 | Closed Cooling Water: Heat Exchangers - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PGA-ME-DSH-0002 | Closed Cooling Water: Pumps - Datasheet | ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-09 | 2026-11-02 | -71
ALP-EPC-00PGA-ME-DSH-0002 | Closed Cooling Water: Pumps - Datasheet | ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-DSH-0002 | Closed Cooling Water: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PGA-ME-DSH-0003 | Closed Cooling Water: Tanks - Datasheet | ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-09 | 2026-11-02 | -71
ALP-EPC-00PGA-ME-DSH-0003 | Closed Cooling Water: Tanks - Datasheet | ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-DSH-0003 | Closed Cooling Water: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00PGA-ME-DSH-0004 | Closed Cooling Water: Filter - Datasheet | ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-09 | 2027-02-09 | 0
ALP-EPC-00PGA-ME-DSH-0004 | Closed Cooling Water: Filter - Datasheet | ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-09 | 71
ALP-EPC-00PGA-ME-DSH-0004 | Closed Cooling Water: Filter - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-02-09 | 21
ALP-EPC-00PGA-ME-ITP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Inspection and Test Plan | ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-03 | 1
ALP-EPC-00PGA-IC-CNR-0001 | Closed Cooling Water - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-EPC-00PGA-IC-CNR-0001 | Closed Cooling Water - Control Narrative | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-02-12 | 0
ALP-EPC-00PGA-IC-DSH-0001 | Closed Cooling Water - Instrument Datasheets | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-02-12 | 0
ALP-EPC-00PGA-IC-DSH-0001 | Closed Cooling Water - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-12 | 54
ALP-EPC-00PGA-IC-DSH-0002 | Closed Cooling Water - Control Valve Sizing and Datasheets | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-02-12 | 0
ALP-EPC-00PGA-IC-DSH-0002 | Closed Cooling Water - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-12 | 54
ALP-EPC-00PGA-IC-DSH-0002 | Closed Cooling Water - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-12 | 44
ALP-EPC-00PGA-PR-DSH-0001 | Closed Cooling Water - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-05-18 | 67
ALP-EPC-00PGA-PR-DSH-0001 | Closed Cooling Water - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-00QCA-ME-DSH-0001 | Chemical Dosing: Package - Datasheet | ALP-EPC-00QCA-ME-CAL-0001 | Chemical Dosing - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-03 | 2026-11-02 | -87
ALP-EPC-00QCA-ME-DSH-0001 | Chemical Dosing: Package - Datasheet | ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QCA-ME-DSH-0001 | Chemical Dosing: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QCA-ME-DSH-0002 | Chemical Dosing: Pumps - Datasheet | ALP-EPC-00QCA-ME-CAL-0001 | Chemical Dosing - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-03-03 | 0
ALP-EPC-00QCA-ME-DSH-0002 | Chemical Dosing: Pumps - Datasheet | ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-03 | 87
ALP-EPC-00QCA-ME-DSH-0002 | Chemical Dosing: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-03-03 | 37
ALP-EPC-00QCA-ME-DSH-0003 | Chemical Dosing: Tanks - Datasheet | ALP-EPC-00QCA-ME-CAL-0001 | Chemical Dosing - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-03-03 | 0
ALP-EPC-00QCA-ME-DSH-0003 | Chemical Dosing: Tanks - Datasheet | ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-03 | 87
ALP-EPC-00QCA-ME-DSH-0003 | Chemical Dosing: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-03-03 | 37
ALP-EPC-00QCA-ME-ITP-0001 | Chemical Dosing Skid - Inspection and Test Plan | ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-12 | 8
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-05-17 | 55
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-05-17 | 26
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-17 | 25
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-05-17 | 52
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-05-17 | 51
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-05-17 | 51
ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-05 | 89
ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00QCA-IC-DSH-0001 | Chemical Dosing - Instrument Datasheets | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-05 | 0
ALP-EPC-00QCA-IC-DSH-0001 | Chemical Dosing - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-05 | 69
ALP-EPC-00QCA-PR-DSH-0001 | Chemical Dosing - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-05-18 | 52
ALP-EPC-00QCA-PR-DSH-0001 | Chemical Dosing - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-00QEA-ME-DSH-0001 | Compressed Air: Compressors - Datasheet | ALP-EPC-00QEA-ME-CAL-0001 | Compressed Air - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-00QEA-ME-DSH-0001 | Compressed Air: Compressors - Datasheet | ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-ME-DSH-0001 | Compressed Air: Compressors - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QEA-ME-DSH-0002 | Compressed Air: Filters - Datasheet | ALP-EPC-00QEA-ME-CAL-0001 | Compressed Air - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-00QEA-ME-DSH-0002 | Compressed Air: Filters - Datasheet | ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-ME-DSH-0002 | Compressed Air: Filters - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QEA-ME-DSH-0003 | Compressed Air: Tanks - Datasheet | ALP-EPC-00QEA-ME-CAL-0001 | Compressed Air - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-00QEA-ME-DSH-0003 | Compressed Air: Tanks - Datasheet | ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-ME-DSH-0003 | Compressed Air: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QEA-ME-ITP-0001 | Air Compressors and Dryers - Inspection and Test Plan | ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-04 | 2
ALP-EPC-00QEA-IC-CNR-0001 | Compressed Air - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-08 | 90
ALP-EPC-00QEA-IC-CNR-0001 | Compressed Air - Control Narrative | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-03-08 | 0
ALP-EPC-00QEA-IC-DSH-0001 | Compressed Air - Instrument Datasheets | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-03-12 | 4
ALP-EPC-00QEA-IC-DSH-0001 | Compressed Air - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-12 | 74
ALP-EPC-00QEA-IC-DSH-0002 | Compressed Air - Control Valve Sizing and Datasheets | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-03-09 | 1
ALP-EPC-00QEA-IC-DSH-0002 | Compressed Air - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-09 | 71
ALP-EPC-00QEA-IC-DSH-0002 | Compressed Air - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-09 | 61
ALP-EPC-00QEA-PR-DSH-0001 | Compressed Air - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-05-18 | 51
ALP-EPC-00QEA-PR-DSH-0001 | Compressed Air - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-00QHA-ME-DSH-0001 | Auxiliary Boiler - Datasheet | ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-08 | 2026-11-02 | -49
ALP-EPC-00QHA-ME-DSH-0001 | Auxiliary Boiler - Datasheet | ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QHA-ME-DSH-0001 | Auxiliary Boiler - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QHA-ME-DSH-0002 | Auxiliary Boiler: Fan - Datasheet | ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-01-11 | 1
ALP-EPC-00QHA-ME-DSH-0002 | Auxiliary Boiler: Fan - Datasheet | ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00QHA-ME-DSH-0002 | Auxiliary Boiler: Fan - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00QHA-ME-DSH-0003 | Auxiliary Boiler: Pumps - Datasheet | ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-01-11 | 1
ALP-EPC-00QHA-ME-DSH-0003 | Auxiliary Boiler: Pumps - Datasheet | ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00QHA-ME-DSH-0003 | Auxiliary Boiler: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00QHA-ME-DSH-0004 | Auxiliary Boiler: Tanks - Datasheet | ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-01-11 | 1
ALP-EPC-00QHA-ME-DSH-0004 | Auxiliary Boiler: Tanks - Datasheet | ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00QHA-ME-DSH-0004 | Auxiliary Boiler: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00QHA-ME-ITP-0001 | Auxiliary Boiler - Inspection and Test Plan | ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QHA-IC-CNR-0001 | Auxiliary Boiler - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-24 | 102
ALP-EPC-00QHA-IC-CNR-0001 | Auxiliary Boiler - Control Narrative | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-03-24 | 0
ALP-EPC-00QHA-IC-DSH-0001 | Auxiliary Boiler - Instrument Datasheets | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-03-24 | 0
ALP-EPC-00QHA-IC-DSH-0001 | Auxiliary Boiler - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-24 | 82
ALP-EPC-00QHA-IC-DSH-0002 | Auxiliary Boiler - Control Valve Sizing and Datasheets | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-03-24 | 0
ALP-EPC-00QHA-IC-DSH-0002 | Auxiliary Boiler - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-24 | 82
ALP-EPC-00QHA-IC-DSH-0002 | Auxiliary Boiler - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-03-24 | 72
ALP-EPC-00QHA-PR-DSH-0001 | Auxiliary Boiler - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-05-18 | 39
ALP-EPC-00QHA-PR-DSH-0001 | Auxiliary Boiler - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-28 | 127
ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-04-28 | 0
ALP-EPC-00QJA-IC-DSH-0001 | Nitrogen Supply - Instrument Datasheets | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-05-27 | 21
ALP-EPC-00QJA-IC-DSH-0001 | Nitrogen Supply - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-27 | 128
ALP-EPC-00QJA-IC-DSH-0002 | Nitrogen Supply - Control Valve Sizing and Datasheets | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-06-07 | 28
ALP-EPC-00QJA-IC-DSH-0002 | Nitrogen Supply - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-07 | 135
ALP-EPC-00QJA-IC-DSH-0002 | Nitrogen Supply - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-06-07 | 125
ALP-EPC-00QJA-PR-DSH-0001 | Nitrogen Supply - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-05-18 | 14
ALP-EPC-00QJA-PR-DSH-0001 | Nitrogen Supply - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-00QJA-ME-DSH-0001 | Nitrogen Supply: Package - Datasheet | ALP-EPC-00QJA-ME-CAL-0001 | Nitrogen Supply - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-04 | 2026-11-02 | -88
ALP-EPC-00QJA-ME-DSH-0001 | Nitrogen Supply: Package - Datasheet | ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QJA-ME-DSH-0001 | Nitrogen Supply: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QJA-ME-DSH-0002 | Nitrogen Supply: Tank - Datasheet | ALP-EPC-00QJA-ME-CAL-0001 | Nitrogen Supply - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-03-04 | 0
ALP-EPC-00QJA-ME-DSH-0002 | Nitrogen Supply: Tank - Datasheet | ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-EPC-00QJA-ME-DSH-0002 | Nitrogen Supply: Tank - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-03-04 | 38
ALP-EPC-00QJA-ME-ITP-0001 | Nitrogen, Hydrogen and CO2 Supply - Inspection and Test Plan | ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00QJB-ME-DSH-0001 | Hydrogen and CO2 Supply: Package - Datasheet | ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QJB-ME-DSH-0001 | Hydrogen and CO2 Supply: Package - Datasheet | ALP-EPC-00QJB-ME-CAL-0001 | Hydrogen and CO2 Supply - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-03 | 2026-11-02 | -87
ALP-EPC-00QJB-ME-DSH-0001 | Hydrogen and CO2 Supply: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-30 | 129
ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-04-30 | 0
ALP-EPC-00QJB-IC-DSH-0001 | Hydrogen and CO2 Supply - Instrument Datasheets | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-06-08 | 27
ALP-EPC-00QJB-IC-DSH-0001 | Hydrogen and CO2 Supply - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-08 | 136
ALP-EPC-00QJB-IC-DSH-0002 | Hydrogen and CO2 Supply - Control Valve Sizing and Datasheets | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-06-08 | 27
ALP-EPC-00QJB-IC-DSH-0002 | Hydrogen and CO2 Supply - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-08 | 136
ALP-EPC-00QJB-IC-DSH-0002 | Hydrogen and CO2 Supply - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-06-08 | 126
ALP-EPC-00QJB-PR-DSH-0001 | Hydrogen and CO2 Supply - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-05-18 | 12
ALP-EPC-00QJB-PR-DSH-0001 | Hydrogen and CO2 Supply - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-00QUA-IC-ITP-0001 | Steam/Water Analysis System - Inspection and Test Plan | ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QUA-ME-DSH-0001 | Sampling and SWAS: Package - Datasheet | ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QUA-ME-DSH-0001 | Sampling and SWAS: Package - Datasheet | ALP-EPC-00QUA-ME-CAL-0001 | Sampling and SWAS - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-08 | 2026-11-02 | -90
ALP-EPC-00QUA-ME-DSH-0001 | Sampling and SWAS: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00QUA-ME-DSH-0002 | Sampling and SWAS: Heat Exchanger - Datasheet | ALP-EPC-00QUA-ME-CAL-0001 | Sampling and SWAS - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-03-08 | 0
ALP-EPC-00QUA-ME-DSH-0002 | Sampling and SWAS: Heat Exchanger - Datasheet | ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-08 | 90
ALP-EPC-00QUA-ME-DSH-0002 | Sampling and SWAS: Heat Exchanger - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-03-08 | 40
ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-06 | 133
ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-05-06 | 0
ALP-EPC-00QUA-IC-DSH-0001 | Sampling and SWAS - Instrument Datasheets | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-06-08 | 23
ALP-EPC-00QUA-IC-DSH-0001 | Sampling and SWAS - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-08 | 136
ALP-EPC-00UBA-HV-GAD-0001 | Electrical Building and Emergency Power - HVAC Layouts | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00UBA-HV-GAD-0001 | Electrical Building and Emergency Power - HVAC Layouts | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-09 | 2027-01-11 | 23
ALP-EPC-00UCA-HV-GAD-0001 | Control, Administration and Workshop Buildings - HVAC Layouts | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-03-29 | 55
ALP-EPC-00UCA-HV-GAD-0001 | Control, Administration and Workshop Buildings - HVAC Layouts | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-03-29 | 74
ALP-EPC-10UMA-HV-GAD-0001 | Power Block - GT and HRSG - HVAC Layouts | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-18 | 5
ALP-EPC-10UMA-HV-GAD-0001 | Power Block - GT and HRSG - HVAC Layouts | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-01-18 | 17
ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-02 | 66
ALP-EPC-00SAA-IC-DSH-0001 | HVAC - Instrument Datasheets | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00SAA-IC-DSH-0001 | HVAC - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-02 | 46
ALP-EPC-00SAA-IC-DSH-0002 | HVAC - Control Valve Sizing and Datasheets | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00SAA-IC-DSH-0002 | HVAC - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-02 | 46
ALP-EPC-00SAA-IC-DSH-0002 | HVAC - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-02-02 | 36
ALP-EPC-00SAA-PR-DSH-0001 | HVAC - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-05-18 | 75
ALP-EPC-00SAA-PR-DSH-0001 | HVAC - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-18 | 111
ALP-EPC-00SAA-HV-DSH-0001 | HVAC: Package - Datasheet | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00SAA-HV-DSH-0001 | HVAC: Package - Datasheet | ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SAA-HV-DSH-0001 | HVAC: Package - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00SAA-HV-ITP-0001 | HVAC Plant and Equipment - Inspection and Test Plan | ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SAA-ME-DSH-0001 | HVAC: Compressors - Datasheet | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-21 | 8
ALP-EPC-00SAA-ME-DSH-0001 | HVAC: Compressors - Datasheet | ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-21 | 58
ALP-EPC-00SAA-ME-DSH-0001 | HVAC: Compressors - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-21 | 8
ALP-EPC-00SAA-ME-DSH-0002 | HVAC: Fans - Datasheet | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-14 | 3
ALP-EPC-00SAA-ME-DSH-0002 | HVAC: Fans - Datasheet | ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-EPC-00SAA-ME-DSH-0002 | HVAC: Fans - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-14 | 3
ALP-EPC-00SAA-ME-DSH-0003 | HVAC: Pumps - Datasheet | ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-25 | 10
ALP-EPC-00SAA-ME-DSH-0003 | HVAC: Pumps - Datasheet | ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00SAA-ME-DSH-0003 | HVAC: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-25 | 10
ALP-EPC-00EGB-ME-DSH-0001 | LDO Storage: Tanks - Datasheet | ALP-EPC-00EGB-ME-CAL-0001 | LDO Storage - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-03-05 | 2026-11-02 | -89
ALP-EPC-00EGB-ME-DSH-0001 | LDO Storage: Tanks - Datasheet | ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGB-ME-DSH-0001 | LDO Storage: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00SGA-PR-CAL-0001 | Fire Water Network Hydraulic Calculation | ALP-EPC-00SGA-ME-CAL-0001 | Fire Water System - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-15 | 2027-05-18 | 87
ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-01-26 | 0
ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00SGA-IC-DSH-0001 | Fire Water System - Instrument Datasheets | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-01-26 | 0
ALP-EPC-00SGA-IC-DSH-0001 | Fire Water System - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-26 | 41
ALP-EPC-00SGA-PI-PPL-0001 | Fire Water System - Underground Piping Drawings | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-06-28 | 109
ALP-EPC-00SGA-PI-PPL-0001 | Fire Water System - Underground Piping Drawings | ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-06-28 | 94
ALP-EPC-00SGA-PR-DSH-0001 | Fire Water System - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-05-24 | 84
ALP-EPC-00SGA-PR-DSH-0001 | Fire Water System - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-24 | 115
ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | ALP-EPC-00SGA-ME-CAL-0001 | Fire Water System - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-15 | 2026-11-02 | -54
ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | ALP-EPC-00SGA-ME-CAL-0001 | Fire Water System - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-15 | 2026-11-02 | -54
ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-ITP-0001 | Fire Pumps and Fire Protection Systems - Inspection and Test Plan | ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGC-ME-DSH-0001 | Deluge, Spray and Foam Systems: Tank - Datasheet | ALP-EPC-00SGC-ME-CAL-0001 | Deluge, Spray and Foam Systems - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-13 | 2027-01-13 | 0
ALP-EPC-00SGC-ME-DSH-0001 | Deluge, Spray and Foam Systems: Tank - Datasheet | ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-13 | 52
ALP-EPC-00SGC-ME-DSH-0001 | Deluge, Spray and Foam Systems: Tank - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-13 | 2
ALP-EPC-00SGC-ME-DSH-0002 | Deluge, Spray and Foam Systems: Valves - Datasheet | ALP-EPC-00SGC-ME-CAL-0001 | Deluge, Spray and Foam Systems - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-13 | 2027-01-25 | 8
ALP-EPC-00SGC-ME-DSH-0002 | Deluge, Spray and Foam Systems: Valves - Datasheet | ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00SGC-ME-DSH-0002 | Deluge, Spray and Foam Systems: Valves - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-25 | 10
ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-04-30 | 55
ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-04-30 | 39
ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-04-30 | 27
ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-04-30 | 2
ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-04-30 | 0
ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-04-30 | 68
ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-04-30 | 68
ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-01-26 | 0
ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-EPC-00SGC-IC-DSH-0001 | Deluge, Spray and Foam Systems - Instrument Datasheets | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-01-26 | 0
ALP-EPC-00SGC-IC-DSH-0001 | Deluge, Spray and Foam Systems - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-01-26 | 41
ALP-EPC-10HAN-ME-DSH-0001 | HRSG Blowdown and Drains - Datasheet | ALP-EPC-10HAN-ME-CAL-0001 | HRSG Blowdown and Drains - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-26 | 2026-11-02 | -84
ALP-EPC-10HAN-ME-DSH-0001 | HRSG Blowdown and Drains - Datasheet | ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HAN-ME-DSH-0001 | HRSG Blowdown and Drains - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-10HAN-ME-DSH-0002 | HRSG Blowdown and Drains: Pumps - Datasheet | ALP-EPC-10HAN-ME-CAL-0001 | HRSG Blowdown and Drains - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-26 | 2027-02-26 | 0
ALP-EPC-10HAN-ME-DSH-0002 | HRSG Blowdown and Drains: Pumps - Datasheet | ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-26 | 84
ALP-EPC-10HAN-ME-DSH-0002 | HRSG Blowdown and Drains: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-02-26 | 34
ALP-EPC-10HAN-ME-ITP-0001 | HRSG Blowdown and Drain Tanks - Inspection and Test Plan | ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-11 | 7
ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-14 | 139
ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-05-14 | 0
ALP-EPC-10HAN-IC-DSH-0001 | HRSG Blowdown and Drains - Instrument Datasheets | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-07-05 | 36
ALP-EPC-10HAN-IC-DSH-0001 | HRSG Blowdown and Drains - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-07-05 | 155
ALP-EPC-10HAN-IC-DSH-0002 | HRSG Blowdown and Drains - Control Valve Sizing and Datasheets | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-06-29 | 32
ALP-EPC-10HAN-IC-DSH-0002 | HRSG Blowdown and Drains - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-29 | 151
ALP-EPC-10HAN-IC-DSH-0002 | HRSG Blowdown and Drains - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-06-29 | 141
ALP-EPC-10HAN-PR-DSH-0001 | HRSG Blowdown and Drains - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-05-26 | 8
ALP-EPC-10HAN-PR-DSH-0001 | HRSG Blowdown and Drains - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-26 | 117
ALP-EPC-10HSB-ME-DSH-0001 | Ammonia Storage and Supply: Tanks - Datasheet | ALP-EPC-10HSB-ME-CAL-0001 | Ammonia Storage and Supply - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-10HSB-ME-DSH-0001 | Ammonia Storage and Supply: Tanks - Datasheet | ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HSB-ME-DSH-0001 | Ammonia Storage and Supply: Tanks - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-10HSB-ME-DSH-0002 | Ammonia Storage and Supply: Pumps - Datasheet | ALP-EPC-10HSB-ME-CAL-0001 | Ammonia Storage and Supply - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-10HSB-ME-DSH-0002 | Ammonia Storage and Supply: Pumps - Datasheet | ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HSB-ME-DSH-0002 | Ammonia Storage and Supply: Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-10HSB-ME-ITP-0001 | Aqueous Ammonia Storage and Forwarding - Inspection and Test Plan | ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-06 | 4
ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-05-17 | 37
ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-05-17 | 29
ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-05-17 | 78
ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-17 | 140
ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-10HSB-IC-DSH-0001 | Ammonia Storage and Supply - Instrument Datasheets | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-24 | 94
ALP-EPC-10HSB-IC-DSH-0001 | Ammonia Storage and Supply - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-09-24 | 214
ALP-EPC-10HSB-IC-DSH-0002 | Ammonia Storage and Supply - Control Valve Sizing and Datasheets | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-24 | 94
ALP-EPC-10HSB-IC-DSH-0002 | Ammonia Storage and Supply - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-09-24 | 214
ALP-EPC-10HSB-IC-DSH-0002 | Ammonia Storage and Supply - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-09-24 | 204
ALP-EPC-10HSB-PR-DSH-0001 | Ammonia Storage and Supply - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-26 | 7
ALP-EPC-10HSB-PR-DSH-0001 | Ammonia Storage and Supply - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-26 | 117
ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-18 | 141
ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-18 | 0
ALP-EPC-10LAB-IC-DSH-0001 | Feedwater Piping - Instrument Datasheets | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-24 | 93
ALP-EPC-10LAB-IC-DSH-0001 | Feedwater Piping - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-09-24 | 214
ALP-EPC-10LAB-IC-DSH-0002 | Feedwater Piping - Control Valve Sizing and Datasheets | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-24 | 93
ALP-EPC-10LAB-IC-DSH-0002 | Feedwater Piping - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-09-24 | 214
ALP-EPC-10LAB-IC-DSH-0002 | Feedwater Piping - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-09-24 | 204
ALP-EPC-10LAB-PR-DSH-0001 | Feedwater Piping - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-27 | 7
ALP-EPC-10LAB-PR-DSH-0001 | Feedwater Piping - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-27 | 118
ALP-EPC-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Datasheet | ALP-EPC-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-01-06 | 2026-11-02 | -47
ALP-EPC-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Datasheet | ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-10LAC-ME-ITP-0001 | Boiler Feed Pumps - Inspection and Test Plan | ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-18 | 141
ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-18 | 0
ALP-EPC-10LAC-IC-DSH-0001 | Boiler Feed Pumps - Instrument Datasheets | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-29 | 96
ALP-EPC-10LAC-IC-DSH-0001 | Boiler Feed Pumps - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-09-29 | 217
ALP-EPC-10LAC-IC-DSH-0002 | Boiler Feed Pumps - Control Valve Sizing and Datasheets | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-29 | 96
ALP-EPC-10LAC-IC-DSH-0002 | Boiler Feed Pumps - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-09-29 | 217
ALP-EPC-10LAC-IC-DSH-0002 | Boiler Feed Pumps - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-09-29 | 207
ALP-EPC-10LAC-PR-DSH-0001 | Boiler Feed Pumps - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-27 | 7
ALP-EPC-10LAC-PR-DSH-0001 | Boiler Feed Pumps - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-27 | 118
ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-17 | 140
ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-10LAE-IC-DSH-0001 | HP Attemperation Spray Water - Instrument Datasheets | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-05-17 | 0
ALP-EPC-10LAE-IC-DSH-0001 | HP Attemperation Spray Water - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-17 | 120
ALP-EPC-10LAE-IC-DSH-0002 | HP Attemperation Spray Water - Control Valve Sizing and Datasheets | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-10-05 | 101
ALP-EPC-10LAE-IC-DSH-0002 | HP Attemperation Spray Water - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-05 | 221
ALP-EPC-10LAE-IC-DSH-0002 | HP Attemperation Spray Water - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-10-05 | 211
ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-18 | 141
ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-18 | 0
ALP-EPC-10LAF-IC-DSH-0001 | Reheat Attemperation Spray Water - Instrument Datasheets | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-08 | 103
ALP-EPC-10LAF-IC-DSH-0001 | Reheat Attemperation Spray Water - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-08 | 224
ALP-EPC-10LAF-IC-DSH-0002 | Reheat Attemperation Spray Water - Control Valve Sizing and Datasheets | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-08 | 103
ALP-EPC-10LAF-IC-DSH-0002 | Reheat Attemperation Spray Water - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-08 | 224
ALP-EPC-10LAF-IC-DSH-0002 | Reheat Attemperation Spray Water - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-10-08 | 214
ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-02 | 152
ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-06-02 | 0
ALP-EPC-10LBA-IC-DSH-0001 | Main Steam Piping - Instrument Datasheets | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-08 | 92
ALP-EPC-10LBA-IC-DSH-0001 | Main Steam Piping - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-08 | 224
ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-02 | 152
ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-06-02 | 0
ALP-EPC-10LBB-IC-DSH-0001 | Hot Reheat Piping - Instrument Datasheets | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-11 | 93
ALP-EPC-10LBB-IC-DSH-0001 | Hot Reheat Piping - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-11 | 225
ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-03 | 153
ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-06-03 | 0
ALP-EPC-10LBC-IC-DSH-0001 | Cold Reheat Piping - Instrument Datasheets | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-10-15 | 96
ALP-EPC-10LBC-IC-DSH-0001 | Cold Reheat Piping - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-15 | 229
ALP-EPC-00000-PI-MRQ-0002 | Alloy Piping P91 / P22 - Material Requisition | ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-30 | 0
ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-07 | 155
ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-07 | 0
ALP-EPC-10LBD-IC-DSH-0001 | LP Steam Piping - Instrument Datasheets | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-10-15 | 94
ALP-EPC-10LBD-IC-DSH-0001 | LP Steam Piping - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-15 | 229
ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-18 | 141
ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-18 | 0
ALP-EPC-20LCA-IC-DSH-0001 | Main Condensate Piping - Instrument Datasheets | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-20 | 111
ALP-EPC-20LCA-IC-DSH-0001 | Main Condensate Piping - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-20 | 232
ALP-EPC-20LCA-IC-DSH-0002 | Main Condensate Piping - Control Valve Sizing and Datasheets | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-22 | 113
ALP-EPC-20LCA-IC-DSH-0002 | Main Condensate Piping - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-22 | 234
ALP-EPC-20LCA-IC-DSH-0002 | Main Condensate Piping - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-10-22 | 224
ALP-EPC-20LCA-PR-DSH-0001 | Main Condensate Piping - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-28 | 8
ALP-EPC-20LCA-PR-DSH-0001 | Main Condensate Piping - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-28 | 119
ALP-EPC-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Datasheet | ALP-EPC-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Sizing and Hydraulic Calculation | EPC | IFR | IFC | NONE | 2027-02-16 | 2026-11-02 | -76
ALP-EPC-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Datasheet | ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2026-11-02 | -50
ALP-EPC-20LCB-ME-ITP-0001 | Condensate Extraction Pumps - Inspection and Test Plan | ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-09 | 5
ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-09 | 157
ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-06-09 | 0
ALP-EPC-20LCB-IC-DSH-0001 | Condensate Extraction Pumps - Instrument Datasheets | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-10-26 | 99
ALP-EPC-20LCB-IC-DSH-0001 | Condensate Extraction Pumps - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-26 | 236
ALP-EPC-20LCB-IC-DSH-0002 | Condensate Extraction Pumps - Control Valve Sizing and Datasheets | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-10-22 | 97
ALP-EPC-20LCB-IC-DSH-0002 | Condensate Extraction Pumps - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-22 | 234
ALP-EPC-20LCB-IC-DSH-0002 | Condensate Extraction Pumps - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-10-22 | 224
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-07-09 | 64
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-07-09 | 64
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-07-09 | 40
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-07-09 | 38
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-07-09 | 38
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-07-09 | 39
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-07-09 | 38
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-07-09 | 27
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-07-09 | 27
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-07-09 | 26
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-07-09 | 24
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-07-09 | 38
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-07-09 | 22
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-07-09 | 38
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | ALP-IEC-10HAA-PR-PID-0001 | HRSG incl. SCR - Supplier P&IDs | IEC | IFR | ACCEPTED | NONE | 2027-01-11 | 2027-07-09 | 129
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-28 | 238
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-10-28 | 155
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-10-28 | 147
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-10-28 | 196
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-10-28 | 198
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-10-28 | 144
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-10-28 | 173
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-10-28 | 144
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-10-28 | 143
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-10-28 | 118
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-10-28 | 170
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-10-28 | 169
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-10-28 | 118
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-10-28 | 143
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-10-28 | 143
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-10-28 | 169
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-10-28 | 143
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-10-28 | 143
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-10-28 | 142
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-10-28 | 169
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-10-28 | 184
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-10-28 | 169
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-10-28 | 168
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-10-28 | 156
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-10-28 | 131
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-10-28 | 129
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-10-28 | 125
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-10-28 | 192
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-10-28 | 197
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-10-28 | 197
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-10-28 | 119
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-10-28 | 118
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-28 | 117
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-28 | 117
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-10-28 | 118
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-28 | 117
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-28 | 106
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-28 | 106
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-10-28 | 105
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-10-28 | 103
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-28 | 117
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-10-28 | 101
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-28 | 117
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-09-14 | 123
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-09-14 | 115
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-09-14 | 164
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-09-14 | 166
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-09-14 | 112
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-09-14 | 141
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-09-14 | 112
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-09-14 | 111
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-14 | 86
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-09-14 | 138
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-09-14 | 137
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-14 | 86
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-09-14 | 111
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-09-14 | 111
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-09-14 | 137
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-09-14 | 111
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-09-14 | 111
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-09-14 | 110
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-09-14 | 137
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-09-14 | 152
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-09-14 | 137
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-09-14 | 136
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-09-14 | 124
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-09-14 | 99
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-09-14 | 97
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-09-14 | 93
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-09-14 | 160
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-09-14 | 165
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-09-14 | 165
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-09-14 | 87
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-14 | 86
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-14 | 85
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-14 | 85
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-14 | 86
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-14 | 85
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-09-14 | 74
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-09-14 | 74
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-09-14 | 73
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-09-14 | 71
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-14 | 85
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-09-14 | 69
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-14 | 85
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-06-09 | 18
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-06-09 | 5
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-06-09 | 5
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-06-09 | 4
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-09 | 2
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-06-09 | 0
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-IEC-10HAA-PR-PID-0001 | HRSG incl. SCR - Supplier P&IDs | IEC | IFR | ACCEPTED | NONE | 2027-01-11 | 2027-06-09 | 107
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | ALP-IEC-20MAA-PR-PID-0001 | Steam Turbine and Condenser - Supplier P&IDs | IEC | IFR | ACCEPTED | NONE | 2027-01-25 | 2027-06-09 | 97
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-06-09 | 54
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-06-09 | 46
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-06-09 | 95
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-06-09 | 97
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-06-09 | 43
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-06-09 | 72
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-06-09 | 43
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-06-09 | 69
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-09 | 68
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-09 | 68
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-06-09 | 41
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-09 | 68
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-06-09 | 83
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-09 | 68
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-06-09 | 67
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-06-09 | 55
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-06-09 | 30
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-06-09 | 28
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-06-09 | 24
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-06-09 | 91
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-06-09 | 96
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-06-09 | 96
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-06-09 | 18
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-06-09 | 5
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-06-09 | 5
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-06-09 | 4
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-09 | 2
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-06-09 | 0
ALP-EPC-00000-IC-LST-0001 | Instrument Index | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-12-23 | 195
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-12-23 | 187
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-12-23 | 236
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-12-23 | 238
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-12-23 | 184
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-12-23 | 213
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-12-23 | 184
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-12-23 | 183
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-12-23 | 158
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-12-23 | 210
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-12-23 | 209
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-12-23 | 158
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-12-23 | 183
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-12-23 | 183
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-12-23 | 209
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-12-23 | 183
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-12-23 | 183
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-12-23 | 182
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-12-23 | 209
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-12-23 | 224
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-12-23 | 209
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-12-23 | 208
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-12-23 | 196
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-12-23 | 171
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-12-23 | 169
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-12-23 | 165
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-12-23 | 232
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-12-23 | 237
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-12-23 | 237
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-12-23 | 159
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-12-23 | 158
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-12-23 | 157
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-12-23 | 157
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-12-23 | 158
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-12-23 | 157
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-12-23 | 146
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-12-23 | 146
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-12-23 | 145
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-12-23 | 143
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-12-23 | 157
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-12-23 | 141
ALP-EPC-00000-PI-LST-0001 | Valve List | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-12-23 | 157
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-06-09 | 54
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-06-09 | 46
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-06-09 | 95
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-06-09 | 97
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-06-09 | 43
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-06-09 | 72
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-06-09 | 43
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-06-09 | 69
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-09 | 68
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-09 | 68
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-09 | 42
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-06-09 | 41
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-09 | 68
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-06-09 | 83
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-09 | 68
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-06-09 | 67
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-06-09 | 55
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-06-09 | 30
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-06-09 | 28
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-06-09 | 24
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-06-09 | 91
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-06-09 | 96
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-06-09 | 96
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-06-09 | 18
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-09 | 17
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-06-09 | 5
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-06-09 | 5
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-06-09 | 4
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-09 | 2
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-06-09 | 0
ALP-EPC-00000-PR-LST-0002 | Line List | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-06-09 | 16
ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-18 | 141
ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-18 | 0
ALP-EPC-20MAN-IC-DSH-0001 | Turbine Bypass Stations and Piping - Instrument Datasheets | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-29 | 118
ALP-EPC-20MAN-IC-DSH-0001 | Turbine Bypass Stations and Piping - Instrument Datasheets | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-29 | 239
ALP-EPC-20MAN-IC-DSH-0002 | Turbine Bypass Stations and Piping - Control Valve Sizing and Datasheets | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-29 | 118
ALP-EPC-20MAN-IC-DSH-0002 | Turbine Bypass Stations and Piping - Control Valve Sizing and Datasheets | ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-10-29 | 239
ALP-EPC-20MAN-IC-DSH-0002 | Turbine Bypass Stations and Piping - Control Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-10-29 | 229
ALP-EPC-20MAN-PR-DSH-0001 | Turbine Bypass Stations and Piping - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-05-31 | 9
ALP-EPC-20MAN-PR-DSH-0001 | Turbine Bypass Stations and Piping - Safety / Relief Valve Sizing and Datasheets | ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | EPC | IFR | IFC | NONE | 2026-12-14 | 2027-05-31 | 120
ALP-EPC-00000-EL-CAL-0002 | Battery, UPS and DC System Sizing Calculation | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-27 | 235
ALP-EPC-00000-EL-CAL-0003 | Emergency Diesel Generator and Transformer Sizing Calculation | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-28 | 236
ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | ALP-IEC-10BAA-EL-SLD-0001 | Power Island Single Line Diagram | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2026-11-02 | -40
ALP-EPC-00UPA-GE-RPT-0001 | Marine Works - Technical Bid Evaluation | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-EPC-00000-GE-RPT-0001 | Piling Works - Technical Bid Evaluation | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-03 | 23
ALP-C02-00000-GE-ITP-0001 | Civil and Building Works - Subcontractor Inspection and Test Plans | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-C02-00000-GE-MOS-0001 | Civil and Building Works - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-C02-00000-GE-MOS-0002 | Civil and Building Works - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-C02-00000-GE-MOS-0003 | Civil and Building Works - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-C02-00000-GE-MOS-0004 | Civil and Building Works - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-C02-00000-GE-MOS-0005 | Civil and Building Works - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-C02-00000-GE-MOS-0006 | Civil and Building Works - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-S01-00000-GE-ITP-0001 | Structural Steel Supply and Fabrication - Subcontractor Inspection and Test Plans | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-03 | 62
ALP-S01-00000-GE-MOS-0001 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-03 | 62
ALP-S01-00000-GE-MOS-0002 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-03 | 62
ALP-S01-00000-GE-MOS-0003 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-03 | 62
ALP-S01-00000-GE-MOS-0004 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-03 | 62
ALP-S01-00000-GE-MOS-0005 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-03 | 62
ALP-S01-00000-GE-MOS-0006 | Structural Steel Supply and Fabrication - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-03 | 62
ALP-E08-00000-ME-DSH-0001 | Power and Control Cables - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-EL-MRQ-0001 | Power and Control Cables - Material Requisition | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-03-15 | 46
ALP-E08-00000-ME-ITP-0001 | Power and Control Cables - Supplier Inspection and Test Plan | ALP-EPC-00000-EL-MRQ-0001 | Power and Control Cables - Material Requisition | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-03-15 | 46
ALP-E08-00000-ME-MDB-0001 | Power and Control Cables - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-EL-MRQ-0001 | Power and Control Cables - Material Requisition | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-05 | 126
ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | ALP-EPC-00CJG-GE-SPC-0001 | BOP Safety Instrumented System - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-15 | 10
ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | ALP-EPC-00CJG-IC-DSH-0001 | Safety Instrumented Systems: Control System - Datasheet | EPC | IFR | IFC | NONE | 2027-02-15 | 2027-02-15 | 0
ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | ALP-EPC-00CKA-GE-SPC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-15 | 10
ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | ALP-EPC-00CKA-IC-DSH-0001 | Historian, Performance Monitoring and Operator Training Simulator: Control System - Datasheet | EPC | IFR | IFC | NONE | 2027-02-15 | 2027-02-15 | 0
ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | ALP-EPC-00CQA-IC-DSH-0001 | Continuous Emission Monitoring: Analyser - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-03-10 | 10
ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | ALP-EPC-00CYA-IC-DSH-0001 | Telecom, CCTV, Access Control, Security - Datasheet | EPC | IFR | IFC | NONE | 2027-03-10 | 2027-03-10 | 0
ALP-I10-00000-ME-DSH-0001 | Instrument Installation Materials - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-GE-MRQ-0003 | Instrument Installation Materials - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-06-02 | 38
ALP-I10-00000-ME-ITP-0001 | Instrument Installation Materials - Supplier Inspection and Test Plan | ALP-EPC-00000-GE-MRQ-0003 | Instrument Installation Materials - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-06-02 | 38
ALP-I10-00000-ME-MDB-0001 | Instrument Installation Materials - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-GE-MRQ-0003 | Instrument Installation Materials - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-07-28 | 78
ALP-E10-00BXA-IC-IOL-0001 | Cathodic Protection - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-05-18 | 53
ALP-E10-00BXA-ME-ITP-0001 | Cathodic Protection - Supplier Inspection and Test Plan | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-05-11 | 48
ALP-E10-00BXA-ME-LST-0001 | Cathodic Protection - Spare Parts and Special Tools Lists | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-06-01 | 63
ALP-E10-00BXA-ME-MDB-0001 | Cathodic Protection - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-08-03 | 108
ALP-E10-00BXA-ME-OMM-0001 | Cathodic Protection - Supplier Operation and Maintenance Manual | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-05-25 | 58
ALP-E10-00BXA-ME-PRC-0001 | Cathodic Protection - Supplier Installation and Erection Manual | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-05-18 | 53
ALP-E10-00BXA-ME-TRP-0001 | Cathodic Protection - Factory Acceptance Test Report | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-07-27 | 103
ALP-E10-00BXA-ME-TST-0001 | Cathodic Protection - Factory Acceptance Test Procedure | ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-04-20 | 33
ALP-P05-00000-ME-DSH-0001 | Pipe Supports, Spring Hangers and Snubbers - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-GE-MRQ-0006 | Pipe Supports, Spring Hangers and Snubbers - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-29 | 2027-05-27 | 43
ALP-P05-00000-ME-ITP-0001 | Pipe Supports, Spring Hangers and Snubbers - Supplier Inspection and Test Plan | ALP-EPC-00000-GE-MRQ-0006 | Pipe Supports, Spring Hangers and Snubbers - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-29 | 2027-05-27 | 43
ALP-P05-00000-ME-MDB-0001 | Pipe Supports, Spring Hangers and Snubbers - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-GE-MRQ-0006 | Pipe Supports, Spring Hangers and Snubbers - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-29 | 2027-08-19 | 103
ALP-P06-00000-ME-DSH-0001 | Piping Specialty Items - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-GE-MRQ-0007 | Piping Specialty Items - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-04-05 | 85
ALP-P06-00000-ME-ITP-0001 | Piping Specialty Items - Supplier Inspection and Test Plan | ALP-EPC-00000-GE-MRQ-0007 | Piping Specialty Items - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-04-05 | 85
ALP-P06-00000-ME-MDB-0001 | Piping Specialty Items - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-GE-MRQ-0007 | Piping Specialty Items - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-06-28 | 145
ALP-P07-00000-ME-DSH-0001 | Safety and Relief Valves - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-GE-MRQ-0008 | Safety and Relief Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-04-01 | 83
ALP-P07-00000-ME-ITP-0001 | Safety and Relief Valves - Supplier Inspection and Test Plan | ALP-EPC-00000-GE-MRQ-0008 | Safety and Relief Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-04-01 | 83
ALP-P07-00000-ME-MDB-0001 | Safety and Relief Valves - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-GE-MRQ-0008 | Safety and Relief Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-07-22 | 163
ALP-P01-00000-ME-DSH-0001 | Piping Bulk Materials - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-PI-MRQ-0001 | Piping Bulk Materials - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-01-28 | 38
ALP-P01-00000-ME-ITP-0001 | Piping Bulk Materials - Supplier Inspection and Test Plan | ALP-EPC-00000-PI-MRQ-0001 | Piping Bulk Materials - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-01-28 | 38
ALP-P01-00000-ME-MDB-0001 | Piping Bulk Materials - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-PI-MRQ-0001 | Piping Bulk Materials - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-05-20 | 118
ALP-P03-00000-ME-DSH-0001 | Valves - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-PI-MRQ-0003 | Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-03-18 | 60
ALP-P03-00000-ME-ITP-0001 | Valves - Supplier Inspection and Test Plan | ALP-EPC-00000-PI-MRQ-0003 | Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-03-18 | 60
ALP-P03-00000-ME-MDB-0001 | Valves - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-PI-MRQ-0003 | Valves - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-08-16 | 167
ALP-EPC-00000-GE-RPT-0009 | Painting and Insulation - Technical Bid Evaluation | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-06-09 | 33
ALP-EPC-00000-GE-RPT-0010 | Mechanical and Piping Erection - Technical Bid Evaluation | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-08-25 | 43
ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | ALP-EPC-00SMA-ME-DSH-0001 | Cranes and Hoists - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | ALP-EPC-00SMA-ME-SPC-0001 | EOT Cranes - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HNE-GE-RPT-0001 | Stack 65 m with Silencer - Technical Bid Evaluation | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-01-12 | 46
ALP-EPC-00SGY-GE-ITP-0001 | Fire Detection and Alarm System - Inspection and Test Plan | ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-03-04 | 1
ALP-EPC-00SGY-IC-DSH-0001 | Fire Detection and Alarm: Control System - Datasheet | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-03 | 87
ALP-EPC-00SGY-IC-DSH-0001 | Fire Detection and Alarm: Control System - Datasheet | ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-03-03 | 0
ALP-EPC-00000-CM-TRP-0006 | Emission Test and Noise Survey Reports | ALP-EPC-00000-CM-CMP-0006 | Emission and Noise Test Procedure | EPC | IFR | IFC | NONE | 2027-08-19 | 2029-03-26 | 417
ALP-EPC-00UZA-EL-ELY-0003 | Roads and Paving - Earthing and Lightning Protection Layouts | ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings | EPC | IFR | IFC | NONE | 2027-02-09 | 2027-02-09 | 0
ALP-EPC-00UZA-EL-ELY-0003 | Roads and Paving - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-02-09 | 31
ALP-EPC-00UZA-EL-ELY-0003 | Roads and Paving - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-02-09 | 30
ALP-EPC-00UZF-GE-SPC-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Specification | ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-05-19 | 117
ALP-EPC-00UZF-GE-SPC-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Specification | ALP-EPC-00000-ME-PLN-0001 | Marine Operations Plan | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-05-19 | 55
ALP-EPC-00UZF-GE-SPC-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Specification | ALP-EPC-00UZF-CV-RPT-0001 | Temporary Barge Landing Design Report and Removal Plan | EPC | IFR | IFC | NONE | 2027-05-19 | 2027-05-19 | 0
ALP-EPC-00UZF-GE-SPC-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Specification | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-05-19 | 92
ALP-EPC-00UAC-HS-GAD-0001 | GIS Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-22 | 11
ALP-EPC-00UAC-HS-GAD-0001 | GIS Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-22 | 0
ALP-EPC-00UAC-HS-GAD-0001 | GIS Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-01-22 | 20
ALP-EPC-00UAC-HV-GAD-0001 | GIS Building - Building Services | ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-07 | 0
ALP-EPC-00UAC-HV-GAD-0001 | GIS Building - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-07 | 48
ALP-EPC-00UAC-IC-ELY-0001 | GIS Building - Fire Detection and Alarm Layouts | ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-01-22 | 11
ALP-EPC-00UAC-IC-ELY-0001 | GIS Building - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-22 | 0
ALP-EPC-00UAC-SS-STL-0001 | GIS Building - Structural Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-08 | 15
ALP-EPC-00UAC-SS-STL-0001 | GIS Building - Structural Drawings | ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-07 | 2027-02-08 | 22
ALP-EPC-00UAC-SS-STL-0001 | GIS Building - Structural Drawings | ALP-EPC-00UAC-CV-CAL-0001 | GIS Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-02-08 | 2027-02-08 | 0
ALP-EPC-00UAC-CV-RBR-0001 | GIS Building - Reinforcement Drawings | ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-02-18 | 0
ALP-EPC-00UAC-EL-ELY-0003 | GIS Building - Earthing and Lightning Protection Layouts | ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-05-21 | 66
ALP-EPC-00UAC-EL-ELY-0003 | GIS Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-05-21 | 104
ALP-EPC-00UAC-EL-ELY-0003 | GIS Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-05-21 | 103
ALP-S01-00UAC-SS-STL-0001 | GIS Building - Steel Fabrication and Erection Drawings | ALP-EPC-00UAC-SS-STL-0002 | GIS Building - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-02-10 | -27
ALP-EPC-00UBA-HS-GAD-0001 | Electrical Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-21 | 2027-01-22 | 1
ALP-EPC-00UBA-HS-GAD-0001 | Electrical Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-22 | 0
ALP-EPC-00UBA-HS-GAD-0001 | Electrical Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-01-22 | 20
ALP-EPC-00UBA-HV-GAD-0002 | Electrical Building - Building Services | ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-21 | 2027-01-21 | 0
ALP-EPC-00UBA-HV-GAD-0002 | Electrical Building - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-21 | 58
ALP-EPC-00UBA-IC-ELY-0001 | Electrical Building - Fire Detection and Alarm Layouts | ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-21 | 2027-01-22 | 1
ALP-EPC-00UBA-IC-ELY-0001 | Electrical Building - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-22 | 0
ALP-EPC-00UBA-SS-STL-0001 | Electrical Building - Structural Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-02 | 31
ALP-EPC-00UBA-SS-STL-0001 | Electrical Building - Structural Drawings | ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-21 | 2027-03-02 | 28
ALP-EPC-00UBA-SS-STL-0001 | Electrical Building - Structural Drawings | ALP-EPC-00UBA-CV-CAL-0001 | Electrical Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-02 | 2027-03-02 | 0
ALP-EPC-00UBA-CV-RBR-0001 | Electrical Building - Reinforcement Drawings | ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-02-18 | 0
ALP-EPC-00UBA-EL-ELY-0003 | Electrical Building - Earthing and Lightning Protection Layouts | ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-02-18 | 0
ALP-EPC-00UBA-EL-ELY-0003 | Electrical Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-02-18 | 38
ALP-EPC-00UBA-EL-ELY-0003 | Electrical Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-02-18 | 37
ALP-EPC-00SAA-PI-ISO-0001 | HVAC - Isometric Drawings | ALP-EPC-00UBA-PI-PPL-0001 | Electrical Building and Emergency Power - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-07-08 | 2027-07-08 | 0
ALP-EPC-00SAA-PI-ISO-0001 | HVAC - Isometric Drawings | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-07-08 | 112
ALP-S01-00UBA-SS-STL-0001 | Electrical Building - Steel Fabrication and Erection Drawings | ALP-EPC-00UBA-SS-STL-0002 | Electrical Building - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-04-08 | 2027-02-10 | -41
ALP-EPC-00UCA-HS-GAD-0001 | Control Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00UCA-HS-GAD-0001 | Control Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-02 | 7
ALP-EPC-00UCA-HS-GAD-0001 | Control Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-02-02 | 27
ALP-EPC-00UCA-HV-GAD-0002 | Control Building - Building Services | ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00UCA-HV-GAD-0002 | Control Building - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-02 | 66
ALP-EPC-00UCA-IC-ELY-0002 | Control Building - Fire Detection and Alarm Layouts | ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00UCA-IC-ELY-0002 | Control Building - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-02 | 7
ALP-EPC-00UCA-SS-STL-0001 | Control Building - Structural Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-31 | 52
ALP-EPC-00UCA-SS-STL-0001 | Control Building - Structural Drawings | ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-03-31 | 41
ALP-EPC-00UCA-SS-STL-0001 | Control Building - Structural Drawings | ALP-EPC-00UCA-CV-CAL-0001 | Control Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-31 | 2027-03-31 | 0
ALP-EPC-00UCA-CV-RBR-0001 | Control Building - Reinforcement Drawings | ALP-EPC-00UCA-CV-FND-0001 | Control Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-17 | 0
ALP-EPC-00UCA-EL-ELY-0003 | Control Building - Earthing and Lightning Protection Layouts | ALP-EPC-00UCA-CV-FND-0001 | Control Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-17 | 0
ALP-EPC-00UCA-EL-ELY-0003 | Control Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-02-17 | 37
ALP-EPC-00UCA-EL-ELY-0003 | Control Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-02-17 | 36
ALP-S01-00UCA-SS-STL-0001 | Control Building - Steel Fabrication and Erection Drawings | ALP-EPC-00UCA-SS-STL-0002 | Control Building - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-05-07 | 2027-02-10 | -62
ALP-EPC-00USA-HS-GAD-0001 | Workshop and Warehouse - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00USA-HS-GAD-0001 | Workshop and Warehouse - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-25 | 1
ALP-EPC-00USA-HS-GAD-0001 | Workshop and Warehouse - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-01-25 | 21
ALP-EPC-00USA-HV-GAD-0001 | Workshop and Warehouse - Building Services | ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00USA-HV-GAD-0001 | Workshop and Warehouse - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00USA-IC-ELY-0001 | Workshop and Warehouse - Fire Detection and Alarm Layouts | ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00USA-IC-ELY-0001 | Workshop and Warehouse - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-25 | 1
ALP-EPC-00USA-SS-STL-0001 | Workshop and Warehouse - Structural Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-31 | 52
ALP-EPC-00USA-SS-STL-0001 | Workshop and Warehouse - Structural Drawings | ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-03-31 | 47
ALP-EPC-00USA-SS-STL-0001 | Workshop and Warehouse - Structural Drawings | ALP-EPC-00USA-CV-CAL-0001 | Workshop and Warehouse - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-31 | 2027-03-31 | 0
ALP-EPC-00USA-CV-RBR-0001 | Workshop and Warehouse - Reinforcement Drawings | ALP-EPC-00USA-CV-FND-0001 | Workshop and Warehouse - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-17 | 0
ALP-EPC-00USA-EL-ELY-0001 | Workshop and Warehouse - Earthing and Lightning Protection Layouts | ALP-EPC-00USA-CV-FND-0001 | Workshop and Warehouse - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-17 | 0
ALP-EPC-00USA-EL-ELY-0001 | Workshop and Warehouse - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-02-17 | 37
ALP-EPC-00USA-EL-ELY-0001 | Workshop and Warehouse - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-02-17 | 36
ALP-S01-00USA-SS-STL-0001 | Workshop and Warehouse - Steel Fabrication and Erection Drawings | ALP-EPC-00USA-SS-STL-0002 | Workshop and Warehouse - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-02-10 | -64
ALP-EPC-00UYA-HS-GAD-0001 | Administration Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00UYA-HS-GAD-0001 | Administration Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-02 | 7
ALP-EPC-00UYA-HS-GAD-0001 | Administration Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-02-02 | 27
ALP-EPC-00UYA-HV-GAD-0001 | Administration Building - Building Services | ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00UYA-HV-GAD-0001 | Administration Building - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-02 | 66
ALP-EPC-00UYA-IC-ELY-0001 | Administration Building - Fire Detection and Alarm Layouts | ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00UYA-IC-ELY-0001 | Administration Building - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-02 | 7
ALP-EPC-00UYA-SS-STL-0001 | Administration Building - Structural Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-04-02 | 54
ALP-EPC-00UYA-SS-STL-0001 | Administration Building - Structural Drawings | ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-04-02 | 43
ALP-EPC-00UYA-SS-STL-0001 | Administration Building - Structural Drawings | ALP-EPC-00UYA-CV-CAL-0001 | Administration Building - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-04-02 | 2027-04-02 | 0
ALP-EPC-00UYA-CV-RBR-0001 | Administration Building - Reinforcement Drawings | ALP-EPC-00UYA-CV-FND-0001 | Administration Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-17 | 0
ALP-EPC-00UYA-EL-ELY-0001 | Administration Building - Earthing and Lightning Protection Layouts | ALP-EPC-00UYA-CV-FND-0001 | Administration Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-17 | 0
ALP-EPC-00UYA-EL-ELY-0001 | Administration Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-02-17 | 37
ALP-EPC-00UYA-EL-ELY-0001 | Administration Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-02-17 | 36
ALP-S01-00UYA-SS-STL-0001 | Administration Building - Steel Fabrication and Erection Drawings | ALP-EPC-00UYA-SS-STL-0002 | Administration Building - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-02-10 | -64
ALP-EPC-00UEG-CV-RBR-0001 | LDO Tank Farm Structures - Reinforcement Drawings | ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-04-22 | 2027-04-22 | 0
ALP-EPC-00UEG-EL-ELY-0003 | LDO Tank Farm Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-04-22 | 2027-07-19 | 62
ALP-EPC-00UEG-EL-ELY-0003 | LDO Tank Farm Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-07-19 | 145
ALP-EPC-00UEG-EL-ELY-0003 | LDO Tank Farm Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-07-19 | 144
ALP-EPC-00EGC-PI-STR-0001 | LDO Forwarding and Treatment - Pipe Stress Analysis | ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-06-28 | 83
ALP-EPC-00EGC-PI-STR-0001 | LDO Forwarding and Treatment - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-06-28 | 121
ALP-S01-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Fabrication and Erection Drawings | ALP-EPC-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-03-30 | 2027-02-10 | -34
ALP-EPC-00UEK-HS-GAD-0001 | Gas Station Structures - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00UEK-CV-ARC-0001 | Gas Station Structures - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-05-24 | 2027-05-24 | 0
ALP-EPC-00UEK-HS-GAD-0001 | Gas Station Structures - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-05-24 | 86
ALP-EPC-00UEK-HS-GAD-0001 | Gas Station Structures - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-05-24 | 106
ALP-EPC-00UEK-HV-GAD-0001 | Gas Station Structures - Building Services | ALP-EPC-00UEK-CV-ARC-0001 | Gas Station Structures - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-05-24 | 2027-05-24 | 0
ALP-EPC-00UEK-HV-GAD-0001 | Gas Station Structures - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-24 | 145
ALP-EPC-00UEK-IC-ELY-0002 | Gas Station Structures - Fire Detection and Alarm Layouts | ALP-EPC-00UEK-CV-ARC-0001 | Gas Station Structures - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-05-24 | 2027-05-24 | 0
ALP-EPC-00UEK-IC-ELY-0002 | Gas Station Structures - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-05-24 | 86
ALP-EPC-00UEK-CV-RBR-0001 | Gas Station Structures - Reinforcement Drawings | ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-05-31 | 0
ALP-EPC-00UEK-EL-ELY-0003 | Gas Station Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-06-14 | 10
ALP-EPC-00UEK-EL-ELY-0003 | Gas Station Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-06-14 | 120
ALP-EPC-00UEK-EL-ELY-0003 | Gas Station Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-06-14 | 119
ALP-EPC-00EKA-PI-STR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Stress Analysis | ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-05-14 | 49
ALP-EPC-00EKA-PI-STR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-05-14 | 90
ALP-EPC-00EKC-PI-STR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-06-28 | 121
ALP-EPC-00EKC-PI-STR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Stress Analysis | ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-06-28 | 80
ALP-EPC-00EKC-PI-STR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-06-28 | 130
ALP-S01-00UEK-SS-STL-0001 | Gas Station Structures - Steel Fabrication and Erection Drawings | ALP-EPC-00UEK-SS-STL-0001 | Gas Station Structures - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-05-28 | 2027-02-10 | -77
ALP-EPC-00UGA-HS-GAD-0001 | Water Treatment Building and Basins - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00UGA-HS-GAD-0001 | Water Treatment Building and Basins - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-25 | 1
ALP-EPC-00UGA-HS-GAD-0001 | Water Treatment Building and Basins - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-01-25 | 21
ALP-EPC-00UGA-HV-GAD-0001 | Water Treatment Building and Basins - Building Services | ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-02-19 | 19
ALP-EPC-00UGA-HV-GAD-0001 | Water Treatment Building and Basins - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-19 | 79
ALP-EPC-00UGA-IC-ELY-0002 | Water Treatment Building and Basins - Fire Detection and Alarm Layouts | ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-01-25 | 0
ALP-EPC-00UGA-IC-ELY-0002 | Water Treatment Building and Basins - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-25 | 1
ALP-EPC-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Structural Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-03-03 | 32
ALP-EPC-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Structural Drawings | ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-03-03 | 27
ALP-EPC-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Structural Drawings | ALP-EPC-00UGA-CV-CAL-0001 | Water Treatment Building and Basins - Structural and Foundation Calculation | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-03-03 | 0
ALP-EPC-00UGA-CV-RBR-0001 | Water Treatment Building and Basins - Reinforcement Drawings | ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-02-24 | 0
ALP-EPC-00UGA-EL-ELY-0003 | Water Treatment Building and Basins - Earthing and Lightning Protection Layouts | ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-08-12 | 121
ALP-EPC-00UGA-EL-ELY-0003 | Water Treatment Building and Basins - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-08-12 | 163
ALP-EPC-00UGA-EL-ELY-0003 | Water Treatment Building and Basins - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-08-12 | 162
ALP-S01-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Steel Fabrication and Erection Drawings | ALP-EPC-00UGA-SS-STL-0002 | Water Treatment Building and Basins - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-02-10 | -42
ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings | ALP-EPC-00UZF-CV-FND-0002 | Temporary Barge Landing - Piling Layout and Pile Schedule | EPC | IFR | IFC | NONE | 2027-05-26 | 2027-05-26 | 0
ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings | ALP-EPC-00UPA-PI-LAY-0001 | Marine Works - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-05-26 | 106
ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-05-26 | 92
ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-26 | 132
ALP-S01-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Fabrication and Erection Drawings | ALP-EPC-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-02-10 | -95
ALP-EPC-00UPC-HS-GAD-0001 | CW Pump House - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00UPC-CV-ARC-0001 | CW Pump House - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-05 | 2027-01-22 | 13
ALP-EPC-00UPC-HS-GAD-0001 | CW Pump House - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-22 | 0
ALP-EPC-00UPC-HS-GAD-0001 | CW Pump House - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-01-22 | 20
ALP-EPC-00UPC-HV-GAD-0001 | CW Pump House - Building Services | ALP-EPC-00UPC-CV-ARC-0001 | CW Pump House - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-05 | 2027-01-05 | 0
ALP-EPC-00UPC-HV-GAD-0001 | CW Pump House - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-05 | 46
ALP-EPC-00UPC-IC-ELY-0002 | CW Pump House - Fire Detection and Alarm Layouts | ALP-EPC-00UPC-CV-ARC-0001 | CW Pump House - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-05 | 2027-01-22 | 13
ALP-EPC-00UPC-IC-ELY-0002 | CW Pump House - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-22 | 0
ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-19 | 1
ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-19 | 41
ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-03 | 2027-01-19 | 33
ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | ALP-EPC-00UPC-CV-FND-0002 | CW Pump House - Piling Layout and Pile Schedule | EPC | IFR | IFC | NONE | 2027-01-19 | 2027-01-19 | 0
ALP-EPC-00PAB-PI-STR-0001 | CW Piping - Pipe Stress Analysis | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-05-14 | 0
ALP-EPC-00PAB-PI-STR-0001 | CW Piping - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-05-14 | 90
ALP-S01-00UPC-SS-STL-0001 | CW Pump House - Steel Fabrication and Erection Drawings | ALP-EPC-00UPC-SS-STL-0001 | CW Pump House - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-03-16 | 2027-02-10 | -24
ALP-EPC-00UQA-HS-GAD-0001 | Utility Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00UQA-CV-ARC-0001 | Utility Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-01-27 | 0
ALP-EPC-00UQA-HS-GAD-0001 | Utility Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-27 | 3
ALP-EPC-00UQA-HS-GAD-0001 | Utility Building - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-01-27 | 23
ALP-EPC-00UQA-HV-GAD-0001 | Utility Building - Building Services | ALP-EPC-00UQA-CV-ARC-0001 | Utility Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-03-29 | 43
ALP-EPC-00UQA-HV-GAD-0001 | Utility Building - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-29 | 105
ALP-EPC-00UQA-IC-ELY-0002 | Utility Building - Fire Detection and Alarm Layouts | ALP-EPC-00UQA-CV-ARC-0001 | Utility Building - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-01-27 | 0
ALP-EPC-00UQA-IC-ELY-0002 | Utility Building - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-27 | 3
ALP-EPC-00UQA-CV-RBR-0001 | Utility Building - Reinforcement Drawings | ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-04-05 | 13
ALP-EPC-00UQA-EL-ELY-0003 | Utility Building - Earthing and Lightning Protection Layouts | ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-07-16 | 87
ALP-EPC-00UQA-EL-ELY-0003 | Utility Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-07-16 | 144
ALP-EPC-00UQA-EL-ELY-0003 | Utility Building - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-07-16 | 143
ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-21 | 138
ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-07-21 | 67
ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-07-21 | 147
ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-07-21 | 17
ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-07-21 | 67
ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-07-21 | 17
ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-21 | 138
ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-07-21 | 67
ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-07-21 | 17
ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-21 | 138
ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-07-21 | 67
ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-07-21 | 17
ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-21 | 138
ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-21 | 138
ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-07-21 | 67
ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-07-21 | 147
ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-07-21 | 17
ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-07-21 | 67
ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-07-21 | 17
ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-21 | 138
ALP-S01-00UQA-SS-STL-0001 | Utility Building - Steel Fabrication and Erection Drawings | ALP-EPC-00UQA-SS-STL-0001 | Utility Building - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-02-10 | -64
ALP-EPC-00000-EL-SLD-0002 | Construction Power Supply Single Line Diagram and RMU Design | ALP-EPC-00000-EL-LST-0002 | Construction Power Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-EL-SLD-0002 | Construction Power Supply Single Line Diagram and RMU Design | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UZD-CV-RBR-0001 | Pipe Racks and Pipe Sleepers - Reinforcement Drawings | ALP-EPC-00UZD-CV-FND-0001 | Pipe Racks and Pipe Sleepers - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-27 | 12
ALP-EPC-00UZD-EL-ELY-0001 | Pipe Racks and Pipe Sleepers - Earthing and Lightning Protection Layouts | ALP-EPC-00UZD-CV-FND-0001 | Pipe Racks and Pipe Sleepers - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-09 | 0
ALP-EPC-00UZD-EL-ELY-0001 | Pipe Racks and Pipe Sleepers - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-04-09 | 74
ALP-EPC-00UZD-EL-ELY-0001 | Pipe Racks and Pipe Sleepers - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-04-09 | 73
ALP-S01-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Fabrication and Erection Drawings, Part 1 of 2 | ALP-EPC-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-04-07 | 2027-02-10 | -40
ALP-S01-00UZD-SS-STL-0002 | Pipe Racks and Pipe Sleepers - Steel Fabrication and Erection Drawings, Part 2 of 2 | ALP-EPC-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-04-07 | 2027-02-10 | -40
ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-02 | 11
ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-02 | 51
ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-02-02 | 28
ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | ALP-IEC-10BAT-EL-GAD-0001 | Generator Step-Up Transformers - Supplier GA Drawings | IEC | IFR | ACCEPTED | ACCEPTED | 2026-09-28 | 2027-02-02 | 91
ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | ALP-EPC-00UBF-CV-FND-0002 | Transformer Bays - Piling Layout and Pile Schedule | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-02 | 7
ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-02-02 | 36
ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-02-02 | 36
ALP-S01-00UBF-SS-STL-0001 | Transformer Bays - Steel Fabrication and Erection Drawings | ALP-EPC-00UBF-SS-STL-0001 | Transformer Bays - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-06-01 | 2027-02-10 | -79
ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-26 | 6
ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-26 | 46
ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-01-26 | 23
ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-01-26 | 31
ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | ALP-EPC-10UHA-CV-FND-0002 | HRSG Foundations and Structures - Piling Layout and Pile Schedule | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-01-26 | 0
ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-01-26 | 31
ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-09 | 16
ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-09 | 56
ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-02-09 | 33
ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | ALP-EPC-10UHN-CV-FND-0002 | Stack Foundation - Piling Layout and Pile Schedule | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-09 | 12
ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-02-09 | 41
ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-02-09 | 41
ALP-EPC-10UMA-HS-GAD-0001 | Gas Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-10UMA-CV-ARC-0001 | Gas Turbine Hall - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-10UMA-HS-GAD-0001 | Gas Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-01 | 6
ALP-EPC-10UMA-HS-GAD-0001 | Gas Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-02-01 | 26
ALP-EPC-10UMA-HV-GAD-0002 | Gas Turbine Hall - Building Services | ALP-EPC-10UMA-CV-ARC-0001 | Gas Turbine Hall - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-03-11 | 28
ALP-EPC-10UMA-HV-GAD-0002 | Gas Turbine Hall - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-EPC-10UMA-IC-ELY-0002 | Gas Turbine Hall - Fire Detection and Alarm Layouts | ALP-EPC-10UMA-CV-ARC-0001 | Gas Turbine Hall - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-10UMA-IC-ELY-0002 | Gas Turbine Hall - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-02-01 | 6
ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-01-28 | 8
ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-01-28 | 48
ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-01-28 | 25
ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-01-28 | 33
ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | ALP-EPC-10UMA-CV-FND-0001 | Gas Turbine Hall - Piling Layout and Pile Schedule | EPC | IFR | IFC | NONE | 2027-01-28 | 2027-01-28 | 0
ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-01-28 | 33
ALP-EPC-10HAN-PI-STR-0001 | HRSG Blowdown and Drains - Pipe Stress Analysis | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-07-08 | 41
ALP-EPC-10HAN-PI-STR-0001 | HRSG Blowdown and Drains - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-08 | 129
ALP-EPC-10LAE-PI-STR-0001 | HP Attemperation Spray Water - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-20 | 137
ALP-EPC-10LAE-PI-STR-0001 | HP Attemperation Spray Water - Pipe Stress Analysis | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-07-20 | 49
ALP-EPC-10LAE-PI-STR-0001 | HP Attemperation Spray Water - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-07-20 | 146
ALP-EPC-10LAF-PI-STR-0001 | Reheat Attemperation Spray Water - Pipe Stress Analysis | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-07-20 | 49
ALP-EPC-10LAF-PI-STR-0001 | Reheat Attemperation Spray Water - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-20 | 137
ALP-EPC-10LBA-PI-STR-0001 | Main Steam Piping - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-06-28 | 121
ALP-EPC-10LBA-PI-STR-0001 | Main Steam Piping - Pipe Stress Analysis | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-06-28 | 33
ALP-EPC-10LBA-PI-STR-0001 | Main Steam Piping - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-06-28 | 130
ALP-EPC-10LBB-PI-STR-0001 | Hot Reheat Piping - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-06-29 | 122
ALP-EPC-10LBB-PI-STR-0001 | Hot Reheat Piping - Pipe Stress Analysis | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-06-29 | 34
ALP-EPC-10LBB-PI-STR-0001 | Hot Reheat Piping - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-06-29 | 131
ALP-EPC-10LBC-PI-STR-0001 | Cold Reheat Piping - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-08 | 129
ALP-EPC-10LBC-PI-STR-0001 | Cold Reheat Piping - Pipe Stress Analysis | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-07-08 | 41
ALP-EPC-10LBC-PI-STR-0001 | Cold Reheat Piping - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-07-08 | 138
ALP-EPC-10LBD-PI-STR-0001 | LP Steam Piping - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-07-08 | 129
ALP-EPC-10LBD-PI-STR-0001 | LP Steam Piping - Pipe Stress Analysis | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-07-08 | 41
ALP-EPC-10LBD-PI-STR-0001 | LP Steam Piping - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-07-08 | 138
ALP-S01-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Fabrication and Erection Drawings | ALP-EPC-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-02-10 | -78
ALP-EPC-20UMB-HS-GAD-0001 | Steam Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-20UMB-CV-ARC-0001 | Steam Turbine Hall - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-19 | 2027-01-22 | 3
ALP-EPC-20UMB-HS-GAD-0001 | Steam Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-22 | 0
ALP-EPC-20UMB-HS-GAD-0001 | Steam Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | EPC | IFR | IFC | NONE | 2026-12-25 | 2027-01-22 | 20
ALP-EPC-20UMB-HV-GAD-0001 | Steam Turbine Hall - Building Services | ALP-EPC-20UMB-CV-ARC-0001 | Steam Turbine Hall - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-19 | 2027-01-19 | 0
ALP-EPC-20UMB-HV-GAD-0001 | Steam Turbine Hall - Building Services | ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-19 | 56
ALP-EPC-20UMB-IC-ELY-0002 | Steam Turbine Hall - Fire Detection and Alarm Layouts | ALP-EPC-20UMB-CV-ARC-0001 | Steam Turbine Hall - Architectural Drawings | EPC | IFR | IFC | NONE | 2027-01-19 | 2027-01-22 | 3
ALP-EPC-20UMB-IC-ELY-0002 | Steam Turbine Hall - Fire Detection and Alarm Layouts | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-01-22 | 0
ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | EPC | IFR | IFC | NONE | 2027-01-18 | 2027-02-01 | 10
ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-01 | 50
ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-11 | 2027-02-01 | 36
ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | ALP-IEC-20MAA-CV-CAL-0001 | Steam Turbine and Condenser - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-02-01 | 25
ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | ALP-EPC-20UMB-CV-FND-0001 | Steam Turbine Hall - Piling Layout and Pile Schedule | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-05-14 | 52
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-05-14 | 49
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-05-14 | 52
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-05-14 | 0
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-05-14 | 19
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-02-15 | 2027-05-14 | 64
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-05-14 | 2
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-05-14 | 3
ALP-EPC-20LCA-PI-STR-0001 | Main Condensate Piping - Pipe Stress Analysis | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-12-07 | 150
ALP-EPC-20LCA-PI-STR-0001 | Main Condensate Piping - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-12-07 | 237
ALP-EPC-20LCB-PI-STR-0001 | Condensate Extraction Pumps - Pipe Stress Analysis | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-12-08 | 151
ALP-EPC-20LCB-PI-STR-0001 | Condensate Extraction Pumps - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-12-08 | 238
ALP-EPC-20MAN-PI-STR-0001 | Turbine Bypass Stations and Piping - Pipe Stress Analysis | ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | EPC | IFR | IFC | NONE | 2027-01-08 | 2027-11-26 | 230
ALP-EPC-20MAN-PI-STR-0001 | Turbine Bypass Stations and Piping - Pipe Stress Analysis | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-11-26 | 143
ALP-EPC-20MAN-PI-STR-0001 | Turbine Bypass Stations and Piping - Pipe Stress Analysis | ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-11-26 | 239
ALP-S01-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Fabrication and Erection Drawings | ALP-EPC-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Structure Drawings | EPC | IFR | IFC | NONE | 2027-06-01 | 2027-02-10 | -79
ALP-EPC-00EGA-CM-CMP-0001 | LDO Unloading - System Commissioning Procedure | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-04-15 | 15
ALP-EPC-00EGA-CM-CMP-0001 | LDO Unloading - System Commissioning Procedure | ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-15 | 2027-04-15 | 0
ALP-EPC-00EGA-CM-CMP-0001 | LDO Unloading - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-15 | 98
ALP-EPC-00EGA-IC-HMI-0001 | LDO Unloading - Operator Displays | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-04-15 | 15
ALP-EPC-00EGA-IC-HMI-0001 | LDO Unloading - Operator Displays | ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-15 | 2027-04-15 | 0
ALP-EPC-00EGA-IC-LOG-0001 | LDO Unloading - Logic Diagrams | ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-15 | 2027-04-15 | 0
ALP-EPC-00EGA-IC-LOG-0001 | LDO Unloading - Logic Diagrams | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-04-15 | 15
ALP-EPC-00EGA-IC-LOG-0001 | LDO Unloading - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-15 | 103
ALP-EPC-00EGB-CM-CMP-0001 | LDO Storage - System Commissioning Procedure | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-04-27 | 15
ALP-EPC-00EGB-CM-CMP-0001 | LDO Storage - System Commissioning Procedure | ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-27 | 2027-04-27 | 0
ALP-EPC-00EGB-CM-CMP-0001 | LDO Storage - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-27 | 106
ALP-EPC-00EGB-IC-HMI-0001 | LDO Storage - Operator Displays | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-04-27 | 15
ALP-EPC-00EGB-IC-HMI-0001 | LDO Storage - Operator Displays | ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-27 | 2027-04-27 | 0
ALP-EPC-00EGB-IC-LOG-0001 | LDO Storage - Logic Diagrams | ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-27 | 2027-04-27 | 0
ALP-EPC-00EGB-IC-LOG-0001 | LDO Storage - Logic Diagrams | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-04-27 | 15
ALP-EPC-00EGB-IC-LOG-0001 | LDO Storage - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-27 | 111
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | ALP-EPC-00EGA-ME-DSH-0001 | LDO Unloading: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | ALP-EPC-00EGC-ME-DSH-0001 | LDO Forwarding and Treatment: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | ALP-EPC-00EGA-ME-DSH-0002 | LDO Unloading: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | ALP-EPC-00EGA-ME-DSH-0003 | LDO Unloading: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | ALP-EPC-00EGA-ME-DSH-0004 | LDO Unloading: Tank - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | ALP-EPC-00EGC-ME-DSH-0002 | LDO Forwarding and Treatment: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | ALP-EPC-00EGC-ME-DSH-0003 | LDO Forwarding and Treatment: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00000-CM-TRP-0005 | Tests on LDO Report | ALP-EPC-00000-CM-CMP-0005 | Tests on LDO Procedure | EPC | IFR | IFC | NONE | 2027-08-17 | 2029-02-26 | 399
ALP-EPC-00EGC-CM-CMP-0001 | LDO Forwarding and Treatment - System Commissioning Procedure | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-02-18 | 16
ALP-EPC-00EGC-CM-CMP-0001 | LDO Forwarding and Treatment - System Commissioning Procedure | ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-02-18 | 0
ALP-EPC-00EGC-CM-CMP-0001 | LDO Forwarding and Treatment - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-18 | 58
ALP-EPC-00EGC-IC-HMI-0001 | LDO Forwarding and Treatment - Operator Displays | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-02-18 | 16
ALP-EPC-00EGC-IC-HMI-0001 | LDO Forwarding and Treatment - Operator Displays | ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-02-18 | 0
ALP-EPC-00EGC-IC-LOG-0001 | LDO Forwarding and Treatment - Logic Diagrams | ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-02-18 | 0
ALP-EPC-00EGC-IC-LOG-0001 | LDO Forwarding and Treatment - Logic Diagrams | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-02-18 | 16
ALP-EPC-00EGC-IC-LOG-0001 | LDO Forwarding and Treatment - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-18 | 63
ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | ALP-EPC-00EKA-ME-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | ALP-EPC-00EKA-ME-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | ALP-EPC-00EKA-ME-DSH-0003 | Gas Receiving, Filtration and Fiscal Metering Station: Heat Exchangers - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | ALP-EPC-00EKA-ME-DSH-0004 | Gas Receiving, Filtration and Fiscal Metering Station: Tank - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00EKA-CM-CMP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Commissioning Procedure | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-02-16 | 16
ALP-EPC-00EKA-CM-CMP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Commissioning Procedure | ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-02-16 | 0
ALP-EPC-00EKA-CM-CMP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-16 | 56
ALP-EPC-00EKA-IC-HMI-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Operator Displays | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-02-16 | 16
ALP-EPC-00EKA-IC-HMI-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Operator Displays | ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-02-16 | 0
ALP-EPC-00EKA-IC-LOG-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Logic Diagrams | ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-02-16 | 0
ALP-EPC-00EKA-IC-LOG-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Logic Diagrams | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-02-16 | 16
ALP-EPC-00EKA-IC-LOG-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-16 | 61
ALP-EPC-00EKC-CM-CMP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Commissioning Procedure | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-30 | 15
ALP-EPC-00EKC-CM-CMP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Commissioning Procedure | ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-04-30 | 0
ALP-EPC-00EKC-CM-CMP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-30 | 109
ALP-EPC-00EKC-IC-HMI-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Operator Displays | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-30 | 15
ALP-EPC-00EKC-IC-HMI-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Operator Displays | ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-04-30 | 0
ALP-EPC-00EKC-IC-LOG-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Logic Diagrams | ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-04-30 | 0
ALP-EPC-00EKC-IC-LOG-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Logic Diagrams | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-30 | 15
ALP-EPC-00EKC-IC-LOG-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-30 | 114
ALP-EPC-00GBA-CM-CMP-0001 | Seawater Reverse Osmosis - System Commissioning Procedure | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-03-23 | 16
ALP-EPC-00GBA-CM-CMP-0001 | Seawater Reverse Osmosis - System Commissioning Procedure | ALP-EPC-00GBA-IC-CNR-0001 | Seawater Reverse Osmosis - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-23 | 2027-03-23 | 0
ALP-EPC-00GBA-CM-CMP-0001 | Seawater Reverse Osmosis - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-23 | 81
ALP-EPC-00GBA-IC-HMI-0001 | Seawater Reverse Osmosis - Operator Displays | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-03-23 | 16
ALP-EPC-00GBA-IC-HMI-0001 | Seawater Reverse Osmosis - Operator Displays | ALP-EPC-00GBA-IC-CNR-0001 | Seawater Reverse Osmosis - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-23 | 2027-03-23 | 0
ALP-EPC-00GCA-CM-CMP-0001 | Demineralisation - System Commissioning Procedure | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-30 | 15
ALP-EPC-00GCA-CM-CMP-0001 | Demineralisation - System Commissioning Procedure | ALP-EPC-00GCA-IC-CNR-0001 | Demineralisation - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-04-30 | 0
ALP-EPC-00GCA-CM-CMP-0001 | Demineralisation - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-30 | 109
ALP-EPC-00GCA-IC-HMI-0001 | Demineralisation - Operator Displays | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-04-30 | 15
ALP-EPC-00GCA-IC-HMI-0001 | Demineralisation - Operator Displays | ALP-EPC-00GCA-IC-CNR-0001 | Demineralisation - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-04-30 | 0
ALP-EPC-00GHA-CM-CMP-0001 | Demineralised Water Storage and Distribution - System Commissioning Procedure | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00GHA-CM-CMP-0001 | Demineralised Water Storage and Distribution - System Commissioning Procedure | ALP-EPC-00GHA-IC-CNR-0001 | Demineralised Water Storage and Distribution - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00GHA-CM-CMP-0001 | Demineralised Water Storage and Distribution - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-03 | 110
ALP-EPC-00GHA-IC-HMI-0001 | Demineralised Water Storage and Distribution - Operator Displays | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00GHA-IC-HMI-0001 | Demineralised Water Storage and Distribution - Operator Displays | ALP-EPC-00GHA-IC-CNR-0001 | Demineralised Water Storage and Distribution - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00GHA-IC-LOG-0001 | Demineralised Water Storage and Distribution - Logic Diagrams | ALP-EPC-00GHA-IC-CNR-0001 | Demineralised Water Storage and Distribution - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00GHA-IC-LOG-0001 | Demineralised Water Storage and Distribution - Logic Diagrams | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00GHA-IC-LOG-0001 | Demineralised Water Storage and Distribution - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-03 | 115
ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | ALP-EPC-00GHA-ME-DSH-0001 | Demineralised Water Storage and Distribution: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | ALP-EPC-00GHA-ME-DSH-0002 | Demineralised Water Storage and Distribution: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | ALP-EPC-00GKA-ME-DSH-0001 | Potable Water: Tank - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | ALP-EPC-00GKA-ME-DSH-0002 | Potable Water: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-03-02 | 2026-11-02 | -86
ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | ALP-EPC-00GKA-ME-DSH-0003 | Potable Water: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-03-03 | 2026-11-02 | -87
ALP-EPC-00GKA-CM-CMP-0001 | Potable Water - System Commissioning Procedure | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-07 | 15
ALP-EPC-00GKA-CM-CMP-0001 | Potable Water - System Commissioning Procedure | ALP-EPC-00GKA-IC-CNR-0001 | Potable Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-07 | 0
ALP-EPC-00GKA-CM-CMP-0001 | Potable Water - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-07 | 135
ALP-EPC-00GKA-IC-HMI-0001 | Potable Water - Operator Displays | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-07 | 15
ALP-EPC-00GKA-IC-HMI-0001 | Potable Water - Operator Displays | ALP-EPC-00GKA-IC-CNR-0001 | Potable Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-07 | 0
ALP-EPC-00GKA-IC-LOG-0001 | Potable Water - Logic Diagrams | ALP-EPC-00GKA-IC-CNR-0001 | Potable Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-07 | 0
ALP-EPC-00GKA-IC-LOG-0001 | Potable Water - Logic Diagrams | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-07 | 15
ALP-EPC-00GKA-IC-LOG-0001 | Potable Water - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-06-07 | 140
ALP-EPC-00GMA-CM-CMP-0001 | Process Drains and Waste Water Collection - System Commissioning Procedure | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-03-25 | 15
ALP-EPC-00GMA-CM-CMP-0001 | Process Drains and Waste Water Collection - System Commissioning Procedure | ALP-EPC-00GMA-IC-CNR-0001 | Process Drains and Waste Water Collection - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-03-25 | 0
ALP-EPC-00GMA-CM-CMP-0001 | Process Drains and Waste Water Collection - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-25 | 83
ALP-EPC-00GMA-IC-HMI-0001 | Process Drains and Waste Water Collection - Operator Displays | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-03-25 | 15
ALP-EPC-00GMA-IC-HMI-0001 | Process Drains and Waste Water Collection - Operator Displays | ALP-EPC-00GMA-IC-CNR-0001 | Process Drains and Waste Water Collection - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-03-25 | 0
ALP-EPC-00GMA-IC-LOG-0001 | Process Drains and Waste Water Collection - Logic Diagrams | ALP-EPC-00GMA-IC-CNR-0001 | Process Drains and Waste Water Collection - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-03-25 | 0
ALP-EPC-00GMA-IC-LOG-0001 | Process Drains and Waste Water Collection - Logic Diagrams | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-03-25 | 15
ALP-EPC-00GMA-IC-LOG-0001 | Process Drains and Waste Water Collection - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-EPC-00GNA-CM-CMP-0001 | Waste Water Treatment - System Commissioning Procedure | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00GNA-CM-CMP-0001 | Waste Water Treatment - System Commissioning Procedure | ALP-EPC-00GNA-IC-CNR-0001 | Waste Water Treatment - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00GNA-CM-CMP-0001 | Waste Water Treatment - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-26 | 84
ALP-EPC-00GNA-IC-HMI-0001 | Waste Water Treatment - Operator Displays | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00GNA-IC-HMI-0001 | Waste Water Treatment - Operator Displays | ALP-EPC-00GNA-IC-CNR-0001 | Waste Water Treatment - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GNA-ME-DSH-0001 | Waste Water Treatment: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GUA-ME-DSH-0001 | Sanitary Waste Water Treatment: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GNA-ME-DSH-0002 | Waste Water Treatment: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-02-10 | 2026-11-02 | -72
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GNA-ME-DSH-0003 | Waste Water Treatment: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GUA-ME-DSH-0002 | Sanitary Waste Water Treatment: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-02-10 | 2026-11-02 | -72
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GMA-ME-DSH-0004 | Process Drains and Waste Water Collection: Filter - Datasheet | EPC | IFR | IFC | NONE | 2027-02-04 | 2026-11-02 | -68
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GMA-ME-DSH-0005 | Process Drains and Waste Water Collection: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-02-10 | 2026-11-02 | -72
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | ALP-EPC-00GMA-ME-DSH-0006 | Process Drains and Waste Water Collection: Tank - Datasheet | EPC | IFR | IFC | NONE | 2027-02-08 | 2026-11-02 | -70
ALP-EPC-00GUA-CM-CMP-0001 | Sanitary Waste Water Treatment - System Commissioning Procedure | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-07 | 15
ALP-EPC-00GUA-CM-CMP-0001 | Sanitary Waste Water Treatment - System Commissioning Procedure | ALP-EPC-00GUA-IC-CNR-0001 | Sanitary Waste Water Treatment - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-07 | 0
ALP-EPC-00GUA-CM-CMP-0001 | Sanitary Waste Water Treatment - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-07 | 135
ALP-EPC-00GUA-IC-HMI-0001 | Sanitary Waste Water Treatment - Operator Displays | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-07 | 15
ALP-EPC-00GUA-IC-HMI-0001 | Sanitary Waste Water Treatment - Operator Displays | ALP-EPC-00GUA-IC-CNR-0001 | Sanitary Waste Water Treatment - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-07 | 0
ALP-EPC-00LBG-CM-CMP-0001 | Auxiliary Steam - System Commissioning Procedure | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-07-19 | 70
ALP-EPC-00LBG-CM-CMP-0001 | Auxiliary Steam - System Commissioning Procedure | ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-07-19 | 55
ALP-EPC-00LBG-CM-CMP-0001 | Auxiliary Steam - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-07-19 | 165
ALP-EPC-00LBG-IC-HMI-0001 | Auxiliary Steam - Operator Displays | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00LBG-IC-HMI-0001 | Auxiliary Steam - Operator Displays | ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00LBG-IC-LOG-0001 | Auxiliary Steam - Logic Diagrams | ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00LBG-IC-LOG-0001 | Auxiliary Steam - Logic Diagrams | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00LBG-IC-LOG-0001 | Auxiliary Steam - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-03 | 115
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00GBA-ME-DSH-0001 | Seawater Reverse Osmosis: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00GCA-ME-DSH-0001 | Demineralisation: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00LDA-ME-DSH-0001 | Condensate Polishing: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00GBA-ME-DSH-0002 | Seawater Reverse Osmosis: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00GBA-ME-DSH-0003 | Seawater Reverse Osmosis: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00GBA-ME-DSH-0004 | Seawater Reverse Osmosis: Tank - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00GCA-ME-DSH-0002 | Demineralisation: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-01-27 | 2026-11-02 | -62
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00GCA-ME-DSH-0003 | Demineralisation: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | ALP-EPC-00LDA-ME-DSH-0002 | Condensate Polishing: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00LDA-CM-CMP-0001 | Condensate Polishing - System Commissioning Procedure | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00LDA-CM-CMP-0001 | Condensate Polishing - System Commissioning Procedure | ALP-EPC-00LDA-IC-CNR-0001 | Condensate Polishing - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00LDA-CM-CMP-0001 | Condensate Polishing - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-03 | 110
ALP-EPC-00LDA-IC-HMI-0001 | Condensate Polishing - Operator Displays | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00LDA-IC-HMI-0001 | Condensate Polishing - Operator Displays | ALP-EPC-00LDA-IC-CNR-0001 | Condensate Polishing - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | ALP-EPC-00PAA-ME-DSH-0001 | CW Intake, Screens and Outfall: Filters - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | ALP-EPC-00PAA-ME-DSH-0002 | CW Intake, Screens and Outfall: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-02-15 | 2026-11-02 | -75
ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | ALP-EPC-00PAA-ME-DSH-0003 | CW Intake, Screens and Outfall: Valves - Datasheet | EPC | IFR | IFC | NONE | 2027-02-15 | 2026-11-02 | -75
ALP-EPC-00PAA-CM-CMP-0001 | CW Intake, Screens and Outfall - System Commissioning Procedure | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00PAA-CM-CMP-0001 | CW Intake, Screens and Outfall - System Commissioning Procedure | ALP-EPC-00PAA-IC-CNR-0001 | CW Intake, Screens and Outfall - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00PAA-CM-CMP-0001 | CW Intake, Screens and Outfall - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-26 | 84
ALP-EPC-00PAA-IC-HMI-0001 | CW Intake, Screens and Outfall - Operator Displays | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00PAA-IC-HMI-0001 | CW Intake, Screens and Outfall - Operator Displays | ALP-EPC-00PAA-IC-CNR-0001 | CW Intake, Screens and Outfall - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00PAA-IC-LOG-0001 | CW Intake, Screens and Outfall - Logic Diagrams | ALP-EPC-00PAA-IC-CNR-0001 | CW Intake, Screens and Outfall - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00PAA-IC-LOG-0001 | CW Intake, Screens and Outfall - Logic Diagrams | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00PAA-IC-LOG-0001 | CW Intake, Screens and Outfall - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-26 | 89
ALP-EPC-00UPA-CV-MOS-0001 | Marine Works Construction Method Statement | ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings | EPC | IFR | IFC | NONE | 2027-07-02 | 2027-07-02 | 0
ALP-EPC-00UPA-CV-RBR-0001 | CW Intake and Outfall Marine Structures - Reinforcement Drawings | ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings | EPC | IFR | IFC | NONE | 2027-07-02 | 2027-07-02 | 0
ALP-EPC-00UPA-EL-ELY-0001 | CW Intake and Outfall Marine Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings | EPC | IFR | IFC | NONE | 2027-07-02 | 2027-07-02 | 0
ALP-EPC-00UPA-EL-ELY-0001 | CW Intake and Outfall Marine Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-07-02 | 134
ALP-EPC-00UPA-EL-ELY-0001 | CW Intake and Outfall Marine Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-07-02 | 133
ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition | ALP-EPC-00000-PI-SPC-0007 | GRP CW Pipes and Fittings - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2026-11-02 | -20
ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition | ALP-EPC-00PAB-ME-DSH-0001 | CW Piping: Valves - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00PAB-CM-CMP-0001 | CW Piping - System Commissioning Procedure | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00PAB-CM-CMP-0001 | CW Piping - System Commissioning Procedure | ALP-EPC-00PAB-IC-CNR-0001 | CW Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00PAB-CM-CMP-0001 | CW Piping - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-03 | 110
ALP-EPC-00PAB-IC-HMI-0001 | CW Piping - Operator Displays | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00PAB-IC-HMI-0001 | CW Piping - Operator Displays | ALP-EPC-00PAB-IC-CNR-0001 | CW Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00PAB-IC-LOG-0001 | CW Piping - Logic Diagrams | ALP-EPC-00PAB-IC-CNR-0001 | CW Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00PAB-IC-LOG-0001 | CW Piping - Logic Diagrams | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00PAB-IC-LOG-0001 | CW Piping - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-03 | 115
ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | ALP-EPC-00PAC-ME-DSH-0001 | CW Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAC-CM-CMP-0001 | CW Pumps - System Commissioning Procedure | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00PAC-CM-CMP-0001 | CW Pumps - System Commissioning Procedure | ALP-EPC-00PAC-IC-CNR-0001 | CW Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00PAC-CM-CMP-0001 | CW Pumps - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-03 | 110
ALP-EPC-00PAC-IC-HMI-0001 | CW Pumps - Operator Displays | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00PAC-IC-HMI-0001 | CW Pumps - Operator Displays | ALP-EPC-00PAC-IC-CNR-0001 | CW Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00PAC-IC-LOG-0001 | CW Pumps - Logic Diagrams | ALP-EPC-00PAC-IC-CNR-0001 | CW Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-05-03 | 0
ALP-EPC-00PAC-IC-LOG-0001 | CW Pumps - Logic Diagrams | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-05-03 | 15
ALP-EPC-00PAC-IC-LOG-0001 | CW Pumps - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-03 | 115
ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | ALP-EPC-00PAH-ME-DSH-0001 | Condenser Tube Cleaning: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | ALP-EPC-00PAH-ME-DSH-0002 | Condenser Tube Cleaning: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-03-12 | 2026-11-02 | -94
ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | ALP-EPC-00PAH-ME-DSH-0003 | Condenser Tube Cleaning: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-03-12 | 2026-11-02 | -94
ALP-EPC-00PAH-CM-CMP-0001 | Condenser Tube Cleaning - System Commissioning Procedure | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-05-04 | 15
ALP-EPC-00PAH-CM-CMP-0001 | Condenser Tube Cleaning - System Commissioning Procedure | ALP-EPC-00PAH-IC-CNR-0001 | Condenser Tube Cleaning - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-04 | 2027-05-04 | 0
ALP-EPC-00PAH-CM-CMP-0001 | Condenser Tube Cleaning - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-04 | 111
ALP-EPC-00PAH-IC-HMI-0001 | Condenser Tube Cleaning - Operator Displays | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-05-04 | 15
ALP-EPC-00PAH-IC-HMI-0001 | Condenser Tube Cleaning - Operator Displays | ALP-EPC-00PAH-IC-CNR-0001 | Condenser Tube Cleaning - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-04 | 2027-05-04 | 0
ALP-EPC-00PAH-IC-LOG-0001 | Condenser Tube Cleaning - Logic Diagrams | ALP-EPC-00PAH-IC-CNR-0001 | Condenser Tube Cleaning - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-04 | 2027-05-04 | 0
ALP-EPC-00PAH-IC-LOG-0001 | Condenser Tube Cleaning - Logic Diagrams | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-05-04 | 15
ALP-EPC-00PAH-IC-LOG-0001 | Condenser Tube Cleaning - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-04 | 116
ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | ALP-EPC-00PBA-ME-DSH-0001 | Electro-Chlorination: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | ALP-EPC-00PBA-ME-DSH-0002 | Electro-Chlorination: Fans - Datasheet | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | ALP-EPC-00PBA-ME-DSH-0003 | Electro-Chlorination: Filters - Datasheet | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | ALP-EPC-00PBA-ME-DSH-0004 | Electro-Chlorination: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-02-16 | 2026-11-02 | -76
ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | ALP-EPC-00PBA-ME-DSH-0005 | Electro-Chlorination: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-00PBA-CM-CMP-0001 | Electro-Chlorination - System Commissioning Procedure | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00PBA-CM-CMP-0001 | Electro-Chlorination - System Commissioning Procedure | ALP-EPC-00PBA-IC-CNR-0001 | Electro-Chlorination - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00PBA-CM-CMP-0001 | Electro-Chlorination - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-26 | 84
ALP-EPC-00PBA-IC-HMI-0001 | Electro-Chlorination - Operator Displays | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00PBA-IC-HMI-0001 | Electro-Chlorination - Operator Displays | ALP-EPC-00PBA-IC-CNR-0001 | Electro-Chlorination - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | ALP-EPC-00PGA-ME-DSH-0001 | Closed Cooling Water: Heat Exchangers - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | ALP-EPC-00PGA-ME-DSH-0002 | Closed Cooling Water: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | ALP-EPC-00PGA-ME-DSH-0003 | Closed Cooling Water: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | ALP-EPC-00PGA-ME-DSH-0004 | Closed Cooling Water: Filter - Datasheet | EPC | IFR | IFC | NONE | 2027-02-23 | 2026-11-02 | -81
ALP-EPC-00PGA-CM-CMP-0001 | Closed Cooling Water - System Commissioning Procedure | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-03-08 | 16
ALP-EPC-00PGA-CM-CMP-0001 | Closed Cooling Water - System Commissioning Procedure | ALP-EPC-00PGA-IC-CNR-0001 | Closed Cooling Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-03-08 | 0
ALP-EPC-00PGA-CM-CMP-0001 | Closed Cooling Water - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-08 | 70
ALP-EPC-00PGA-IC-HMI-0001 | Closed Cooling Water - Operator Displays | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-03-08 | 16
ALP-EPC-00PGA-IC-HMI-0001 | Closed Cooling Water - Operator Displays | ALP-EPC-00PGA-IC-CNR-0001 | Closed Cooling Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-03-08 | 0
ALP-EPC-00PGA-IC-LOG-0001 | Closed Cooling Water - Logic Diagrams | ALP-EPC-00PGA-IC-CNR-0001 | Closed Cooling Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-03-08 | 0
ALP-EPC-00PGA-IC-LOG-0001 | Closed Cooling Water - Logic Diagrams | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-03-08 | 16
ALP-EPC-00PGA-IC-LOG-0001 | Closed Cooling Water - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-08 | 75
ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | ALP-EPC-00QCA-ME-DSH-0001 | Chemical Dosing: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-19 | 99
ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-19 | 99
ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | ALP-EPC-00QCA-ME-DSH-0002 | Chemical Dosing: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-03-19 | 0
ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | ALP-EPC-00QCA-ME-DSH-0003 | Chemical Dosing: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2027-03-18 | 2027-03-19 | 1
ALP-EPC-00QCA-CM-CMP-0001 | Chemical Dosing - System Commissioning Procedure | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00QCA-CM-CMP-0001 | Chemical Dosing - System Commissioning Procedure | ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00QCA-CM-CMP-0001 | Chemical Dosing - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-26 | 84
ALP-EPC-00QCA-IC-HMI-0001 | Chemical Dosing - Operator Displays | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-26 | 15
ALP-EPC-00QCA-IC-HMI-0001 | Chemical Dosing - Operator Displays | ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-26 | 0
ALP-EPC-00QCA-IC-LOG-0001 | Chemical Dosing - Logic Diagrams | ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-03-29 | 1
ALP-EPC-00QCA-IC-LOG-0001 | Chemical Dosing - Logic Diagrams | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-03-29 | 16
ALP-EPC-00QCA-IC-LOG-0001 | Chemical Dosing - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-29 | 90
ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | ALP-EPC-00QEA-ME-DSH-0001 | Compressed Air: Compressors - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | ALP-EPC-00QEA-ME-DSH-0002 | Compressed Air: Filters - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | ALP-EPC-00QEA-ME-DSH-0003 | Compressed Air: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QEA-CM-CMP-0001 | Compressed Air - System Commissioning Procedure | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-03-29 | 15
ALP-EPC-00QEA-CM-CMP-0001 | Compressed Air - System Commissioning Procedure | ALP-EPC-00QEA-IC-CNR-0001 | Compressed Air - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-29 | 2027-03-29 | 0
ALP-EPC-00QEA-CM-CMP-0001 | Compressed Air - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-03-29 | 85
ALP-EPC-00QEA-IC-HMI-0001 | Compressed Air - Operator Displays | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-04-02 | 19
ALP-EPC-00QEA-IC-HMI-0001 | Compressed Air - Operator Displays | ALP-EPC-00QEA-IC-CNR-0001 | Compressed Air - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-29 | 2027-04-02 | 4
ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | ALP-EPC-00QHA-ME-DSH-0001 | Auxiliary Boiler - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | ALP-EPC-00QHA-ME-DSH-0002 | Auxiliary Boiler: Fan - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | ALP-EPC-00QHA-ME-DSH-0003 | Auxiliary Boiler: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | ALP-EPC-00QHA-ME-DSH-0004 | Auxiliary Boiler: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-00QHA-CM-CMP-0001 | Auxiliary Boiler - System Commissioning Procedure | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-04-15 | 16
ALP-EPC-00QHA-CM-CMP-0001 | Auxiliary Boiler - System Commissioning Procedure | ALP-EPC-00QHA-IC-CNR-0001 | Auxiliary Boiler - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-15 | 2027-04-15 | 0
ALP-EPC-00QHA-CM-CMP-0001 | Auxiliary Boiler - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-04-15 | 98
ALP-EPC-00QHA-IC-HMI-0001 | Auxiliary Boiler - Operator Displays | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-05-28 | 47
ALP-EPC-00QHA-IC-HMI-0001 | Auxiliary Boiler - Operator Displays | ALP-EPC-00QHA-IC-CNR-0001 | Auxiliary Boiler - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-15 | 2027-05-28 | 31
ALP-EPC-00QJA-CM-CMP-0001 | Nitrogen Supply - System Commissioning Procedure | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-05-19 | 15
ALP-EPC-00QJA-CM-CMP-0001 | Nitrogen Supply - System Commissioning Procedure | ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-19 | 2027-05-19 | 0
ALP-EPC-00QJA-CM-CMP-0001 | Nitrogen Supply - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-19 | 122
ALP-EPC-00QJA-IC-HMI-0001 | Nitrogen Supply - Operator Displays | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-06-07 | 28
ALP-EPC-00QJA-IC-HMI-0001 | Nitrogen Supply - Operator Displays | ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-19 | 2027-06-07 | 13
ALP-EPC-00QJA-IC-LOG-0001 | Nitrogen Supply - Logic Diagrams | ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-19 | 2027-06-08 | 14
ALP-EPC-00QJA-IC-LOG-0001 | Nitrogen Supply - Logic Diagrams | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-06-08 | 29
ALP-EPC-00QJA-IC-LOG-0001 | Nitrogen Supply - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-06-08 | 141
ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | ALP-EPC-00QJA-ME-DSH-0001 | Nitrogen Supply: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-18 | 98
ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-18 | 98
ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | ALP-EPC-00QJB-ME-DSH-0001 | Hydrogen and CO2 Supply: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-18 | 98
ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | ALP-EPC-00QJA-ME-DSH-0002 | Nitrogen Supply: Tank - Datasheet | EPC | IFR | IFC | NONE | 2027-03-18 | 2027-03-18 | 0
ALP-EPC-00QJB-CM-CMP-0001 | Hydrogen and CO2 Supply - System Commissioning Procedure | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-05-21 | 15
ALP-EPC-00QJB-CM-CMP-0001 | Hydrogen and CO2 Supply - System Commissioning Procedure | ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-21 | 2027-05-21 | 0
ALP-EPC-00QJB-CM-CMP-0001 | Hydrogen and CO2 Supply - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-21 | 124
ALP-EPC-00QJB-IC-HMI-0001 | Hydrogen and CO2 Supply - Operator Displays | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-06-08 | 27
ALP-EPC-00QJB-IC-HMI-0001 | Hydrogen and CO2 Supply - Operator Displays | ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-21 | 2027-06-08 | 12
ALP-EPC-00QJB-IC-LOG-0001 | Hydrogen and CO2 Supply - Logic Diagrams | ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-21 | 2027-06-08 | 12
ALP-EPC-00QJB-IC-LOG-0001 | Hydrogen and CO2 Supply - Logic Diagrams | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-06-08 | 27
ALP-EPC-00QJB-IC-LOG-0001 | Hydrogen and CO2 Supply - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-06-08 | 141
ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | ALP-EPC-00QUA-ME-DSH-0001 | Sampling and SWAS: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | ALP-EPC-00QUA-ME-DSH-0002 | Sampling and SWAS: Heat Exchanger - Datasheet | EPC | IFR | IFC | NONE | 2027-03-22 | 2026-11-02 | -100
ALP-EPC-00QUA-CM-CMP-0001 | Sampling and SWAS - System Commissioning Procedure | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-05-28 | 16
ALP-EPC-00QUA-CM-CMP-0001 | Sampling and SWAS - System Commissioning Procedure | ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-28 | 2027-05-28 | 0
ALP-EPC-00QUA-CM-CMP-0001 | Sampling and SWAS - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-05-28 | 129
ALP-EPC-00QUA-IC-HMI-0001 | Sampling and SWAS - Operator Displays | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-06-14 | 27
ALP-EPC-00QUA-IC-HMI-0001 | Sampling and SWAS - Operator Displays | ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-28 | 2027-06-14 | 11
ALP-EPC-00QUA-IC-LOG-0001 | Sampling and SWAS - Logic Diagrams | ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-28 | 2027-06-14 | 11
ALP-EPC-00QUA-IC-LOG-0001 | Sampling and SWAS - Logic Diagrams | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-06-14 | 27
ALP-EPC-00QUA-IC-LOG-0001 | Sampling and SWAS - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-06-14 | 145
ALP-EPC-00SAA-CM-CMP-0001 | HVAC - System Commissioning Procedure | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-24 | 16
ALP-EPC-00SAA-CM-CMP-0001 | HVAC - System Commissioning Procedure | ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-02-24 | 0
ALP-EPC-00SAA-CM-CMP-0001 | HVAC - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-24 | 62
ALP-EPC-00SAA-IC-HMI-0001 | HVAC - Operator Displays | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-24 | 16
ALP-EPC-00SAA-IC-HMI-0001 | HVAC - Operator Displays | ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-02-24 | 0
ALP-EPC-00SAA-IC-LOG-0001 | HVAC - Logic Diagrams, Part 1 of 2 | ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-02-24 | 0
ALP-EPC-00SAA-IC-LOG-0001 | HVAC - Logic Diagrams, Part 1 of 2 | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-24 | 16
ALP-EPC-00SAA-IC-LOG-0001 | HVAC - Logic Diagrams, Part 1 of 2 | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-24 | 67
ALP-EPC-00SAA-IC-LOG-0002 | HVAC - Logic Diagrams, Part 2 of 2 | ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-02-24 | 0
ALP-EPC-00SAA-IC-LOG-0002 | HVAC - Logic Diagrams, Part 2 of 2 | ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-24 | 16
ALP-EPC-00SAA-IC-LOG-0002 | HVAC - Logic Diagrams, Part 2 of 2 | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-24 | 67
ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | ALP-EPC-00SAA-HV-DSH-0001 | HVAC: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | ALP-EPC-00SAA-ME-DSH-0001 | HVAC: Compressors - Datasheet | EPC | IFR | IFC | NONE | 2027-02-05 | 2026-11-02 | -69
ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | ALP-EPC-00SAA-ME-DSH-0002 | HVAC: Fans - Datasheet | EPC | IFR | IFC | NONE | 2027-02-10 | 2026-11-02 | -72
ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | ALP-EPC-00SAA-ME-DSH-0003 | HVAC: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-02-08 | 2026-11-02 | -70
ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-02-17 | 16
ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure | ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-17 | 0
ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-17 | 57
ALP-EPC-00SGA-IC-HMI-0001 | Fire Water System - Operator Displays | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-02-23 | 20
ALP-EPC-00SGA-IC-HMI-0001 | Fire Water System - Operator Displays | ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-23 | 4
ALP-EPC-00SGA-IC-LOG-0001 | Fire Water System - Logic Diagrams | ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-06-28 | 93
ALP-EPC-00SGA-IC-LOG-0001 | Fire Water System - Logic Diagrams | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-06-28 | 109
ALP-EPC-00SGA-IC-LOG-0001 | Fire Water System - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-06-28 | 155
ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | ALP-EPC-00EGB-ME-DSH-0001 | LDO Storage: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | ALP-EPC-00SGC-ME-DSH-0001 | Deluge, Spray and Foam Systems: Tank - Datasheet | EPC | IFR | IFC | NONE | 2027-02-09 | 2026-11-02 | -71
ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | ALP-EPC-00SGC-ME-DSH-0002 | Deluge, Spray and Foam Systems: Valves - Datasheet | EPC | IFR | IFC | NONE | 2027-02-12 | 2026-11-02 | -74
ALP-EPC-00SGC-CM-CMP-0001 | Deluge, Spray and Foam Systems - System Commissioning Procedure | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-02-17 | 16
ALP-EPC-00SGC-CM-CMP-0001 | Deluge, Spray and Foam Systems - System Commissioning Procedure | ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-02-17 | 0
ALP-EPC-00SGC-CM-CMP-0001 | Deluge, Spray and Foam Systems - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-02-17 | 57
ALP-EPC-00SGC-IC-HMI-0001 | Deluge, Spray and Foam Systems - Operator Displays | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-09-20 | 169
ALP-EPC-00SGC-IC-HMI-0001 | Deluge, Spray and Foam Systems - Operator Displays | ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-09-20 | 153
ALP-EPC-00SGC-IC-LOG-0001 | Deluge, Spray and Foam Systems - Logic Diagrams | ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-09-22 | 155
ALP-EPC-00SGC-IC-LOG-0001 | Deluge, Spray and Foam Systems - Logic Diagrams | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-09-22 | 171
ALP-EPC-00SGC-IC-LOG-0001 | Deluge, Spray and Foam Systems - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-09-22 | 217
ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | ALP-EPC-10HAN-ME-DSH-0001 | HRSG Blowdown and Drains - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | ALP-EPC-10HAN-ME-DSH-0002 | HRSG Blowdown and Drains: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2027-03-12 | 2026-11-02 | -94
ALP-EPC-10HAN-CM-CMP-0001 | HRSG Blowdown and Drains - System Commissioning Procedure | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-08-04 | 58
ALP-EPC-10HAN-CM-CMP-0001 | HRSG Blowdown and Drains - System Commissioning Procedure | ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-08-04 | 43
ALP-EPC-10HAN-CM-CMP-0001 | HRSG Blowdown and Drains - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-04 | 177
ALP-EPC-10HAN-IC-HMI-0001 | HRSG Blowdown and Drains - Operator Displays | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-09-23 | 94
ALP-EPC-10HAN-IC-HMI-0001 | HRSG Blowdown and Drains - Operator Displays | ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-09-23 | 79
ALP-EPC-10HAN-IC-LOG-0001 | HRSG Blowdown and Drains - Logic Diagrams | ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-09-23 | 79
ALP-EPC-10HAN-IC-LOG-0001 | HRSG Blowdown and Drains - Logic Diagrams | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-09-23 | 94
ALP-EPC-10HAN-IC-LOG-0001 | HRSG Blowdown and Drains - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-09-23 | 218
ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | ALP-EPC-10HSB-ME-DSH-0001 | Ammonia Storage and Supply: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | ALP-EPC-10HSB-ME-DSH-0002 | Ammonia Storage and Supply: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | EPC | IFR | IFC | NONE | 2027-05-07 | 2027-06-14 | 26
ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | EPC | IFR | IFC | NONE | 2027-06-14 | 2027-06-14 | 0
ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-23 | 2027-06-14 | 123
ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-06-14 | 120
ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-06-14 | 122
ALP-EPC-00000-HS-HAZ-0010 | Major Accident Assessment and QRA | ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | EPC | IFR | IFC | NONE | 2027-05-07 | 2027-07-19 | 51
ALP-EPC-00000-HS-HAZ-0010 | Major Accident Assessment and QRA | ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | EPC | IFR | IFC | NONE | 2027-06-14 | 2027-07-19 | 25
ALP-EPC-10HSB-CM-CMP-0001 | Ammonia Storage and Supply - System Commissioning Procedure | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-07 | 15
ALP-EPC-10HSB-CM-CMP-0001 | Ammonia Storage and Supply - System Commissioning Procedure | ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-06-07 | 0
ALP-EPC-10HSB-CM-CMP-0001 | Ammonia Storage and Supply - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-07 | 135
ALP-EPC-10HSB-IC-HMI-0001 | Ammonia Storage and Supply - Operator Displays | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-24 | 94
ALP-EPC-10HSB-IC-HMI-0001 | Ammonia Storage and Supply - Operator Displays | ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-09-24 | 79
ALP-EPC-10HSB-IC-LOG-0001 | Ammonia Storage and Supply - Logic Diagrams | ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-09-24 | 79
ALP-EPC-10HSB-IC-LOG-0001 | Ammonia Storage and Supply - Logic Diagrams | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-24 | 94
ALP-EPC-10HSB-IC-LOG-0001 | Ammonia Storage and Supply - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-09-24 | 219
ALP-EPC-10LAB-CM-CMP-0001 | Feedwater Piping - System Commissioning Procedure | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-08-04 | 56
ALP-EPC-10LAB-CM-CMP-0001 | Feedwater Piping - System Commissioning Procedure | ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-08-04 | 41
ALP-EPC-10LAB-CM-CMP-0001 | Feedwater Piping - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-04 | 177
ALP-EPC-10LAB-IC-HMI-0001 | Feedwater Piping - Operator Displays | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-24 | 93
ALP-EPC-10LAB-IC-HMI-0001 | Feedwater Piping - Operator Displays | ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-09-24 | 78
ALP-EPC-10LAB-IC-LOG-0001 | Feedwater Piping - Logic Diagrams | ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-09-27 | 79
ALP-EPC-10LAB-IC-LOG-0001 | Feedwater Piping - Logic Diagrams | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-27 | 94
ALP-EPC-10LAB-IC-LOG-0001 | Feedwater Piping - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-09-27 | 220
ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | ALP-EPC-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10LAC-CM-CMP-0001 | Boiler Feed Pumps - System Commissioning Procedure | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-08-06 | 58
ALP-EPC-10LAC-CM-CMP-0001 | Boiler Feed Pumps - System Commissioning Procedure | ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-08-06 | 42
ALP-EPC-10LAC-CM-CMP-0001 | Boiler Feed Pumps - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-06 | 179
ALP-EPC-10LAC-IC-HMI-0001 | Boiler Feed Pumps - Operator Displays | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-29 | 96
ALP-EPC-10LAC-IC-HMI-0001 | Boiler Feed Pumps - Operator Displays | ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-09-29 | 80
ALP-EPC-10LAC-IC-LOG-0001 | Boiler Feed Pumps - Logic Diagrams | ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-09-29 | 80
ALP-EPC-10LAC-IC-LOG-0001 | Boiler Feed Pumps - Logic Diagrams | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-29 | 96
ALP-EPC-10LAC-IC-LOG-0001 | Boiler Feed Pumps - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-09-29 | 222
ALP-EPC-10LAE-CM-CMP-0001 | HP Attemperation Spray Water - System Commissioning Procedure | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-08-06 | 59
ALP-EPC-10LAE-CM-CMP-0001 | HP Attemperation Spray Water - System Commissioning Procedure | ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-08-06 | 44
ALP-EPC-10LAE-CM-CMP-0001 | HP Attemperation Spray Water - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-06 | 179
ALP-EPC-10LAE-IC-HMI-0001 | HP Attemperation Spray Water - Operator Displays | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-09-08 | 82
ALP-EPC-10LAE-IC-HMI-0001 | HP Attemperation Spray Water - Operator Displays | ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-09-08 | 67
ALP-EPC-10LAE-IC-LOG-0001 | HP Attemperation Spray Water - Logic Diagrams | ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-10-06 | 87
ALP-EPC-10LAE-IC-LOG-0001 | HP Attemperation Spray Water - Logic Diagrams | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-10-06 | 102
ALP-EPC-10LAE-IC-LOG-0001 | HP Attemperation Spray Water - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-10-06 | 227
ALP-EPC-10LAF-CM-CMP-0001 | Reheat Attemperation Spray Water - System Commissioning Procedure | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-08-06 | 58
ALP-EPC-10LAF-CM-CMP-0001 | Reheat Attemperation Spray Water - System Commissioning Procedure | ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-08-06 | 43
ALP-EPC-10LAF-CM-CMP-0001 | Reheat Attemperation Spray Water - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-06 | 179
ALP-EPC-10LAF-IC-HMI-0001 | Reheat Attemperation Spray Water - Operator Displays | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-08 | 103
ALP-EPC-10LAF-IC-HMI-0001 | Reheat Attemperation Spray Water - Operator Displays | ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-10-08 | 88
ALP-EPC-10LAF-IC-LOG-0001 | Reheat Attemperation Spray Water - Logic Diagrams | ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-10-08 | 88
ALP-EPC-10LAF-IC-LOG-0001 | Reheat Attemperation Spray Water - Logic Diagrams | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-08 | 103
ALP-EPC-10LAF-IC-LOG-0001 | Reheat Attemperation Spray Water - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-10-08 | 229
ALP-EPC-10LBA-CM-CMP-0001 | Main Steam Piping - System Commissioning Procedure | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-08-16 | 53
ALP-EPC-10LBA-CM-CMP-0001 | Main Steam Piping - System Commissioning Procedure | ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-16 | 38
ALP-EPC-10LBA-CM-CMP-0001 | Main Steam Piping - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-16 | 185
ALP-EPC-10LBA-IC-HMI-0001 | Main Steam Piping - Operator Displays | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-08 | 92
ALP-EPC-10LBA-IC-HMI-0001 | Main Steam Piping - Operator Displays | ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-10-08 | 77
ALP-EPC-10LBA-IC-LOG-0001 | Main Steam Piping - Logic Diagrams | ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-10-08 | 77
ALP-EPC-10LBA-IC-LOG-0001 | Main Steam Piping - Logic Diagrams | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-08 | 92
ALP-EPC-10LBA-IC-LOG-0001 | Main Steam Piping - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-10-08 | 229
ALP-EPC-10LBB-CM-CMP-0001 | Hot Reheat Piping - System Commissioning Procedure | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-08-17 | 54
ALP-EPC-10LBB-CM-CMP-0001 | Hot Reheat Piping - System Commissioning Procedure | ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-17 | 39
ALP-EPC-10LBB-CM-CMP-0001 | Hot Reheat Piping - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-17 | 186
ALP-EPC-10LBB-IC-HMI-0001 | Hot Reheat Piping - Operator Displays | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-12 | 94
ALP-EPC-10LBB-IC-HMI-0001 | Hot Reheat Piping - Operator Displays | ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-10-12 | 79
ALP-EPC-10LBB-IC-LOG-0001 | Hot Reheat Piping - Logic Diagrams | ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-10-13 | 80
ALP-EPC-10LBB-IC-LOG-0001 | Hot Reheat Piping - Logic Diagrams | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-13 | 95
ALP-EPC-10LBB-IC-LOG-0001 | Hot Reheat Piping - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-10-13 | 232
ALP-EPC-10LBC-CM-CMP-0001 | Cold Reheat Piping - System Commissioning Procedure | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-08-17 | 53
ALP-EPC-10LBC-CM-CMP-0001 | Cold Reheat Piping - System Commissioning Procedure | ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-24 | 2027-08-17 | 38
ALP-EPC-10LBC-CM-CMP-0001 | Cold Reheat Piping - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-17 | 186
ALP-EPC-10LBC-IC-HMI-0001 | Cold Reheat Piping - Operator Displays | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-10-13 | 94
ALP-EPC-10LBC-IC-HMI-0001 | Cold Reheat Piping - Operator Displays | ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-24 | 2027-10-13 | 79
ALP-EPC-10LBC-IC-LOG-0001 | Cold Reheat Piping - Logic Diagrams | ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-24 | 2027-10-15 | 81
ALP-EPC-10LBC-IC-LOG-0001 | Cold Reheat Piping - Logic Diagrams | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-10-15 | 96
ALP-EPC-10LBC-IC-LOG-0001 | Cold Reheat Piping - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-10-15 | 234
ALP-EPC-10LBA-GE-RPT-0001 | Alloy Piping P91 / P22 - Technical Bid Evaluation | ALP-EPC-00000-PI-MRQ-0002 | Alloy Piping P91 / P22 - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-01-14 | 28
ALP-EPC-10LBD-CM-CMP-0001 | LP Steam Piping - System Commissioning Procedure | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-08-19 | 53
ALP-EPC-10LBD-CM-CMP-0001 | LP Steam Piping - System Commissioning Procedure | ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-08-19 | 38
ALP-EPC-10LBD-CM-CMP-0001 | LP Steam Piping - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-19 | 188
ALP-EPC-10LBD-IC-HMI-0001 | LP Steam Piping - Operator Displays | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-10-18 | 95
ALP-EPC-10LBD-IC-HMI-0001 | LP Steam Piping - Operator Displays | ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-10-18 | 80
ALP-EPC-10LBD-IC-LOG-0001 | LP Steam Piping - Logic Diagrams | ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-10-18 | 80
ALP-EPC-10LBD-IC-LOG-0001 | LP Steam Piping - Logic Diagrams | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-10-18 | 95
ALP-EPC-10LBD-IC-LOG-0001 | LP Steam Piping - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-10-18 | 235
ALP-EPC-20LCA-CM-CMP-0001 | Main Condensate Piping - System Commissioning Procedure | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-08-19 | 67
ALP-EPC-20LCA-CM-CMP-0001 | Main Condensate Piping - System Commissioning Procedure | ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-08-19 | 52
ALP-EPC-20LCA-CM-CMP-0001 | Main Condensate Piping - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-19 | 188
ALP-EPC-20LCA-IC-HMI-0001 | Main Condensate Piping - Operator Displays | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-21 | 112
ALP-EPC-20LCA-IC-HMI-0001 | Main Condensate Piping - Operator Displays | ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-10-21 | 97
ALP-EPC-20LCA-IC-LOG-0001 | Main Condensate Piping - Logic Diagrams | ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-10-22 | 98
ALP-EPC-20LCA-IC-LOG-0001 | Main Condensate Piping - Logic Diagrams | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-10-22 | 113
ALP-EPC-20LCA-IC-LOG-0001 | Main Condensate Piping - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-10-22 | 239
ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | ALP-EPC-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20LCB-CM-CMP-0001 | Condensate Extraction Pumps - System Commissioning Procedure | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-08-24 | 54
ALP-EPC-20LCB-CM-CMP-0001 | Condensate Extraction Pumps - System Commissioning Procedure | ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-08-24 | 39
ALP-EPC-20LCB-CM-CMP-0001 | Condensate Extraction Pumps - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-08-24 | 191
ALP-EPC-20LCB-IC-HMI-0001 | Condensate Extraction Pumps - Operator Displays | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-10-26 | 99
ALP-EPC-20LCB-IC-HMI-0001 | Condensate Extraction Pumps - Operator Displays | ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-10-26 | 84
ALP-EPC-20LCB-IC-LOG-0001 | Condensate Extraction Pumps - Logic Diagrams | ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-10-27 | 85
ALP-EPC-20LCB-IC-LOG-0001 | Condensate Extraction Pumps - Logic Diagrams | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-10-27 | 100
ALP-EPC-20LCB-IC-LOG-0001 | Condensate Extraction Pumps - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-10-27 | 242
ALP-EPC-00000-CM-TRP-0001 | Steam Blowing and Chemical Cleaning Report | ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | EPC | IFR | IFC | NONE | 2027-08-06 | 2028-09-18 | 291
ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | EPC | IFR | IFC | NONE | 2027-05-07 | 2027-07-07 | 43
ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | EPC | IFR | IFC | NONE | 2027-07-07 | 2027-07-07 | 0
ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | EPC | IFR | IFC | NONE | 2027-06-14 | 2027-07-07 | 17
ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | EPC | IFR | IFC | NONE | 2027-06-15 | 2027-07-07 | 16
ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-07-07 | 25
ALP-EPC-00000-HS-RPT-0004 | HAZOP Close-Out Report | ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | EPC | IFR | IFC | NONE | 2027-05-07 | 2027-07-20 | 52
ALP-EPC-00000-HS-RPT-0004 | HAZOP Close-Out Report | ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | EPC | IFR | IFC | NONE | 2027-07-07 | 2027-07-20 | 9
ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | ALP-IEC-10MBY-IC-IOL-0001 | Turbine Control System - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IFR | ACCEPTED | NONE | 2027-02-22 | 2027-06-30 | 92
ALP-EPC-00UAC-IC-ELY-0002 | 380 kV GIS Switchyard - Instrument Location and I&C Cable Routing | ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2027-06-30 | 151
ALP-EPC-00UAC-IC-ELY-0002 | 380 kV GIS Switchyard - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UAC-IC-HUP-0001 | 380 kV GIS Switchyard - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UAC-IC-HUP-0001 | 380 kV GIS Switchyard - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-00UBA-IC-ELY-0002 | Electrical Building and Emergency Power - Instrument Location and I&C Cable Routing | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-09 | 2027-06-30 | 145
ALP-EPC-00UBA-IC-ELY-0002 | Electrical Building and Emergency Power - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UBA-IC-HUP-0001 | Electrical Building and Emergency Power - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UBA-IC-HUP-0001 | Electrical Building and Emergency Power - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-00UCA-IC-ELY-0001 | Control, Administration and Workshop Buildings - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UCA-IC-ELY-0001 | Control, Administration and Workshop Buildings - Instrument Location and I&C Cable Routing | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-06-30 | 141
ALP-EPC-00UCA-IC-HUP-0001 | Control, Administration and Workshop Buildings - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UCA-IC-HUP-0001 | Control, Administration and Workshop Buildings - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-00UEG-IC-ELY-0001 | LDO Tank Farm and Unloading - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UEG-IC-ELY-0001 | LDO Tank Farm and Unloading - Instrument Location and I&C Cable Routing | ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-23 | 2027-06-30 | 135
ALP-EPC-00UEG-IC-HUP-0001 | LDO Tank Farm and Unloading - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UEG-IC-HUP-0001 | LDO Tank Farm and Unloading - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-00UEK-IC-ELY-0001 | Fuel Gas Station - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UEK-IC-ELY-0001 | Fuel Gas Station - Instrument Location and I&C Cable Routing | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-06-30 | 132
ALP-EPC-00UEK-IC-HUP-0001 | Fuel Gas Station - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UEK-IC-HUP-0001 | Fuel Gas Station - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-00UGA-IC-ELY-0001 | Water Treatment and Effluents - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UGA-IC-ELY-0001 | Water Treatment and Effluents - Instrument Location and I&C Cable Routing | ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-06-30 | 141
ALP-EPC-00UGA-IC-HUP-0001 | Water Treatment and Effluents - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UGA-IC-HUP-0001 | Water Treatment and Effluents - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-00UPC-IC-ELY-0001 | CW Pump House and Onshore CW - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UPC-IC-ELY-0001 | CW Pump House and Onshore CW - Instrument Location and I&C Cable Routing | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-03 | 2027-06-30 | 149
ALP-EPC-00UPC-IC-HUP-0001 | CW Pump House and Onshore CW - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UPC-IC-HUP-0001 | CW Pump House and Onshore CW - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-00UQA-IC-ELY-0001 | BOP Utilities - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UQA-IC-ELY-0001 | BOP Utilities - Instrument Location and I&C Cable Routing | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-22 | 2027-06-30 | 136
ALP-EPC-00UQA-IC-HUP-0001 | BOP Utilities - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UQA-IC-HUP-0001 | BOP Utilities - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-00UZA-IC-ELY-0001 | Site-Wide Infrastructure - Instrument Location and I&C Cable Routing | ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2027-06-30 | 151
ALP-EPC-00UZA-IC-ELY-0001 | Site-Wide Infrastructure - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UZA-IC-HUP-0001 | Site-Wide Infrastructure - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-00UZA-IC-HUP-0001 | Site-Wide Infrastructure - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-10UMA-IC-ELY-0001 | Power Block - GT and HRSG - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-10UMA-IC-ELY-0001 | Power Block - GT and HRSG - Instrument Location and I&C Cable Routing | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2027-06-30 | 134
ALP-EPC-10UMA-IC-HUP-0001 | Power Block - GT and HRSG - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-10UMA-IC-HUP-0001 | Power Block - GT and HRSG - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-20UMB-IC-ELY-0001 | Power Block - ST and Condenser - Instrument Location and I&C Cable Routing | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-20UMB-IC-ELY-0001 | Power Block - ST and Condenser - Instrument Location and I&C Cable Routing | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-11 | 2027-06-30 | 143
ALP-EPC-20UMB-IC-HUP-0001 | Power Block - ST and Condenser - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-06-30 | 0
ALP-EPC-20UMB-IC-HUP-0001 | Power Block - ST and Condenser - Instrument Hook-Up Drawings | ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-06-30 | 152
ALP-EPC-20MAN-CM-CMP-0001 | Turbine Bypass Stations and Piping - System Commissioning Procedure | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-01 | 76
ALP-EPC-20MAN-CM-CMP-0001 | Turbine Bypass Stations and Piping - System Commissioning Procedure | ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-09-01 | 61
ALP-EPC-20MAN-CM-CMP-0001 | Turbine Bypass Stations and Piping - System Commissioning Procedure | ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | EPC | IFR | IFC | NONE | 2026-11-30 | 2027-09-01 | 197
ALP-EPC-20MAN-IC-HMI-0001 | Turbine Bypass Stations and Piping - Operator Displays | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-11-01 | 119
ALP-EPC-20MAN-IC-HMI-0001 | Turbine Bypass Stations and Piping - Operator Displays | ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-11-01 | 104
ALP-EPC-20MAN-IC-LOG-0001 | Turbine Bypass Stations and Piping - Logic Diagrams | ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-11-01 | 104
ALP-EPC-20MAN-IC-LOG-0001 | Turbine Bypass Stations and Piping - Logic Diagrams | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-11-01 | 119
ALP-EPC-20MAN-IC-LOG-0001 | Turbine Bypass Stations and Piping - Logic Diagrams | ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-11-01 | 245
ALP-EPC-00000-EL-SPC-0003 | Revenue Metering and TSO SCADA Interface Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-27 | 214
ALP-EPC-00000-EL-STU-0001 | Load Flow, Short-Circuit and Motor Starting Study | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-07 | 25
ALP-EPC-00000-EL-STU-0005 | Insulation Coordination Study | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-EL-STU-0006 | Grid Code Compliance and Reactive Capability Study | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-EPC-00000-EL-STU-0006 | Grid Code Compliance and Reactive Capability Study | ALP-IEC-10MKA-EL-DSH-0001 | Generators, Excitation, GCB and Busducts - Supplier Certified Datasheets and Performance Curves | IEC | IFR | ACCEPTED | ACCEPTED | 2026-09-28 | 2026-12-24 | 63
ALP-EPC-00000-GE-SPC-0002 | Electrical and I&C Installation - Technical Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-04 | 2
ALP-EPC-00000-GE-SPC-0002 | Electrical and I&C Installation - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-04 | 2
ALP-EPC-00ACA-EL-SLD-0001 | 380 kV GIS Switchyard - Single Line Diagram | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-07 | 243
ALP-EPC-00ACA-EL-SLD-0001 | 380 kV GIS Switchyard - Single Line Diagram | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-07 | 243
ALP-EPC-00BBA-EL-SLD-0001 | MV Switchgear 10.5 kV - Single Line Diagram | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-10 | 28
ALP-EPC-00BBA-EL-SLD-0001 | MV Switchgear 10.5 kV - Single Line Diagram | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-10 | 28
ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-16 | 32
ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-16 | 32
ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BLA-EL-SLD-0001 | Lighting and Small Power - Single Line Diagram | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-07 | 243
ALP-EPC-00BLA-EL-SLD-0001 | Lighting and Small Power - Single Line Diagram | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-07 | 243
ALP-EPC-00BMA-EL-SLD-0001 | Emergency LV Switchgear - Single Line Diagram | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-18 | 250
ALP-EPC-00BMA-EL-SLD-0001 | Emergency LV Switchgear - Single Line Diagram | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-18 | 250
ALP-EPC-00BRA-EL-SLD-0001 | UPS - Single Line Diagram | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-19 | 251
ALP-EPC-00BRA-EL-SLD-0001 | UPS - Single Line Diagram | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-19 | 251
ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UAC-EL-ELY-0001 | 380 kV GIS Switchyard - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-02 | 66
ALP-EPC-00UAC-EL-ELY-0001 | 380 kV GIS Switchyard - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-02-02 | 26
ALP-EPC-00UAC-EL-ELY-0001 | 380 kV GIS Switchyard - Electrical Layouts | ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2027-02-02 | 45
ALP-EPC-00UBA-EL-ELY-0001 | Electrical Building and Emergency Power - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-28 | 40
ALP-EPC-00UBA-EL-ELY-0001 | Electrical Building and Emergency Power - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00UBA-EL-ELY-0001 | Electrical Building and Emergency Power - Electrical Layouts | ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-09 | 2026-12-28 | 13
ALP-EPC-00UCA-EL-ELY-0001 | Control, Administration and Workshop Buildings - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-28 | 40
ALP-EPC-00UCA-EL-ELY-0001 | Control, Administration and Workshop Buildings - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00UCA-EL-ELY-0001 | Control, Administration and Workshop Buildings - Electrical Layouts | ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2026-12-28 | 9
ALP-EPC-00UEG-EL-ELY-0001 | LDO Tank Farm and Unloading - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-09 | 157
ALP-EPC-00UEG-EL-ELY-0001 | LDO Tank Farm and Unloading - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-06-09 | 117
ALP-EPC-00UEG-EL-ELY-0001 | LDO Tank Farm and Unloading - Electrical Layouts | ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-23 | 2027-06-09 | 120
ALP-EPC-00UEK-EL-ELY-0001 | Fuel Gas Station - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-EPC-00UEK-EL-ELY-0001 | Fuel Gas Station - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-01-28 | 23
ALP-EPC-00UEK-EL-ELY-0001 | Fuel Gas Station - Electrical Layouts | ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-01-28 | 23
ALP-EPC-00UGA-EL-ELY-0001 | Water Treatment and Effluents - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-16 | 184
ALP-EPC-00UGA-EL-ELY-0001 | Water Treatment and Effluents - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-07-16 | 144
ALP-EPC-00UGA-EL-ELY-0001 | Water Treatment and Effluents - Electrical Layouts | ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-15 | 2027-07-16 | 153
ALP-EPC-00UPA-EL-ELY-0002 | Marine Works - Electrical Layouts | ALP-EPC-00UPA-PI-LAY-0001 | Marine Works - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-29 | 2026-12-29 | 0
ALP-EPC-00UPA-EL-ELY-0002 | Marine Works - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-29 | 41
ALP-EPC-00UPA-EL-ELY-0002 | Marine Works - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-29 | 1
ALP-EPC-00UPC-EL-ELY-0001 | CW Pump House and Onshore CW - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-15 | 161
ALP-EPC-00UPC-EL-ELY-0001 | CW Pump House and Onshore CW - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-06-15 | 121
ALP-EPC-00UPC-EL-ELY-0001 | CW Pump House and Onshore CW - Electrical Layouts | ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-03 | 2027-06-15 | 138
ALP-EPC-00UQA-EL-ELY-0001 | BOP Utilities - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-29 | 64
ALP-EPC-00UQA-EL-ELY-0001 | BOP Utilities - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-01-29 | 24
ALP-EPC-00UQA-EL-ELY-0001 | BOP Utilities - Electrical Layouts | ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-22 | 2027-01-29 | 28
ALP-EPC-00UZA-EL-ELY-0001 | Site-Wide Infrastructure - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-28 | 40
ALP-EPC-00UZA-EL-ELY-0001 | Site-Wide Infrastructure - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-00UZA-EL-ELY-0001 | Site-Wide Infrastructure - Electrical Layouts | ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-01 | 2026-12-28 | 19
ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10UMA-EL-ELY-0001 | Power Block - GT and HRSG - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-28 | 40
ALP-EPC-10UMA-EL-ELY-0001 | Power Block - GT and HRSG - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2026-12-28 | 0
ALP-EPC-10UMA-EL-ELY-0001 | Power Block - GT and HRSG - Electrical Layouts | ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-24 | 2026-12-28 | 2
ALP-EPC-20UMB-EL-ELY-0001 | Power Block - ST and Condenser - Electrical Layouts | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-01 | 173
ALP-EPC-20UMB-EL-ELY-0001 | Power Block - ST and Condenser - Electrical Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-07-01 | 133
ALP-EPC-20UMB-EL-ELY-0001 | Power Block - ST and Condenser - Electrical Layouts | ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | EPC | IFR | IFC | NONE | 2026-12-11 | 2027-07-01 | 144
ALP-C03-00UPA-GE-ITP-0001 | Marine Works - Subcontractor Inspection and Test Plans | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-C03-00UPA-GE-MOS-0001 | Marine Works - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-C03-00UPA-GE-MOS-0002 | Marine Works - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-C03-00UPA-GE-MOS-0003 | Marine Works - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-C03-00UPA-GE-MOS-0004 | Marine Works - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-C03-00UPA-GE-MOS-0005 | Marine Works - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-C03-00UPA-GE-MOS-0006 | Marine Works - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-C01-00000-GE-ITP-0001 | Piling Works - Subcontractor Inspection and Test Plans | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-C01-00000-GE-MOS-0001 | Piling Works - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-C01-00000-GE-MOS-0002 | Piling Works - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-C01-00000-GE-MOS-0003 | Piling Works - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-C01-00000-GE-MOS-0004 | Piling Works - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-C01-00000-GE-MOS-0005 | Piling Works - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-C01-00000-GE-MOS-0006 | Piling Works - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-EPC-00CJG-GE-RPT-0001 | BOP Safety Instrumented System - Technical Bid Evaluation | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-04-08 | 33
ALP-EPC-00CKA-GE-RPT-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Bid Evaluation | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-04-22 | 43
ALP-EPC-00CQA-GE-RPT-0001 | Continuous Emission Monitoring System - Technical Bid Evaluation | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-24 | 82
ALP-EPC-00CYA-GE-RPT-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Bid Evaluation | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-05-03 | 33
ALP-M22-00000-GE-ITP-0001 | Painting and Insulation - Subcontractor Inspection and Test Plans | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-06-30 | 48
ALP-M22-00000-GE-MOS-0001 | Painting and Insulation - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-06-30 | 48
ALP-M22-00000-GE-MOS-0002 | Painting and Insulation - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-06-30 | 48
ALP-M22-00000-GE-MOS-0003 | Painting and Insulation - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-06-30 | 48
ALP-M22-00000-GE-MOS-0004 | Painting and Insulation - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-06-30 | 48
ALP-M22-00000-GE-MOS-0005 | Painting and Insulation - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-06-30 | 48
ALP-M22-00000-GE-MOS-0006 | Painting and Insulation - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-06-30 | 48
ALP-M23-00000-GE-ITP-0001 | Mechanical and Piping Erection - Subcontractor Inspection and Test Plans | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-09-15 | 58
ALP-M23-00000-GE-MOS-0001 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-09-15 | 58
ALP-M23-00000-GE-MOS-0002 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-09-15 | 58
ALP-M23-00000-GE-MOS-0003 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-09-15 | 58
ALP-M23-00000-GE-MOS-0004 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-09-15 | 58
ALP-M23-00000-GE-MOS-0005 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-09-15 | 58
ALP-M23-00000-GE-MOS-0006 | Mechanical and Piping Erection - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-09-15 | 58
ALP-EPC-00SMA-GE-RPT-0001 | EOT Cranes - Technical Bid Evaluation | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-17 | 33
ALP-S02-10HNE-CV-CAL-0001 | Stack 65 m with Silencer - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-11 | 68
ALP-S02-10HNE-GE-ITP-0001 | Stack 65 m with Silencer - Subcontractor Inspection and Test Plans | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-09 | 66
ALP-S02-10HNE-GE-MOS-0001 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-09 | 66
ALP-S02-10HNE-GE-MOS-0002 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-09 | 66
ALP-S02-10HNE-GE-MOS-0003 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-09 | 66
ALP-S02-10HNE-GE-MOS-0004 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-09 | 66
ALP-S02-10HNE-GE-MOS-0005 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-09 | 66
ALP-S02-10HNE-GE-MOS-0006 | Stack 65 m with Silencer - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-09 | 2027-02-09 | 66
ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-03-17 | 10
ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | ALP-EPC-00SGY-IC-DSH-0001 | Fire Detection and Alarm: Control System - Datasheet | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-03-17 | 0
ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | ALP-EPC-00UZF-GE-SPC-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Specification | EPC | IFR | IFC | NONE | 2027-06-16 | 2027-06-16 | 0
ALP-EPC-00SAA-PI-SUP-0001 | HVAC - Pipe Support Drawings | ALP-EPC-00SAA-PI-ISO-0001 | HVAC - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-09-09 | 2027-09-09 | 0
ALP-EPC-00UZF-CV-RBR-0001 | Temporary Barge Landing - Reinforcement Drawings | ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-07-02 | 2027-07-02 | 0
ALP-EPC-00UZF-EL-ELY-0001 | Temporary Barge Landing - Earthing and Lightning Protection Layouts | ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-07-02 | 2027-07-02 | 0
ALP-EPC-00UZF-EL-ELY-0001 | Temporary Barge Landing - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-07-02 | 134
ALP-EPC-00UZF-EL-ELY-0001 | Temporary Barge Landing - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-07-02 | 133
ALP-EPC-00UPC-CV-RBR-0001 | CW Pump House - Reinforcement Drawings | ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-25 | 2027-03-04 | 5
ALP-EPC-00UPC-EL-ELY-0003 | CW Pump House - Earthing and Lightning Protection Layouts | ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-25 | 2027-08-11 | 119
ALP-EPC-00UPC-EL-ELY-0003 | CW Pump House - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-08-11 | 162
ALP-EPC-00UPC-EL-ELY-0003 | CW Pump House - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-08-11 | 161
ALP-EPC-00000-GE-SPC-0001 | Construction Power Supply - Technical Specification | ALP-EPC-00000-EL-SLD-0002 | Construction Power Supply Single Line Diagram and RMU Design | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-GE-SPC-0001 | Construction Power Supply - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UBF-CV-RBR-0001 | Transformer Bays - Reinforcement Drawings | ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-09 | 2027-03-29 | 14
ALP-EPC-00UBF-EL-ELY-0001 | Transformer Bays - Earthing and Lightning Protection Layouts | ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-09 | 2027-08-10 | 110
ALP-EPC-00UBF-EL-ELY-0001 | Transformer Bays - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-08-10 | 161
ALP-EPC-00UBF-EL-ELY-0001 | Transformer Bays - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-08-10 | 160
ALP-EPC-10UHA-CV-RBR-0001 | HRSG Foundations and Structures - Reinforcement Drawings | ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-03-18 | 10
ALP-EPC-10UHA-EL-ELY-0001 | HRSG Foundations and Structures - Earthing and Lightning Protection Layouts | ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-08-10 | 113
ALP-EPC-10UHA-EL-ELY-0001 | HRSG Foundations and Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-08-10 | 161
ALP-EPC-10UHA-EL-ELY-0001 | HRSG Foundations and Structures - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-08-10 | 160
ALP-EPC-10UHN-CV-RBR-0001 | Stack Foundation - Reinforcement Drawings | ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-10 | 2027-04-06 | 19
ALP-EPC-10UHN-EL-ELY-0001 | Stack Foundation - Earthing and Lightning Protection Layouts | ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-10 | 2027-03-16 | 4
ALP-EPC-10UHN-EL-ELY-0001 | Stack Foundation - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-03-16 | 56
ALP-EPC-10UHN-EL-ELY-0001 | Stack Foundation - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-03-16 | 55
ALP-EPC-10UMA-CV-RBR-0001 | Gas Turbine Hall - Reinforcement Drawings | ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-12 | 2027-03-12 | 0
ALP-EPC-10UMA-EL-ELY-0003 | Gas Turbine Hall - Earthing and Lightning Protection Layouts | ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-12 | 2027-08-09 | 106
ALP-EPC-10UMA-EL-ELY-0003 | Gas Turbine Hall - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-08-09 | 160
ALP-EPC-10UMA-EL-ELY-0003 | Gas Turbine Hall - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-08-09 | 159
ALP-EPC-20UMB-CV-RBR-0001 | Steam Turbine Hall - Reinforcement Drawings | ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-16 | 2027-03-16 | 0
ALP-EPC-20UMB-EL-ELY-0003 | Steam Turbine Hall - Earthing and Lightning Protection Layouts | ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-16 | 2027-08-25 | 116
ALP-EPC-20UMB-EL-ELY-0003 | Steam Turbine Hall - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0003 | Earthing Study | EPC | IFR | IFC | NONE | 2026-12-28 | 2027-08-25 | 172
ALP-EPC-20UMB-EL-ELY-0003 | Steam Turbine Hall - Earthing and Lightning Protection Layouts | ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | EPC | IFR | IFC | NONE | 2026-12-29 | 2027-08-25 | 171
ALP-EPC-00EGA-PI-ISO-0001 | LDO Unloading - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-07-09 | 25
ALP-EPC-00EGA-PI-ISO-0001 | LDO Unloading - Isometric Drawings | ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-07-09 | 76
ALP-EPC-00EGA-PI-ISO-0001 | LDO Unloading - Isometric Drawings | ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-07-09 | 92
ALP-EPC-00EGB-PI-ISO-0001 | LDO Storage - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-07-20 | 32
ALP-EPC-00EGB-PI-ISO-0001 | LDO Storage - Isometric Drawings | ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | EPC | IFR | IFC | NONE | 2027-04-06 | 2027-07-20 | 75
ALP-EPC-00EGB-PI-ISO-0001 | LDO Storage - Isometric Drawings | ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-07-20 | 99
ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-07-26 | 36
ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings | ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-01-27 | 2027-07-26 | 128
ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings | ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-07-26 | 103
ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings | ALP-EPC-00EGC-PI-STR-0001 | LDO Forwarding and Treatment - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-07-26 | 2027-07-26 | 0
ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-07-13 | 27
ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings | ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | EPC | IFR | IFC | NONE | 2027-01-25 | 2027-07-13 | 121
ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings | ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-07-13 | 91
ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings | ALP-EPC-00EKA-PI-STR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-07-13 | 2027-07-13 | 0
ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-07-27 | 37
ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings | ALP-EPC-00EKC-PI-STR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-07-27 | 2027-07-27 | 0
ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings | ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-07-27 | 77
ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings | ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-07-27 | 101
ALP-EPC-00GBA-PI-ISO-0001 | Seawater Reverse Osmosis - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-10-29 | 105
ALP-EPC-00GBA-PI-ISO-0001 | Seawater Reverse Osmosis - Isometric Drawings | ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | EPC | IFR | IFC | NONE | 2027-03-01 | 2027-10-29 | 174
ALP-EPC-00GBA-PI-ISO-0001 | Seawater Reverse Osmosis - Isometric Drawings | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-10-29 | 172
ALP-EPC-00GCA-PI-ISO-0001 | Demineralisation - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-11-11 | 114
ALP-EPC-00GCA-PI-ISO-0001 | Demineralisation - Isometric Drawings | ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | EPC | IFR | IFC | NONE | 2027-04-09 | 2027-11-11 | 154
ALP-EPC-00GCA-PI-ISO-0001 | Demineralisation - Isometric Drawings | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-11-11 | 181
ALP-EPC-00GHA-PI-ISO-0001 | Demineralised Water Storage and Distribution - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-11-24 | 123
ALP-EPC-00GHA-PI-ISO-0001 | Demineralised Water Storage and Distribution - Isometric Drawings | ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-11-24 | 162
ALP-EPC-00GHA-PI-ISO-0001 | Demineralised Water Storage and Distribution - Isometric Drawings | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-11-24 | 190
ALP-EPC-00GKA-PI-ISO-0001 | Potable Water - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-06-24 | 14
ALP-EPC-00GKA-PI-ISO-0001 | Potable Water - Isometric Drawings | ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-06-24 | 28
ALP-EPC-00GKA-PI-ISO-0001 | Potable Water - Isometric Drawings | ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-02-15 | 2027-06-24 | 93
ALP-EPC-00GMA-PI-ISO-0001 | Process Drains and Waste Water Collection - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-06-04 | 0
ALP-EPC-00GMA-PI-ISO-0001 | Process Drains and Waste Water Collection - Isometric Drawings | ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-06-04 | 66
ALP-EPC-00GMA-PI-ISO-0001 | Process Drains and Waste Water Collection - Isometric Drawings | ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-02-15 | 2027-06-04 | 79
ALP-EPC-00GNA-PI-ISO-0001 | Waste Water Treatment - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-11-15 | 116
ALP-EPC-00GNA-PI-ISO-0001 | Waste Water Treatment - Isometric Drawings | ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-11-15 | 181
ALP-EPC-00GNA-PI-ISO-0001 | Waste Water Treatment - Isometric Drawings | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-11-15 | 183
ALP-EPC-00GUA-PI-ISO-0001 | Sanitary Waste Water Treatment - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-12-08 | 133
ALP-EPC-00GUA-PI-ISO-0001 | Sanitary Waste Water Treatment - Isometric Drawings | ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-12-08 | 147
ALP-EPC-00GUA-PI-ISO-0001 | Sanitary Waste Water Treatment - Isometric Drawings | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-12-08 | 200
ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-09-07 | 67
ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-20 | 2027-09-07 | 12
ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-09-07 | 106
ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-09-07 | 101
ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-09-07 | 51
ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-09-07 | 34
ALP-EPC-00LDA-PI-ISO-0001 | Condensate Polishing - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-11-17 | 118
ALP-EPC-00LDA-PI-ISO-0001 | Condensate Polishing - Isometric Drawings | ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-11-17 | 157
ALP-EPC-00LDA-PI-ISO-0001 | Condensate Polishing - Isometric Drawings | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-11-17 | 185
ALP-EPC-00PAA-PI-ISO-0001 | CW Intake, Screens and Outfall - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-06-28 | 16
ALP-EPC-00PAA-PI-ISO-0001 | CW Intake, Screens and Outfall - Isometric Drawings | ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-28 | 81
ALP-EPC-00PAA-PI-ISO-0001 | CW Intake, Screens and Outfall - Isometric Drawings | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-06-28 | 31
ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-06-28 | 16
ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings | ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-28 | 55
ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-06-28 | 31
ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings | ALP-EPC-00PAB-PI-STR-0001 | CW Piping - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-06-14 | 2027-06-28 | 10
ALP-EPC-00PAC-PI-ISO-0001 | CW Pumps - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-06-28 | 16
ALP-EPC-00PAC-PI-ISO-0001 | CW Pumps - Isometric Drawings | ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-04-12 | 2027-06-28 | 55
ALP-EPC-00PAC-PI-ISO-0001 | CW Pumps - Isometric Drawings | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-06-28 | 31
ALP-EPC-00PAH-PI-ISO-0001 | Condenser Tube Cleaning - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-12-09 | 134
ALP-EPC-00PAH-PI-ISO-0001 | Condenser Tube Cleaning - Isometric Drawings | ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | EPC | IFR | IFC | NONE | 2027-04-13 | 2027-12-09 | 172
ALP-EPC-00PAH-PI-ISO-0001 | Condenser Tube Cleaning - Isometric Drawings | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-12-09 | 152
ALP-EPC-00PBA-PI-ISO-0001 | Electro-Chlorination - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-06-28 | 16
ALP-EPC-00PBA-PI-ISO-0001 | Electro-Chlorination - Isometric Drawings | ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-06-28 | 81
ALP-EPC-00PBA-PI-ISO-0001 | Electro-Chlorination - Isometric Drawings | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-06-28 | 31
ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-08-19 | 54
ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | EPC | IFR | IFC | NONE | 2027-02-12 | 2027-08-19 | 134
ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-08-19 | 88
ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-08-19 | 38
ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-19 | 21
ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-19 | 2027-08-19 | 0
ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-09-24 | 80
ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | EPC | IFR | IFC | NONE | 2027-03-05 | 2027-09-24 | 145
ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-09-24 | 114
ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-09-24 | 64
ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-09-24 | 47
ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-07-21 | 33
ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-07-21 | 97
ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-07-21 | 67
ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-07-21 | 17
ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-09-07 | 67
ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-09-07 | 119
ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-09-07 | 101
ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-09-07 | 51
ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-09-07 | 34
ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-19 | 2027-09-07 | 13
ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-10-13 | 93
ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-28 | 2027-10-13 | 120
ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-10-13 | 127
ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-10-13 | 77
ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-10-13 | 60
ALP-EPC-00QJB-PI-ISO-0001 | Hydrogen and CO2 Supply - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-11-18 | 119
ALP-EPC-00QJB-PI-ISO-0001 | Hydrogen and CO2 Supply - Isometric Drawings | ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-11-18 | 144
ALP-EPC-00QJB-PI-ISO-0001 | Hydrogen and CO2 Supply - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-11-18 | 136
ALP-EPC-00QUA-PI-ISO-0001 | Sampling and SWAS - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-07-20 | 32
ALP-EPC-00QUA-PI-ISO-0001 | Sampling and SWAS - Isometric Drawings | ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | EPC | IFR | IFC | NONE | 2027-05-06 | 2027-07-20 | 53
ALP-EPC-00QUA-PI-ISO-0001 | Sampling and SWAS - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-07-20 | 49
ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-08-18 | 53
ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-08-18 | 146
ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-08-18 | 87
ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-08-18 | 37
ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-18 | 20
ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-18 | 2027-08-18 | 0
ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-08-13 | 50
ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | EPC | IFR | IFC | NONE | 2027-01-26 | 2027-08-13 | 143
ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-08-13 | 84
ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-08-13 | 34
ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-13 | 17
ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-10-14 | 94
ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-10-14 | 109
ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-10-14 | 111
ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | ALP-EPC-10HAN-PI-STR-0001 | HRSG Blowdown and Drains - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-13 | 2027-10-14 | 44
ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-10-01 | 85
ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-10-01 | 119
ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-10-01 | 99
ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-10-01 | 69
ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-10-01 | 52
ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-08-26 | 59
ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-08-26 | 93
ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-23 | 2027-08-26 | 3
ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-08-26 | 72
ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-08-26 | 43
ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-26 | 26
ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-09-22 | 78
ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-09-22 | 112
ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-09-22 | 91
ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-09-22 | 62
ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-09-22 | 45
ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-19 | 2027-09-22 | 24
ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-11-24 | 123
ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings | ALP-EPC-10LAE-PI-STR-0001 | HP Attemperation Spray Water - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-10-29 | 2027-11-24 | 18
ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings | ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-17 | 2027-11-24 | 137
ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-11-24 | 140
ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-11-24 | 123
ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings | ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-11-24 | 136
ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-11-24 | 140
ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings | ALP-EPC-10LAF-PI-STR-0001 | Reheat Attemperation Spray Water - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-11-09 | 2027-11-24 | 11
ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-10-13 | 93
ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings | ALP-EPC-10LBA-PI-STR-0001 | Main Steam Piping - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-03 | 2027-10-13 | 51
ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings | ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-13 | 95
ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-10-13 | 110
ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-10-14 | 94
ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings | ALP-EPC-10LBB-PI-STR-0001 | Hot Reheat Piping - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-05 | 2027-10-14 | 50
ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings | ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-02 | 2027-10-14 | 96
ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-10-14 | 111
ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-10-14 | 94
ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings | ALP-EPC-10LBC-PI-STR-0001 | Cold Reheat Piping - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-13 | 2027-10-14 | 44
ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings | ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-03 | 2027-10-14 | 95
ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-10-14 | 111
ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-11-02 | 107
ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings | ALP-EPC-10LBD-PI-STR-0001 | LP Steam Piping - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-08-17 | 2027-11-02 | 55
ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings | ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-11-02 | 106
ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-11-02 | 124
ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2028-01-06 | 154
ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings | ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2028-01-06 | 167
ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2028-01-06 | 172
ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings | ALP-EPC-20LCA-PI-STR-0001 | Main Condensate Piping - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2028-01-06 | 2028-01-06 | 0
ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2028-01-05 | 153
ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings | ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | EPC | IFR | IFC | NONE | 2027-06-09 | 2028-01-05 | 150
ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2028-01-05 | 171
ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings | ALP-EPC-20LCB-PI-STR-0001 | Condensate Extraction Pumps - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2028-01-05 | 2028-01-05 | 0
ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings | ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-12-31 | 150
ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings | ALP-EPC-20MAN-PI-STR-0001 | Turbine Bypass Stations and Piping - Pipe Stress Analysis | EPC | IFR | IFC | NONE | 2027-12-31 | 2027-12-31 | 0
ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings | ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | EPC | IFR | IFC | NONE | 2027-05-18 | 2027-12-31 | 163
ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-12-31 | 168
ALP-EPC-00EGA-CM-MDB-0001 | LDO Unloading - System Turnover Dossier | ALP-EPC-00EGA-CM-CMP-0001 | LDO Unloading - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-13 | 2028-03-20 | 222
ALP-EPC-00EGA-CM-OMM-0001 | LDO Unloading - Operating Procedures | ALP-EPC-00EGA-CM-CMP-0001 | LDO Unloading - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-13 | 2027-05-13 | 0
ALP-EPC-00EGB-CM-MDB-0001 | LDO Storage - System Turnover Dossier | ALP-EPC-00EGB-CM-CMP-0001 | LDO Storage - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-25 | 2028-03-20 | 214
ALP-EPC-00EGB-CM-OMM-0001 | LDO Storage - Operating Procedures | ALP-EPC-00EGB-CM-CMP-0001 | LDO Storage - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-25 | 2027-05-25 | 0
ALP-EPC-00EGA-GE-RPT-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Bid Evaluation | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-17 | 33
ALP-EPC-00EGC-CM-MDB-0001 | LDO Forwarding and Treatment - System Turnover Dossier | ALP-EPC-00EGC-CM-CMP-0001 | LDO Forwarding and Treatment - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-18 | 2028-03-20 | 262
ALP-EPC-00EGC-CM-OMM-0001 | LDO Forwarding and Treatment - Operating Procedures | ALP-EPC-00EGC-CM-CMP-0001 | LDO Forwarding and Treatment - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-18 | 2027-03-18 | 0
ALP-EPC-00EKA-GE-RPT-0001 | Gas Receiving and Metering Station - Technical Bid Evaluation | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-17 | 33
ALP-EPC-00EKA-CM-MDB-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Turnover Dossier | ALP-EPC-00EKA-CM-CMP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-16 | 2028-03-20 | 264
ALP-EPC-00EKA-CM-OMM-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Operating Procedures | ALP-EPC-00EKA-CM-CMP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-16 | 2027-03-16 | 0
ALP-EPC-00EKC-CM-MDB-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Turnover Dossier | ALP-EPC-00EKC-CM-CMP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-28 | 2028-03-20 | 211
ALP-EPC-00EKC-CM-OMM-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Operating Procedures | ALP-EPC-00EKC-CM-CMP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-28 | 2027-05-28 | 0
ALP-EPC-00GBA-CM-MDB-0001 | Seawater Reverse Osmosis - System Turnover Dossier | ALP-EPC-00GBA-CM-CMP-0001 | Seawater Reverse Osmosis - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-20 | 2028-03-20 | 239
ALP-EPC-00GBA-CM-OMM-0001 | Seawater Reverse Osmosis - Operating Procedures | ALP-EPC-00GBA-CM-CMP-0001 | Seawater Reverse Osmosis - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-20 | 2027-04-20 | 0
ALP-EPC-00GCA-CM-MDB-0001 | Demineralisation - System Turnover Dossier | ALP-EPC-00GCA-CM-CMP-0001 | Demineralisation - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-28 | 2028-03-20 | 211
ALP-EPC-00GCA-CM-OMM-0001 | Demineralisation - Operating Procedures | ALP-EPC-00GCA-CM-CMP-0001 | Demineralisation - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-28 | 2027-05-28 | 0
ALP-EPC-00GHA-CM-MDB-0001 | Demineralised Water Storage and Distribution - System Turnover Dossier | ALP-EPC-00GHA-CM-CMP-0001 | Demineralised Water Storage and Distribution - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-31 | 2028-03-20 | 210
ALP-EPC-00GHA-CM-OMM-0001 | Demineralised Water Storage and Distribution - Operating Procedures | ALP-EPC-00GHA-CM-CMP-0001 | Demineralised Water Storage and Distribution - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-05-31 | 0
ALP-EPC-00GHA-GE-RPT-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Bid Evaluation | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-03 | 23
ALP-EPC-00GKA-CM-MDB-0001 | Potable Water - System Turnover Dossier | ALP-EPC-00GKA-CM-CMP-0001 | Potable Water - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-07-05 | 2028-03-20 | 185
ALP-EPC-00GKA-CM-OMM-0001 | Potable Water - Operating Procedures | ALP-EPC-00GKA-CM-CMP-0001 | Potable Water - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-07-05 | 2027-07-05 | 0
ALP-EPC-00GMA-CM-MDB-0001 | Process Drains and Waste Water Collection - System Turnover Dossier | ALP-EPC-00GMA-CM-CMP-0001 | Process Drains and Waste Water Collection - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-22 | 2028-04-03 | 247
ALP-EPC-00GMA-CM-OMM-0001 | Process Drains and Waste Water Collection - Operating Procedures | ALP-EPC-00GMA-CM-CMP-0001 | Process Drains and Waste Water Collection - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-22 | 2027-04-22 | 0
ALP-EPC-00GNA-CM-MDB-0001 | Waste Water Treatment - System Turnover Dossier | ALP-EPC-00GNA-CM-CMP-0001 | Waste Water Treatment - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-23 | 2028-04-03 | 246
ALP-EPC-00GNA-CM-OMM-0001 | Waste Water Treatment - Operating Procedures | ALP-EPC-00GNA-CM-CMP-0001 | Waste Water Treatment - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-04-23 | 0
ALP-EPC-00GNA-GE-RPT-0001 | Waste Water and Sanitary Treatment Packages - Technical Bid Evaluation | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-07 | 48
ALP-EPC-00GUA-CM-MDB-0001 | Sanitary Waste Water Treatment - System Turnover Dossier | ALP-EPC-00GUA-CM-CMP-0001 | Sanitary Waste Water Treatment - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-07-05 | 2028-04-03 | 195
ALP-EPC-00GUA-CM-OMM-0001 | Sanitary Waste Water Treatment - Operating Procedures | ALP-EPC-00GUA-CM-CMP-0001 | Sanitary Waste Water Treatment - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-07-05 | 2027-07-05 | 0
ALP-EPC-00LBG-CM-MDB-0001 | Auxiliary Steam - System Turnover Dossier | ALP-EPC-00LBG-CM-CMP-0001 | Auxiliary Steam - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-08-24 | 2028-05-22 | 194
ALP-EPC-00LBG-CM-OMM-0001 | Auxiliary Steam - Operating Procedures | ALP-EPC-00LBG-CM-CMP-0001 | Auxiliary Steam - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-08-24 | 2027-09-01 | 6
ALP-EPC-00GBA-GE-RPT-0001 | Water Treatment Package - Technical Bid Evaluation | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-24 | 38
ALP-EPC-00LDA-CM-MDB-0001 | Condensate Polishing - System Turnover Dossier | ALP-EPC-00LDA-CM-CMP-0001 | Condensate Polishing - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-31 | 2028-04-03 | 220
ALP-EPC-00LDA-CM-OMM-0001 | Condensate Polishing - Operating Procedures | ALP-EPC-00LDA-CM-CMP-0001 | Condensate Polishing - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-05-31 | 0
ALP-EPC-00PAA-GE-RPT-0001 | Travelling Band Screens and Trash Rakes - Technical Bid Evaluation | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-22 | 59
ALP-EPC-00PAA-CM-MDB-0001 | CW Intake, Screens and Outfall - System Turnover Dossier | ALP-EPC-00PAA-CM-CMP-0001 | CW Intake, Screens and Outfall - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-23 | 2028-04-03 | 246
ALP-EPC-00PAA-CM-OMM-0001 | CW Intake, Screens and Outfall - Operating Procedures | ALP-EPC-00PAA-CM-CMP-0001 | CW Intake, Screens and Outfall - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-04-23 | 0
ALP-EPC-00PAB-GE-RPT-0001 | GRP CW Pipes and Fittings - Technical Bid Evaluation | ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-10 | 28
ALP-EPC-00PAB-CM-MDB-0001 | CW Piping - System Turnover Dossier | ALP-EPC-00PAB-CM-CMP-0001 | CW Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-31 | 2028-04-03 | 220
ALP-EPC-00PAB-CM-OMM-0001 | CW Piping - Operating Procedures | ALP-EPC-00PAB-CM-CMP-0001 | CW Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-05-31 | 0
ALP-EPC-00PAC-GE-RPT-0001 | CW Pumps - Technical Bid Evaluation | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-17 | 33
ALP-EPC-00PAC-CM-MDB-0001 | CW Pumps - System Turnover Dossier | ALP-EPC-00PAC-CM-CMP-0001 | CW Pumps - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-31 | 2028-04-03 | 220
ALP-EPC-00PAC-CM-OMM-0001 | CW Pumps - Operating Procedures | ALP-EPC-00PAC-CM-CMP-0001 | CW Pumps - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-05-31 | 0
ALP-EPC-00PAH-GE-RPT-0001 | Condenser Tube Cleaning System - Technical Bid Evaluation | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-24 | 82
ALP-EPC-00PAH-CM-MDB-0001 | Condenser Tube Cleaning - System Turnover Dossier | ALP-EPC-00PAH-CM-CMP-0001 | Condenser Tube Cleaning - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-06-01 | 2028-04-03 | 219
ALP-EPC-00PAH-CM-OMM-0001 | Condenser Tube Cleaning - Operating Procedures | ALP-EPC-00PAH-CM-CMP-0001 | Condenser Tube Cleaning - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-06-01 | 2027-06-01 | 0
ALP-EPC-00PBA-GE-RPT-0001 | Electro-Chlorination Package - Technical Bid Evaluation | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-EPC-00PBA-CM-MDB-0001 | Electro-Chlorination - System Turnover Dossier | ALP-EPC-00PBA-CM-CMP-0001 | Electro-Chlorination - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-23 | 2028-04-03 | 246
ALP-EPC-00PBA-CM-OMM-0001 | Electro-Chlorination - Operating Procedures | ALP-EPC-00PBA-CM-CMP-0001 | Electro-Chlorination - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-04-23 | 0
ALP-EPC-00PGA-GE-RPT-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Bid Evaluation | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-EPC-00PGA-CM-MDB-0001 | Closed Cooling Water - System Turnover Dossier | ALP-EPC-00PGA-CM-CMP-0001 | Closed Cooling Water - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-05 | 2028-04-03 | 260
ALP-EPC-00PGA-CM-OMM-0001 | Closed Cooling Water - Operating Procedures | ALP-EPC-00PGA-CM-CMP-0001 | Closed Cooling Water - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-05 | 2027-04-05 | 0
ALP-EPC-00QCA-GE-RPT-0001 | Chemical Dosing Skid - Technical Bid Evaluation | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-04-21 | 18
ALP-EPC-00QCA-CM-MDB-0001 | Chemical Dosing - System Turnover Dossier | ALP-EPC-00QCA-CM-CMP-0001 | Chemical Dosing - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-23 | 2028-04-03 | 246
ALP-EPC-00QCA-CM-OMM-0001 | Chemical Dosing - Operating Procedures | ALP-EPC-00QCA-CM-CMP-0001 | Chemical Dosing - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-23 | 2027-04-23 | 0
ALP-EPC-00QEA-GE-RPT-0001 | Air Compressors and Dryers - Technical Bid Evaluation | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-EPC-00QEA-CM-MDB-0001 | Compressed Air - System Turnover Dossier | ALP-EPC-00QEA-CM-CMP-0001 | Compressed Air - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-26 | 2028-04-03 | 245
ALP-EPC-00QEA-CM-OMM-0001 | Compressed Air - Operating Procedures | ALP-EPC-00QEA-CM-CMP-0001 | Compressed Air - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-04-26 | 2027-04-26 | 0
ALP-EPC-00QHA-GE-RPT-0001 | Auxiliary Boiler - Technical Bid Evaluation | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-17 | 33
ALP-EPC-00QHA-CM-MDB-0001 | Auxiliary Boiler - System Turnover Dossier | ALP-EPC-00QHA-CM-CMP-0001 | Auxiliary Boiler - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-13 | 2028-04-03 | 232
ALP-EPC-00QHA-CM-OMM-0001 | Auxiliary Boiler - Operating Procedures | ALP-EPC-00QHA-CM-CMP-0001 | Auxiliary Boiler - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-05-13 | 2027-06-25 | 31
ALP-EPC-00QJA-CM-MDB-0001 | Nitrogen Supply - System Turnover Dossier | ALP-EPC-00QJA-CM-CMP-0001 | Nitrogen Supply - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-06-16 | 2028-04-03 | 208
ALP-EPC-00QJA-CM-OMM-0001 | Nitrogen Supply - Operating Procedures | ALP-EPC-00QJA-CM-CMP-0001 | Nitrogen Supply - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-06-16 | 2027-06-25 | 7
ALP-EPC-00QJA-GE-RPT-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Bid Evaluation | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-04-27 | 23
ALP-EPC-00QJB-CM-MDB-0001 | Hydrogen and CO2 Supply - System Turnover Dossier | ALP-EPC-00QJB-CM-CMP-0001 | Hydrogen and CO2 Supply - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-06-18 | 2028-04-17 | 216
ALP-EPC-00QJB-CM-OMM-0001 | Hydrogen and CO2 Supply - Operating Procedures | ALP-EPC-00QJB-CM-CMP-0001 | Hydrogen and CO2 Supply - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-06-18 | 2027-06-25 | 5
ALP-EPC-00QUA-GE-RPT-0001 | Steam/Water Analysis System - Technical Bid Evaluation | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-02 | 86
ALP-EPC-00QUA-CM-MDB-0001 | Sampling and SWAS - System Turnover Dossier | ALP-EPC-00QUA-CM-CMP-0001 | Sampling and SWAS - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-06-25 | 2028-04-17 | 211
ALP-EPC-00QUA-CM-OMM-0001 | Sampling and SWAS - Operating Procedures | ALP-EPC-00QUA-CM-CMP-0001 | Sampling and SWAS - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-06-25 | 2027-06-29 | 2
ALP-EPC-00SAA-CM-MDB-0001 | HVAC - System Turnover Dossier | ALP-EPC-00SAA-CM-CMP-0001 | HVAC - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-24 | 2028-04-17 | 278
ALP-EPC-00SAA-CM-OMM-0001 | HVAC - Operating Procedures | ALP-EPC-00SAA-CM-CMP-0001 | HVAC - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-03-24 | 0
ALP-EPC-00SAA-GE-RPT-0001 | HVAC Plant and Equipment - Technical Bid Evaluation | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-07 | 48
ALP-EPC-00000-CM-TRP-0007 | Fire Protection System Test Certificates | ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-17 | 2028-07-04 | 339
ALP-EPC-00SGA-CM-MDB-0001 | Fire Water System - System Turnover Dossier | ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-17 | 2028-04-17 | 283
ALP-EPC-00SGA-CM-OMM-0001 | Fire Water System - Operating Procedures | ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-03-17 | 0
ALP-EPC-00EGB-GE-RPT-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Bid Evaluation | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-04 | 73
ALP-EPC-00SGA-GE-RPT-0001 | Fire Pumps and Fire Protection Systems - Technical Bid Evaluation | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-07 | 48
ALP-EPC-00SGC-CM-MDB-0001 | Deluge, Spray and Foam Systems - System Turnover Dossier | ALP-EPC-00SGC-CM-CMP-0001 | Deluge, Spray and Foam Systems - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-17 | 2028-04-17 | 283
ALP-EPC-00SGC-CM-OMM-0001 | Deluge, Spray and Foam Systems - Operating Procedures | ALP-EPC-00SGC-CM-CMP-0001 | Deluge, Spray and Foam Systems - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-03-17 | 0
ALP-EPC-10HAN-GE-RPT-0001 | HRSG Blowdown and Drain Tanks - Technical Bid Evaluation | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-03 | 23
ALP-EPC-10HAN-CM-MDB-0001 | HRSG Blowdown and Drains - System Turnover Dossier | ALP-EPC-10HAN-CM-CMP-0001 | HRSG Blowdown and Drains - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-01 | 2028-05-22 | 188
ALP-EPC-10HAN-CM-OMM-0001 | HRSG Blowdown and Drains - Operating Procedures | ALP-EPC-10HAN-CM-CMP-0001 | HRSG Blowdown and Drains - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-01 | 2027-09-01 | 0
ALP-EPC-10HSB-GE-RPT-0001 | Aqueous Ammonia Storage and Forwarding - Technical Bid Evaluation | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-EPC-00000-EL-LST-0004 | Hazardous Area Electrical Equipment Register | ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | EPC | IFR | IFC | NONE | 2027-07-20 | 2027-09-08 | 36
ALP-EPC-00000-HS-RPT-0005 | Explosion Protection Document | ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | EPC | IFR | IFC | NONE | 2027-07-20 | 2027-08-04 | 11
ALP-EPC-00000-HS-STU-0003 | Fire and Gas Detector Mapping Study | ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | EPC | IFR | IFC | NONE | 2027-07-20 | 2027-08-10 | 15
ALP-EPC-00000-HS-STU-0003 | Fire and Gas Detector Mapping Study | ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | EPC | IFR | IFC | NONE | 2027-01-22 | 2027-08-10 | 142
ALP-EPC-00000-HS-PLN-0005 | Emergency Response Plan | ALP-EPC-00000-HS-HAZ-0010 | Major Accident Assessment and QRA | EPC | IFR | IFC | NONE | 2027-08-17 | 2027-08-17 | 0
ALP-EPC-10HSB-CM-MDB-0001 | Ammonia Storage and Supply - System Turnover Dossier | ALP-EPC-10HSB-CM-CMP-0001 | Ammonia Storage and Supply - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-07-05 | 2028-04-17 | 205
ALP-EPC-10HSB-CM-OMM-0001 | Ammonia Storage and Supply - Operating Procedures | ALP-EPC-10HSB-CM-CMP-0001 | Ammonia Storage and Supply - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-07-05 | 2027-07-06 | 1
ALP-EPC-10LAB-CM-MDB-0001 | Feedwater Piping - System Turnover Dossier | ALP-EPC-10LAB-CM-CMP-0001 | Feedwater Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-01 | 2028-05-22 | 188
ALP-EPC-10LAB-CM-OMM-0001 | Feedwater Piping - Operating Procedures | ALP-EPC-10LAB-CM-CMP-0001 | Feedwater Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-01 | 2027-09-03 | 2
ALP-EPC-10LAC-GE-RPT-0001 | Boiler Feed Pumps - Technical Bid Evaluation | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-17 | 33
ALP-EPC-10LAC-CM-MDB-0001 | Boiler Feed Pumps - System Turnover Dossier | ALP-EPC-10LAC-CM-CMP-0001 | Boiler Feed Pumps - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-03 | 2028-05-22 | 186
ALP-EPC-10LAC-CM-OMM-0001 | Boiler Feed Pumps - Operating Procedures | ALP-EPC-10LAC-CM-CMP-0001 | Boiler Feed Pumps - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-03 | 2027-09-03 | 0
ALP-EPC-10LAE-CM-MDB-0001 | HP Attemperation Spray Water - System Turnover Dossier | ALP-EPC-10LAE-CM-CMP-0001 | HP Attemperation Spray Water - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-03 | 2028-05-22 | 186
ALP-EPC-10LAE-CM-OMM-0001 | HP Attemperation Spray Water - Operating Procedures | ALP-EPC-10LAE-CM-CMP-0001 | HP Attemperation Spray Water - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-03 | 2027-09-03 | 0
ALP-EPC-10LAF-CM-MDB-0001 | Reheat Attemperation Spray Water - System Turnover Dossier | ALP-EPC-10LAF-CM-CMP-0001 | Reheat Attemperation Spray Water - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-03 | 2028-05-22 | 186
ALP-EPC-10LAF-CM-OMM-0001 | Reheat Attemperation Spray Water - Operating Procedures | ALP-EPC-10LAF-CM-CMP-0001 | Reheat Attemperation Spray Water - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-03 | 2027-09-03 | 0
ALP-EPC-10LBA-CM-MDB-0001 | Main Steam Piping - System Turnover Dossier | ALP-EPC-10LBA-CM-CMP-0001 | Main Steam Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-13 | 2028-05-22 | 180
ALP-EPC-10LBA-CM-OMM-0001 | Main Steam Piping - Operating Procedures | ALP-EPC-10LBA-CM-CMP-0001 | Main Steam Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-13 | 2027-09-13 | 0
ALP-EPC-10LBB-CM-MDB-0001 | Hot Reheat Piping - System Turnover Dossier | ALP-EPC-10LBB-CM-CMP-0001 | Hot Reheat Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-14 | 2028-05-22 | 179
ALP-EPC-10LBB-CM-OMM-0001 | Hot Reheat Piping - Operating Procedures | ALP-EPC-10LBB-CM-CMP-0001 | Hot Reheat Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-14 | 2027-09-14 | 0
ALP-EPC-10LBC-CM-MDB-0001 | Cold Reheat Piping - System Turnover Dossier | ALP-EPC-10LBC-CM-CMP-0001 | Cold Reheat Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-14 | 2028-05-22 | 179
ALP-EPC-10LBC-CM-OMM-0001 | Cold Reheat Piping - Operating Procedures | ALP-EPC-10LBC-CM-CMP-0001 | Cold Reheat Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-14 | 2027-09-14 | 0
ALP-P02-10LBA-ME-DSH-0001 | Alloy Piping P91 / P22 - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-PI-MRQ-0002 | Alloy Piping P91 / P22 - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-02-25 | 58
ALP-P02-10LBA-ME-ITP-0001 | Alloy Piping P91 / P22 - Supplier Inspection and Test Plan | ALP-EPC-00000-PI-MRQ-0002 | Alloy Piping P91 / P22 - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-02-25 | 58
ALP-P02-10LBA-ME-MDB-0001 | Alloy Piping P91 / P22 - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-PI-MRQ-0002 | Alloy Piping P91 / P22 - Material Requisition | EPC | IFR | IFC | NONE | 2026-12-07 | 2027-10-21 | 228
ALP-EPC-10LBD-CM-MDB-0001 | LP Steam Piping - System Turnover Dossier | ALP-EPC-10LBD-CM-CMP-0001 | LP Steam Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-16 | 2028-05-22 | 177
ALP-EPC-10LBD-CM-OMM-0001 | LP Steam Piping - Operating Procedures | ALP-EPC-10LBD-CM-CMP-0001 | LP Steam Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-16 | 2027-09-16 | 0
ALP-EPC-20LCA-CM-MDB-0001 | Main Condensate Piping - System Turnover Dossier | ALP-EPC-20LCA-CM-CMP-0001 | Main Condensate Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-16 | 2028-05-22 | 177
ALP-EPC-20LCA-CM-OMM-0001 | Main Condensate Piping - Operating Procedures | ALP-EPC-20LCA-CM-CMP-0001 | Main Condensate Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-16 | 2027-09-16 | 0
ALP-EPC-20LCB-GE-RPT-0001 | Condensate Extraction Pumps - Technical Bid Evaluation | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-EPC-20LCB-CM-MDB-0001 | Condensate Extraction Pumps - System Turnover Dossier | ALP-EPC-20LCB-CM-CMP-0001 | Condensate Extraction Pumps - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-21 | 2028-05-22 | 174
ALP-EPC-20LCB-CM-OMM-0001 | Condensate Extraction Pumps - Operating Procedures | ALP-EPC-20LCB-CM-CMP-0001 | Condensate Extraction Pumps - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-21 | 2027-09-21 | 0
ALP-EPC-00000-IC-LST-0003 | Interlock and Trip List | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-08-11 | 5
ALP-EPC-00000-IC-SPC-0006 | BOP SIS - Safety Requirements Specification | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00EGA-IC-CEM-0001 | LDO Unloading - Cause and Effect Matrix | ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-15 | 2027-08-20 | 91
ALP-EPC-00EGA-IC-CEM-0001 | LDO Unloading - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-08-20 | 12
ALP-EPC-00EGB-IC-CEM-0001 | LDO Storage - Cause and Effect Matrix | ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-27 | 2027-09-01 | 91
ALP-EPC-00EGB-IC-CEM-0001 | LDO Storage - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00EGC-IC-CEM-0001 | LDO Forwarding and Treatment - Cause and Effect Matrix | ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-09-01 | 139
ALP-EPC-00EGC-IC-CEM-0001 | LDO Forwarding and Treatment - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00EKA-IC-CEM-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Cause and Effect Matrix | ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-16 | 2027-09-01 | 141
ALP-EPC-00EKA-IC-CEM-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00EKC-IC-CEM-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Cause and Effect Matrix | ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-30 | 2027-08-10 | 72
ALP-EPC-00EKC-IC-CEM-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-08-10 | 4
ALP-EPC-00LBG-IC-CEM-0001 | Auxiliary Steam - Cause and Effect Matrix | ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-03 | 2027-09-01 | 87
ALP-EPC-00LBG-IC-CEM-0001 | Auxiliary Steam - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00QCA-IC-CEM-0001 | Chemical Dosing - Cause and Effect Matrix | ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-09-01 | 113
ALP-EPC-00QCA-IC-CEM-0001 | Chemical Dosing - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00QEA-IC-CEM-0001 | Compressed Air - Cause and Effect Matrix | ALP-EPC-00QEA-IC-CNR-0001 | Compressed Air - Control Narrative | EPC | IFR | IFC | NONE | 2027-03-29 | 2027-09-01 | 112
ALP-EPC-00QEA-IC-CEM-0001 | Compressed Air - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00QHA-IC-CEM-0001 | Auxiliary Boiler - Cause and Effect Matrix | ALP-EPC-00QHA-IC-CNR-0001 | Auxiliary Boiler - Control Narrative | EPC | IFR | IFC | NONE | 2027-04-15 | 2027-09-01 | 99
ALP-EPC-00QHA-IC-CEM-0001 | Auxiliary Boiler - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00QJA-IC-CEM-0001 | Nitrogen Supply - Cause and Effect Matrix | ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-19 | 2027-09-01 | 75
ALP-EPC-00QJA-IC-CEM-0001 | Nitrogen Supply - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00QJB-IC-CEM-0001 | Hydrogen and CO2 Supply - Cause and Effect Matrix | ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-21 | 2027-09-01 | 73
ALP-EPC-00QJB-IC-CEM-0001 | Hydrogen and CO2 Supply - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00QUA-IC-CEM-0001 | Sampling and SWAS - Cause and Effect Matrix | ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative | EPC | IFR | IFC | NONE | 2027-05-28 | 2027-09-01 | 68
ALP-EPC-00QUA-IC-CEM-0001 | Sampling and SWAS - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-01 | 20
ALP-EPC-00SGA-IC-CEM-0001 | Fire Water System - Cause and Effect Matrix | ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-09-02 | 141
ALP-EPC-00SGA-IC-CEM-0001 | Fire Water System - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-02 | 21
ALP-EPC-00SGC-IC-CEM-0001 | Deluge, Spray and Foam Systems - Cause and Effect Matrix | ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative | EPC | IFR | IFC | NONE | 2027-02-17 | 2027-09-13 | 148
ALP-EPC-00SGC-IC-CEM-0001 | Deluge, Spray and Foam Systems - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-13 | 28
ALP-EPC-10HAN-IC-CEM-0001 | HRSG Blowdown and Drains - Cause and Effect Matrix | ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-04 | 2027-09-02 | 64
ALP-EPC-10HAN-IC-CEM-0001 | HRSG Blowdown and Drains - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-02 | 21
ALP-EPC-10HSB-IC-CEM-0001 | Ammonia Storage and Supply - Cause and Effect Matrix | ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-09-23 | 78
ALP-EPC-10HSB-IC-CEM-0001 | Ammonia Storage and Supply - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-23 | 36
ALP-EPC-10LAB-IC-CEM-0001 | Feedwater Piping - Cause and Effect Matrix | ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-09-23 | 77
ALP-EPC-10LAB-IC-CEM-0001 | Feedwater Piping - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-23 | 36
ALP-EPC-10LAC-IC-CEM-0001 | Boiler Feed Pumps - Cause and Effect Matrix | ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-09 | 2027-09-28 | 79
ALP-EPC-10LAC-IC-CEM-0001 | Boiler Feed Pumps - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-09-28 | 39
ALP-EPC-10LAE-IC-CEM-0001 | HP Attemperation Spray Water - Cause and Effect Matrix | ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-07 | 2027-10-05 | 86
ALP-EPC-10LAE-IC-CEM-0001 | HP Attemperation Spray Water - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-05 | 44
ALP-EPC-10LAF-IC-CEM-0001 | Reheat Attemperation Spray Water - Cause and Effect Matrix | ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-10-07 | 87
ALP-EPC-10LAF-IC-CEM-0001 | Reheat Attemperation Spray Water - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-07 | 46
ALP-EPC-10LBA-IC-CEM-0001 | Main Steam Piping - Cause and Effect Matrix | ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-10-08 | 77
ALP-EPC-10LBA-IC-CEM-0001 | Main Steam Piping - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-08 | 47
ALP-EPC-10LBB-IC-CEM-0001 | Hot Reheat Piping - Cause and Effect Matrix | ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-10-11 | 78
ALP-EPC-10LBB-IC-CEM-0001 | Hot Reheat Piping - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-11 | 48
ALP-EPC-10LBC-IC-CEM-0001 | Cold Reheat Piping - Cause and Effect Matrix | ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-24 | 2027-10-12 | 78
ALP-EPC-10LBC-IC-CEM-0001 | Cold Reheat Piping - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-12 | 49
ALP-EPC-10LBD-IC-CEM-0001 | LP Steam Piping - Cause and Effect Matrix | ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-10-15 | 79
ALP-EPC-10LBD-IC-CEM-0001 | LP Steam Piping - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-15 | 52
ALP-EPC-20LCA-IC-CEM-0001 | Main Condensate Piping - Cause and Effect Matrix | ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-10-19 | 95
ALP-EPC-20LCA-IC-CEM-0001 | Main Condensate Piping - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-19 | 54
ALP-EPC-20LCB-IC-CEM-0001 | Condensate Extraction Pumps - Cause and Effect Matrix | ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-10-22 | 82
ALP-EPC-20LCB-IC-CEM-0001 | Condensate Extraction Pumps - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-22 | 57
ALP-EPC-20MAN-IC-CEM-0001 | Turbine Bypass Stations and Piping - Cause and Effect Matrix | ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative | EPC | IFR | IFC | NONE | 2027-06-08 | 2027-10-28 | 102
ALP-EPC-20MAN-IC-CEM-0001 | Turbine Bypass Stations and Piping - Cause and Effect Matrix | ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-10-28 | 61
ALP-EPC-00000-EL-BLK-0001 | Cable Block Diagrams, Part 1 of 2 | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-09 | 223
ALP-EPC-00000-EL-BLK-0001 | Cable Block Diagrams, Part 1 of 2 | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-09-09 | 36
ALP-EPC-00000-EL-BLK-0002 | Cable Block Diagrams, Part 2 of 2 | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-21 | 231
ALP-EPC-00000-EL-BLK-0002 | Cable Block Diagrams, Part 2 of 2 | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-09-21 | 44
ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2026-11-02 | -187
ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification | ALP-EPC-00CJA-IC-BLK-0001 | Plant DCS - System Architecture | EPC | IFR | IFC | NONE | 2027-02-01 | 2026-11-02 | -65
ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UAC-IC-LOP-0002 | 380 kV GIS Switchyard - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UAC-IC-LOP-0002 | 380 kV GIS Switchyard - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-00UBA-IC-LOP-0002 | Electrical Building and Emergency Power - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UBA-IC-LOP-0002 | Electrical Building and Emergency Power - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-00UCA-IC-LOP-0001 | Control, Administration and Workshop Buildings - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UCA-IC-LOP-0001 | Control, Administration and Workshop Buildings - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-00UEG-IC-LOP-0001 | LDO Tank Farm and Unloading - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UEG-IC-LOP-0001 | LDO Tank Farm and Unloading - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-00UEK-IC-LOP-0001 | Fuel Gas Station - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UEK-IC-LOP-0001 | Fuel Gas Station - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-00UGA-IC-LOP-0001 | Water Treatment and Effluents - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-28 | 5
ALP-EPC-00UGA-IC-LOP-0001 | Water Treatment and Effluents - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-28 | 20
ALP-EPC-00UPC-IC-LOP-0001 | CW Pump House and Onshore CW - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UPC-IC-LOP-0001 | CW Pump House and Onshore CW - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-00UQA-IC-LOP-0001 | BOP Utilities - Loop and Connection Diagrams, Part 1 of 2 | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UQA-IC-LOP-0001 | BOP Utilities - Loop and Connection Diagrams, Part 1 of 2 | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-00UQA-IC-LOP-0003 | BOP Utilities - Loop and Connection Diagrams, Part 2 of 2 | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UQA-IC-LOP-0003 | BOP Utilities - Loop and Connection Diagrams, Part 2 of 2 | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-00UZA-IC-LOP-0002 | Site-Wide Infrastructure - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UZA-IC-LOP-0002 | Site-Wide Infrastructure - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-10UMA-IC-LOP-0001 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 1 of 2 | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-10UMA-IC-LOP-0001 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 1 of 2 | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-10UMA-IC-LOP-0001 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 1 of 2 | ALP-IEC-10MBY-IC-CBL-0001 | Power Island Cable List | IEC | IFR | ACCEPTED | NONE | 2027-05-31 | 2027-07-21 | 37
ALP-EPC-10UMA-IC-LOP-0001 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 1 of 2 | ALP-IEC-10MBY-IC-IOL-0001 | Turbine Control System - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IFR | ACCEPTED | NONE | 2027-02-22 | 2027-07-21 | 107
ALP-EPC-10UMA-IC-LOP-0003 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 2 of 2 | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-10UMA-IC-LOP-0003 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 2 of 2 | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-07-21 | 15
ALP-EPC-20UMB-IC-LOP-0001 | Power Block - ST and Condenser - Loop and Connection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-09 | 13
ALP-EPC-20UMB-IC-LOP-0001 | Power Block - ST and Condenser - Loop and Connection Diagrams | ALP-EPC-00000-IC-LST-0001 | Instrument Index | EPC | IFR | IFC | NONE | 2027-06-30 | 2027-08-09 | 28
ALP-EPC-20UMB-IC-LOP-0001 | Power Block - ST and Condenser - Loop and Connection Diagrams | ALP-IEC-10MBY-IC-CBL-0001 | Power Island Cable List | IEC | IFR | ACCEPTED | NONE | 2027-05-31 | 2027-08-09 | 50
ALP-EPC-20UMB-IC-LOP-0001 | Power Block - ST and Condenser - Loop and Connection Diagrams | ALP-IEC-10MBY-IC-IOL-0001 | Turbine Control System - Supplier I/O List, Control Philosophy and Interface Signals | IEC | IFR | ACCEPTED | NONE | 2027-02-22 | 2027-08-09 | 120
ALP-EPC-00UAC-IC-LOP-0001 | 380 kV GIS Switchyard - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UAC-IC-ELY-0002 | 380 kV GIS Switchyard - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-07-28 | 2027-07-28 | 0
ALP-EPC-00UAC-IC-LOP-0001 | 380 kV GIS Switchyard - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-28 | 5
ALP-EPC-00UBA-IC-LOP-0001 | Electrical Building and Emergency Power - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UBA-IC-ELY-0002 | Electrical Building and Emergency Power - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-03 | 2027-08-03 | 0
ALP-EPC-00UBA-IC-LOP-0001 | Electrical Building and Emergency Power - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-03 | 9
ALP-EPC-00UCA-IC-LOP-0002 | Control, Administration and Workshop Buildings - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UCA-IC-ELY-0001 | Control, Administration and Workshop Buildings - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-02 | 2027-08-02 | 0
ALP-EPC-00UCA-IC-LOP-0002 | Control, Administration and Workshop Buildings - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-02 | 8
ALP-EPC-00UEG-IC-LOP-0002 | LDO Tank Farm and Unloading - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UEG-IC-ELY-0001 | LDO Tank Farm and Unloading - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-02 | 2027-08-02 | 0
ALP-EPC-00UEG-IC-LOP-0002 | LDO Tank Farm and Unloading - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-02 | 8
ALP-EPC-00UEK-IC-LOP-0002 | Fuel Gas Station - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UEK-IC-ELY-0001 | Fuel Gas Station - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-02 | 2027-08-02 | 0
ALP-EPC-00UEK-IC-LOP-0002 | Fuel Gas Station - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-02 | 8
ALP-EPC-00UGA-IC-LOP-0002 | Water Treatment and Effluents - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UGA-IC-ELY-0001 | Water Treatment and Effluents - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-04 | 2027-08-04 | 0
ALP-EPC-00UGA-IC-LOP-0002 | Water Treatment and Effluents - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-04 | 10
ALP-EPC-00UPC-IC-LOP-0002 | CW Pump House and Onshore CW - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UPC-IC-ELY-0001 | CW Pump House and Onshore CW - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-02 | 2027-08-02 | 0
ALP-EPC-00UPC-IC-LOP-0002 | CW Pump House and Onshore CW - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-02 | 8
ALP-EPC-00UQA-IC-LOP-0002 | BOP Utilities - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UQA-IC-ELY-0001 | BOP Utilities - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-16 | 2027-08-16 | 0
ALP-EPC-00UQA-IC-LOP-0002 | BOP Utilities - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-16 | 18
ALP-EPC-00UZA-IC-LOP-0001 | Site-Wide Infrastructure - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00UZA-IC-ELY-0001 | Site-Wide Infrastructure - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-07-28 | 2027-07-28 | 0
ALP-EPC-00UZA-IC-LOP-0001 | Site-Wide Infrastructure - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-28 | 5
ALP-EPC-10UMA-IC-LOP-0002 | Power Block - GT and HRSG - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-10UMA-IC-ELY-0001 | Power Block - GT and HRSG - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-11 | 2027-08-11 | 0
ALP-EPC-10UMA-IC-LOP-0002 | Power Block - GT and HRSG - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-11 | 15
ALP-EPC-20UMB-IC-LOP-0002 | Power Block - ST and Condenser - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-20UMB-IC-ELY-0001 | Power Block - ST and Condenser - Instrument Location and I&C Cable Routing | EPC | IFR | IFC | NONE | 2027-08-02 | 2027-08-10 | 6
ALP-EPC-20UMB-IC-LOP-0002 | Power Block - ST and Condenser - Junction Box and Cabinet Interconnection Diagrams | ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-08-10 | 14
ALP-EPC-20MAN-CM-MDB-0001 | Turbine Bypass Stations and Piping - System Turnover Dossier | ALP-EPC-20MAN-CM-CMP-0001 | Turbine Bypass Stations and Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-29 | 2028-06-05 | 178
ALP-EPC-20MAN-CM-OMM-0001 | Turbine Bypass Stations and Piping - Operating Procedures | ALP-EPC-20MAN-CM-CMP-0001 | Turbine Bypass Stations and Piping - System Commissioning Procedure | EPC | IFR | IFC | NONE | 2027-09-29 | 2027-09-29 | 0
ALP-EPC-00000-EL-TRP-0001 | Revenue Metering and TSO SCADA Interface Test Report | ALP-EPC-00000-EL-SPC-0003 | Revenue Metering and TSO SCADA Interface Specification | EPC | IFR | IFC | NONE | 2027-09-24 | 2028-07-04 | 202
ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | ALP-EPC-00000-EL-STU-0001 | Load Flow, Short-Circuit and Motor Starting Study | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00000-EL-STU-0002 | Protection Coordination Study and Relay Settings | ALP-EPC-00000-EL-STU-0001 | Load Flow, Short-Circuit and Motor Starting Study | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification | ALP-EPC-00000-EL-STU-0005 | Insulation Coordination Study | EPC | IFR | IFC | NONE | 2026-12-07 | 2026-11-02 | -25
ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification | ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CM-CMP-0003 | Grid Code Compliance Test Programme | ALP-EPC-00000-EL-STU-0006 | Grid Code Compliance and Reactive Capability Study | EPC | IFR | IFC | NONE | 2027-09-29 | 2027-09-29 | 0
ALP-EPC-00000-CM-CMP-0003 | Grid Code Compliance Test Programme | ALP-IEC-10MKA-EL-RPT-0001 | Generator Capability Curves and Dynamic Models | IEC | IFR | ACCEPTED | NONE | 2027-01-25 | 2027-09-29 | 177
ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | ALP-EPC-00000-GE-SPC-0002 | Electrical and I&C Installation - Technical Specification | EPC | IFR | IFC | NONE | 2026-12-11 | 2026-12-11 | 0
ALP-EPC-00BBA-EL-DSH-0001 | MV Switchgear 10.5 kV - Datasheet | ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BBA-EL-DSH-0001 | MV Switchgear 10.5 kV - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BBA-EL-ITP-0001 | MV Switchgear 10.5 kV - Inspection and Test Plan | ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-WIR-0001 | LV Schematic and Wiring Diagrams, Part 1 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-03-08 | 16
ALP-EPC-00BFA-EL-WIR-0001 | LV Schematic and Wiring Diagrams, Part 1 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-03-08 | 70
ALP-EPC-00BFA-EL-WIR-0002 | LV Schematic and Wiring Diagrams, Part 10 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-03-09 | 17
ALP-EPC-00BFA-EL-WIR-0002 | LV Schematic and Wiring Diagrams, Part 10 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-03-09 | 71
ALP-EPC-00BFA-EL-WIR-0003 | LV Schematic and Wiring Diagrams, Part 11 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-03-18 | 24
ALP-EPC-00BFA-EL-WIR-0003 | LV Schematic and Wiring Diagrams, Part 11 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-03-18 | 78
ALP-EPC-00BFA-EL-WIR-0004 | LV Schematic and Wiring Diagrams, Part 12 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-03-22 | 26
ALP-EPC-00BFA-EL-WIR-0004 | LV Schematic and Wiring Diagrams, Part 12 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-03-22 | 80
ALP-EPC-00BFA-EL-WIR-0005 | LV Schematic and Wiring Diagrams, Part 13 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-03-31 | 33
ALP-EPC-00BFA-EL-WIR-0005 | LV Schematic and Wiring Diagrams, Part 13 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-03-31 | 87
ALP-EPC-00BFA-EL-WIR-0006 | LV Schematic and Wiring Diagrams, Part 2 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-04-19 | 46
ALP-EPC-00BFA-EL-WIR-0006 | LV Schematic and Wiring Diagrams, Part 2 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-04-19 | 100
ALP-EPC-00BFA-EL-WIR-0007 | LV Schematic and Wiring Diagrams, Part 3 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-04-23 | 50
ALP-EPC-00BFA-EL-WIR-0007 | LV Schematic and Wiring Diagrams, Part 3 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-04-23 | 104
ALP-EPC-00BFA-EL-WIR-0008 | LV Schematic and Wiring Diagrams, Part 4 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-04-26 | 51
ALP-EPC-00BFA-EL-WIR-0008 | LV Schematic and Wiring Diagrams, Part 4 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-04-26 | 105
ALP-EPC-00BFA-EL-WIR-0009 | LV Schematic and Wiring Diagrams, Part 5 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-04-30 | 55
ALP-EPC-00BFA-EL-WIR-0009 | LV Schematic and Wiring Diagrams, Part 5 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-04-30 | 109
ALP-EPC-00BFA-EL-WIR-0010 | LV Schematic and Wiring Diagrams, Part 6 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-05-06 | 59
ALP-EPC-00BFA-EL-WIR-0010 | LV Schematic and Wiring Diagrams, Part 6 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-05-06 | 113
ALP-EPC-00BFA-EL-WIR-0011 | LV Schematic and Wiring Diagrams, Part 7 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-05-24 | 71
ALP-EPC-00BFA-EL-WIR-0011 | LV Schematic and Wiring Diagrams, Part 7 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-05-24 | 125
ALP-EPC-00BFA-EL-WIR-0012 | LV Schematic and Wiring Diagrams, Part 8 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-06-01 | 77
ALP-EPC-00BFA-EL-WIR-0012 | LV Schematic and Wiring Diagrams, Part 8 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-06-01 | 131
ALP-EPC-00BFA-EL-WIR-0013 | LV Schematic and Wiring Diagrams, Part 9 of 13 | ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-12 | 2027-06-04 | 80
ALP-EPC-00BFA-EL-WIR-0013 | LV Schematic and Wiring Diagrams, Part 9 of 13 | ALP-EPC-00000-EL-LST-0001 | Electrical Load List | EPC | IFC | IFC | NONE | 2026-11-30 | 2027-06-04 | 134
ALP-EPC-00BFA-EL-DSH-0001 | LV Switchgear 0.4 kV - Datasheet | ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-DSH-0001 | LV Switchgear 0.4 kV - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-ITP-0001 | LV Switchboards and MCCs - Inspection and Test Plan | ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-03 | 1
ALP-EPC-00BMA-EL-DSH-0001 | Emergency LV Switchgear - Datasheet | ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BMA-EL-DSH-0001 | Emergency LV Switchgear - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFT-EL-DSH-0001 | LV Transformers - Datasheet | ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFT-EL-DSH-0001 | LV Transformers - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFT-EL-ITP-0001 | LV Transformers - Inspection and Test Plan | ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-26 | 18
ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet | ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet | ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-DSH-0002 | UPS: Switchgear - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-DSH-0002 | UPS: Switchgear - Datasheet | ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-DSH-0002 | UPS: Switchgear - Datasheet | ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-ITP-0001 | UPS, Batteries and DC Systems - Inspection and Test Plan | ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-02 | 22
ALP-EPC-00BTA-EL-DSH-0001 | Batteries and DC 220 V: Battery - Datasheet | ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BTA-EL-DSH-0001 | Batteries and DC 220 V: Battery - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UAC-EL-ELY-0002 | 380 kV GIS Switchyard - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UAC-EL-ELY-0001 | 380 kV GIS Switchyard - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-04-01 | 2027-07-16 | 76
ALP-EPC-00UBA-EL-ELY-0002 | Electrical Building and Emergency Power - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UBA-EL-ELY-0001 | Electrical Building and Emergency Power - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-07-08 | 112
ALP-EPC-00UBA-EL-ELY-0002 | Electrical Building and Emergency Power - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UBA-PI-PPL-0001 | Electrical Building and Emergency Power - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-07-08 | 2027-07-08 | 0
ALP-EPC-00UCA-EL-ELY-0002 | Control, Administration and Workshop Buildings - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UCA-EL-ELY-0001 | Control, Administration and Workshop Buildings - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-07-09 | 114
ALP-EPC-00UCA-EL-ELY-0002 | Control, Administration and Workshop Buildings - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UCA-PI-PPL-0001 | Control, Administration and Workshop Buildings - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-07-09 | 2027-07-09 | 0
ALP-EPC-00UEG-EL-ELY-0002 | LDO Tank Farm and Unloading - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UEG-EL-ELY-0001 | LDO Tank Farm and Unloading - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-07-12 | 2027-07-19 | 5
ALP-EPC-00UEG-EL-ELY-0002 | LDO Tank Farm and Unloading - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-07-19 | 98
ALP-EPC-00UEK-EL-ELY-0002 | Fuel Gas Station - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UEK-EL-ELY-0001 | Fuel Gas Station - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-04-09 | 27
ALP-EPC-00UEK-EL-ELY-0002 | Fuel Gas Station - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-08 | 2027-04-09 | 24
ALP-EPC-00UGA-EL-ELY-0002 | Water Treatment and Effluents - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UGA-EL-ELY-0001 | Water Treatment and Effluents - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-08-20 | 2027-08-20 | 0
ALP-EPC-00UGA-EL-ELY-0002 | Water Treatment and Effluents - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-08-20 | 122
ALP-EPC-00UPC-EL-ELY-0002 | CW Pump House and Onshore CW - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UPC-EL-ELY-0001 | CW Pump House and Onshore CW - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-07-16 | 2027-08-10 | 17
ALP-EPC-00UPC-EL-ELY-0002 | CW Pump House and Onshore CW - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-14 | 2027-08-10 | 62
ALP-EPC-00UQA-EL-ELY-0002 | BOP Utilities - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UQA-EL-ELY-0001 | BOP Utilities - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-03-18 | 2027-07-21 | 89
ALP-EPC-00UQA-EL-ELY-0002 | BOP Utilities - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | EPC | IFR | IFC | NONE | 2027-04-19 | 2027-07-21 | 67
ALP-EPC-00UQA-EL-ELY-0002 | BOP Utilities - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | EPC | IFR | IFC | NONE | 2027-06-28 | 2027-07-21 | 17
ALP-EPC-00UQA-EL-ELY-0002 | BOP Utilities - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | EPC | IFR | IFC | NONE | 2027-07-21 | 2027-07-21 | 0
ALP-EPC-00UZA-EL-ELY-0002 | Site-Wide Infrastructure - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UZA-EL-ELY-0001 | Site-Wide Infrastructure - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-01-28 | 2027-02-15 | 12
ALP-EPC-00UZA-EL-ELY-0002 | Site-Wide Infrastructure - Cable Routing, Tray and Trench Layouts | ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-02-15 | 2027-02-15 | 0
ALP-EPC-00XJA-EL-DSH-0001 | Emergency Diesel Generator - Datasheet | ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00XJA-EL-DSH-0001 | Emergency Diesel Generator - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00XJA-EL-ITP-0001 | Emergency Diesel Generator - Inspection and Test Plan | ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00XJA-ME-DSH-0001 | Emergency Diesel Generator: Tank - Datasheet | ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-11 | 50
ALP-EPC-00XJA-ME-DSH-0001 | Emergency Diesel Generator: Tank - Datasheet | ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | EPC | IFR | IFC | NONE | 2027-01-11 | 2027-01-11 | 0
ALP-EPC-10BBT-EL-DSH-0001 | GT Unit Auxiliary Transformer - Datasheet | ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10BBT-EL-DSH-0001 | GT Unit Auxiliary Transformer - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10BBT-EL-ITP-0001 | Unit Auxiliary Transformers - Inspection and Test Plan | ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-05 | 3
ALP-EPC-20BBT-EL-DSH-0001 | ST Unit Auxiliary Transformer - Datasheet | ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-20BBT-EL-DSH-0001 | ST Unit Auxiliary Transformer - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10UMA-EL-ELY-0002 | Power Block - GT and HRSG - Cable Routing, Tray and Trench Layouts | ALP-EPC-10UMA-EL-ELY-0001 | Power Block - GT and HRSG - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-03-09 | 2027-06-15 | 70
ALP-EPC-10UMA-EL-ELY-0002 | Power Block - GT and HRSG - Cable Routing, Tray and Trench Layouts | ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-12 | 2027-06-15 | 24
ALP-EPC-20UMB-EL-ELY-0002 | Power Block - ST and Condenser - Cable Routing, Tray and Trench Layouts | ALP-EPC-20UMB-EL-ELY-0001 | Power Block - ST and Condenser - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-08-30 | 2027-08-30 | 0
ALP-EPC-20UMB-EL-ELY-0002 | Power Block - ST and Condenser - Cable Routing, Tray and Trench Layouts | ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | EPC | IFR | IFC | NONE | 2027-05-11 | 2027-08-30 | 79
ALP-I08-00CJG-EL-WIR-0001 | BOP Safety Instrumented System - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFC | IFC | NONE | 2027-02-25 | 2027-05-24 | 62
ALP-I08-00CJG-IC-IOL-0001 | BOP Safety Instrumented System - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-05-14 | 59
ALP-I08-00CJG-IC-LOG-0001 | BOP Safety Instrumented System - Supplier Logic Diagrams | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-07-01 | 93
ALP-I08-00CJG-ME-CAL-0001 | BOP Safety Instrumented System - Supplier Design Calculations | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-05-14 | 59
ALP-I08-00CJG-ME-DSH-0001 | BOP Safety Instrumented System - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-05-04 | 51
ALP-I08-00CJG-ME-GAD-0001 | BOP Safety Instrumented System - Supplier GA Drawings | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-04-29 | 48
ALP-I08-00CJG-ME-ITP-0001 | BOP Safety Instrumented System - Supplier Inspection and Test Plan | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-05-04 | 51
ALP-I08-00CJG-ME-LST-0001 | BOP Safety Instrumented System - Spare Parts and Special Tools Lists | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-06-02 | 72
ALP-I08-00CJG-ME-MDB-0001 | BOP Safety Instrumented System - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-09-30 | 158
ALP-I08-00CJG-ME-OMM-0001 | BOP Safety Instrumented System - Supplier Operation and Maintenance Manual | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-07-22 | 108
ALP-I08-00CJG-ME-PRC-0001 | BOP Safety Instrumented System - Supplier Installation and Erection Manual | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-07-15 | 103
ALP-I08-00CJG-ME-TRP-0001 | BOP Safety Instrumented System - Factory Acceptance Test Report | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-09-23 | 153
ALP-I08-00CJG-ME-TST-0001 | BOP Safety Instrumented System - Factory Acceptance Test Procedure | ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-06-17 | 83
ALP-I09-00CKA-EL-WIR-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFC | IFC | NONE | 2027-02-25 | 2027-07-01 | 90
ALP-I09-00CKA-IC-IOL-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-06-17 | 83
ALP-I09-00CKA-ME-CAL-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Design Calculations | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-06-17 | 83
ALP-I09-00CKA-ME-DSH-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-05-27 | 68
ALP-I09-00CKA-ME-GAD-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier GA Drawings | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-05-27 | 68
ALP-I09-00CKA-ME-ITP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Inspection and Test Plan | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-05-27 | 68
ALP-I09-00CKA-ME-LST-0001 | Operator Training Simulator, Historian and Performance Monitoring - Spare Parts and Special Tools Lists | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-07-15 | 103
ALP-I09-00CKA-ME-MDB-0001 | Operator Training Simulator, Historian and Performance Monitoring - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2028-01-20 | 238
ALP-I09-00CKA-ME-OMM-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Operation and Maintenance Manual | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-11-11 | 188
ALP-I09-00CKA-ME-PRC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Installation and Erection Manual | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-11-04 | 183
ALP-I09-00CKA-ME-TRP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Factory Acceptance Test Report | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2028-01-13 | 233
ALP-I09-00CKA-ME-TST-0001 | Operator Training Simulator, Historian and Performance Monitoring - Factory Acceptance Test Procedure | ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | EPC | IFR | IFC | NONE | 2027-02-22 | 2027-10-07 | 163
ALP-I02-00CQA-EL-WIR-0001 | Continuous Emission Monitoring System - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-04-21 | 119
ALP-I02-00CQA-IC-DSH-0001 | Continuous Emission Monitoring System - Supplier Instrument List and Datasheets | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-28 | 127
ALP-I02-00CQA-IC-IOL-0001 | Continuous Emission Monitoring System - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-I02-00CQA-ME-CAL-0001 | Continuous Emission Monitoring System - Supplier Design Calculations | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-I02-00CQA-ME-DSH-0001 | Continuous Emission Monitoring System - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-26 | 104
ALP-I02-00CQA-ME-GAD-0001 | Continuous Emission Monitoring System - Supplier GA Drawings | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-23 | 101
ALP-I02-00CQA-ME-ITP-0001 | Continuous Emission Monitoring System - Supplier Inspection and Test Plan | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-26 | 104
ALP-I02-00CQA-ME-LST-0001 | Continuous Emission Monitoring System - Spare Parts and Special Tools Lists | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-30 | 129
ALP-I02-00CQA-ME-MDB-0001 | Continuous Emission Monitoring System - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-17 | 229
ALP-I02-00CQA-ME-OMM-0001 | Continuous Emission Monitoring System - Supplier Operation and Maintenance Manual | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-09 | 179
ALP-I02-00CQA-ME-PRC-0001 | Continuous Emission Monitoring System - Supplier Installation and Erection Manual | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-02 | 174
ALP-I02-00CQA-ME-TRP-0001 | Continuous Emission Monitoring System - Factory Acceptance Test Report | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-10 | 224
ALP-I02-00CQA-ME-TST-0001 | Continuous Emission Monitoring System - Factory Acceptance Test Procedure | ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-04 | 154
ALP-I07-00CYA-EL-WIR-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFC | IFC | NONE | 2027-03-22 | 2027-06-07 | 55
ALP-I07-00CYA-IC-IOL-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-05-31 | 53
ALP-I07-00CYA-ME-CAL-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Design Calculations | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-05-31 | 53
ALP-I07-00CYA-ME-DSH-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-05-24 | 48
ALP-I07-00CYA-ME-GAD-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier GA Drawings | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-05-17 | 43
ALP-I07-00CYA-ME-ITP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Inspection and Test Plan | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-05-24 | 48
ALP-I07-00CYA-ME-LST-0001 | Telecom, CCTV, Access Control and Perimeter Security - Spare Parts and Special Tools Lists | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-06-14 | 63
ALP-I07-00CYA-ME-MDB-0001 | Telecom, CCTV, Access Control and Perimeter Security - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-09-13 | 128
ALP-I07-00CYA-ME-OMM-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Operation and Maintenance Manual | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-07-05 | 78
ALP-I07-00CYA-ME-PRC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Installation and Erection Manual | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-06-28 | 73
ALP-I07-00CYA-ME-TRP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Factory Acceptance Test Report | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-09-06 | 123
ALP-I07-00CYA-ME-TST-0001 | Telecom, CCTV, Access Control and Perimeter Security - Factory Acceptance Test Procedure | ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-05-31 | 53
ALP-M21-00SMA-CV-CAL-0001 | EOT Cranes - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-M21-00SMA-EL-WIR-0001 | EOT Cranes - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-02-25 | 80
ALP-M21-00SMA-IC-IOL-0001 | EOT Cranes - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-M21-00SMA-ME-CAL-0001 | EOT Cranes - Supplier Design Calculations | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-M21-00SMA-ME-DSH-0001 | EOT Cranes - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-M21-00SMA-ME-GAD-0001 | EOT Cranes - Supplier GA Drawings | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-M21-00SMA-ME-ITP-0001 | EOT Cranes - Supplier Inspection and Test Plan | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-M21-00SMA-ME-LST-0001 | EOT Cranes - Spare Parts and Special Tools Lists | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-10 | 92
ALP-M21-00SMA-ME-MDB-0001 | EOT Cranes - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-26 | 213
ALP-M21-00SMA-ME-OMM-0001 | EOT Cranes - Supplier Operation and Maintenance Manual | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-17 | 163
ALP-M21-00SMA-ME-PRC-0001 | EOT Cranes - Supplier Installation and Erection Manual | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-M21-00SMA-ME-TRP-0001 | EOT Cranes - Factory Acceptance Test Report | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-19 | 208
ALP-M21-00SMA-ME-TST-0001 | EOT Cranes - Factory Acceptance Test Procedure | ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-13 | 138
ALP-EPC-10UHN-CV-EFD-0001 | Stack Foundation - Equipment Foundation Drawings | ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-10 | 2027-03-17 | 5
ALP-EPC-10UHN-CV-EFD-0001 | Stack Foundation - Equipment Foundation Drawings | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-03-17 | 67
ALP-EPC-10UHN-CV-EFD-0001 | Stack Foundation - Equipment Foundation Drawings | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-03-17 | 67
ALP-EPC-10UHN-CV-EFD-0001 | Stack Foundation - Equipment Foundation Drawings | ALP-S02-10HNE-CV-CAL-0001 | Stack 65 m with Silencer - Supplier Foundation Loads and Anchor Bolt Drawings | S02 | IFR | ACCEPTED | NONE | 2027-03-04 | 2027-03-17 | 9
ALP-EPC-00SGY-GE-RPT-0001 | Fire Detection and Alarm System - Technical Bid Evaluation | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-05-10 | 33
ALP-EPC-00UZF-GE-RPT-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Bid Evaluation | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-09 | 33
ALP-EPC-00000-GE-ITP-0001 | Construction Power Supply - Inspection and Test Plan | ALP-EPC-00000-GE-SPC-0001 | Construction Power Supply - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | ALP-EPC-00000-GE-SPC-0001 | Construction Power Supply - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00EGA-PI-SUP-0001 | LDO Unloading - Pipe Support Drawings | ALP-EPC-00EGA-PI-ISO-0001 | LDO Unloading - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-11-23 | 2027-12-09 | 12
ALP-EPC-00EGB-PI-SUP-0001 | LDO Storage - Pipe Support Drawings | ALP-EPC-00EGB-PI-ISO-0001 | LDO Storage - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-14 | 2027-12-14 | 0
ALP-EPC-00EGC-PI-SUP-0001 | LDO Forwarding and Treatment - Pipe Support Drawings | ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-10-01 | 2027-12-08 | 48
ALP-EPC-00EGC-PI-SUP-0001 | LDO Forwarding and Treatment - Pipe Support Drawings | ALP-EPC-00EGC-PI-STR-0001 | LDO Forwarding and Treatment - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-08-16 | 2027-12-08 | 82
ALP-EPC-00EKA-PI-SUP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Support Drawings | ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-09-14 | 2027-10-13 | 21
ALP-EPC-00EKA-PI-SUP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Support Drawings | ALP-EPC-00EKA-PI-STR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-08-03 | 2027-10-13 | 51
ALP-EPC-00EKC-PI-SUP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Support Drawings | ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-09-28 | 2027-10-28 | 22
ALP-EPC-00EKC-PI-SUP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Support Drawings | ALP-EPC-00EKC-PI-STR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-08-17 | 2027-10-28 | 52
ALP-EPC-00GBA-PI-SUP-0001 | Seawater Reverse Osmosis - Pipe Support Drawings | ALP-EPC-00GBA-PI-ISO-0001 | Seawater Reverse Osmosis - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-04 | 2028-01-04 | 0
ALP-EPC-00GCA-PI-SUP-0001 | Demineralisation - Pipe Support Drawings | ALP-EPC-00GCA-PI-ISO-0001 | Demineralisation - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-13 | 2028-01-13 | 0
ALP-EPC-00GHA-PI-SUP-0001 | Demineralised Water Storage and Distribution - Pipe Support Drawings | ALP-EPC-00GHA-PI-ISO-0001 | Demineralised Water Storage and Distribution - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-28 | 2028-01-28 | 0
ALP-EPC-00GKA-PI-SUP-0001 | Potable Water - Pipe Support Drawings | ALP-EPC-00GKA-PI-ISO-0001 | Potable Water - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-08-26 | 2027-08-26 | 0
ALP-EPC-00GMA-PI-SUP-0001 | Process Drains and Waste Water Collection - Pipe Support Drawings | ALP-EPC-00GMA-PI-ISO-0001 | Process Drains and Waste Water Collection - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-08-09 | 2027-08-09 | 0
ALP-EPC-00GNA-PI-SUP-0001 | Waste Water Treatment - Pipe Support Drawings | ALP-EPC-00GNA-PI-ISO-0001 | Waste Water Treatment - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-18 | 2028-01-18 | 0
ALP-EPC-00GUA-PI-SUP-0001 | Sanitary Waste Water Treatment - Pipe Support Drawings | ALP-EPC-00GUA-PI-ISO-0001 | Sanitary Waste Water Treatment - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-02-08 | 2028-02-08 | 0
ALP-EPC-00LBG-PI-SUP-0001 | Auxiliary Steam - Pipe Support Drawings | ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-11-09 | 2027-12-09 | 22
ALP-EPC-00LBG-PI-SUP-0001 | Auxiliary Steam - Pipe Support Drawings | ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-10 | 2027-12-09 | 64
ALP-EPC-00LDA-PI-SUP-0001 | Condensate Polishing - Pipe Support Drawings | ALP-EPC-00LDA-PI-ISO-0001 | Condensate Polishing - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-20 | 2028-01-20 | 0
ALP-EPC-00PAA-PI-SUP-0001 | CW Intake, Screens and Outfall - Pipe Support Drawings | ALP-EPC-00PAA-PI-ISO-0001 | CW Intake, Screens and Outfall - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-08-27 | 2027-08-27 | 0
ALP-EPC-00PAB-PI-SUP-0001 | CW Piping - Pipe Support Drawings | ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-08-30 | 2027-08-30 | 0
ALP-EPC-00PAB-PI-SUP-0001 | CW Piping - Pipe Support Drawings | ALP-EPC-00PAB-PI-STR-0001 | CW Piping - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-07-05 | 2027-08-30 | 40
ALP-EPC-00PAC-PI-SUP-0001 | CW Pumps - Pipe Support Drawings | ALP-EPC-00PAC-PI-ISO-0001 | CW Pumps - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-08-27 | 2027-08-27 | 0
ALP-EPC-00PAH-PI-SUP-0001 | Condenser Tube Cleaning - Pipe Support Drawings | ALP-EPC-00PAH-PI-ISO-0001 | Condenser Tube Cleaning - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-02-14 | 2028-02-14 | 0
ALP-EPC-00PBA-PI-SUP-0001 | Electro-Chlorination - Pipe Support Drawings | ALP-EPC-00PBA-PI-ISO-0001 | Electro-Chlorination - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-08-30 | 2027-08-30 | 0
ALP-EPC-00PGA-PI-SUP-0001 | Closed Cooling Water - Pipe Support Drawings | ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-10-21 | 2027-12-08 | 34
ALP-EPC-00PGA-PI-SUP-0001 | Closed Cooling Water - Pipe Support Drawings | ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-09 | 2027-12-08 | 64
ALP-EPC-00QCA-PI-SUP-0001 | Chemical Dosing - Pipe Support Drawings | ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-01 | 2027-12-09 | 6
ALP-EPC-00QEA-PI-SUP-0001 | Compressed Air - Pipe Support Drawings | ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-10-11 | 2027-12-09 | 43
ALP-EPC-00QHA-PI-SUP-0001 | Auxiliary Boiler - Pipe Support Drawings | ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-11-18 | 2027-12-09 | 15
ALP-EPC-00QHA-PI-SUP-0001 | Auxiliary Boiler - Pipe Support Drawings | ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-09 | 2027-12-09 | 65
ALP-EPC-00QJA-PI-SUP-0001 | Nitrogen Supply - Pipe Support Drawings | ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-15 | 2027-12-15 | 0
ALP-EPC-00QJB-PI-SUP-0001 | Hydrogen and CO2 Supply - Pipe Support Drawings | ALP-EPC-00QJB-PI-ISO-0001 | Hydrogen and CO2 Supply - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-24 | 2028-01-24 | 0
ALP-EPC-00QUA-PI-SUP-0001 | Sampling and SWAS - Pipe Support Drawings | ALP-EPC-00QUA-PI-ISO-0001 | Sampling and SWAS - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-31 | 2027-12-31 | 0
ALP-EPC-00SGA-PI-SUP-0001 | Fire Water System - Pipe Support Drawings | ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-10-20 | 2027-12-09 | 36
ALP-EPC-00SGA-PI-SUP-0001 | Fire Water System - Pipe Support Drawings | ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-08 | 2027-12-09 | 66
ALP-EPC-00SGC-PI-SUP-0001 | Deluge, Spray and Foam Systems - Pipe Support Drawings | ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-10-22 | 2027-12-09 | 34
ALP-EPC-10HAN-PI-SUP-0001 | HRSG Blowdown and Drains - Pipe Support Drawings | ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-16 | 2027-12-16 | 0
ALP-EPC-10HAN-PI-SUP-0001 | HRSG Blowdown and Drains - Pipe Support Drawings | ALP-EPC-10HAN-PI-STR-0001 | HRSG Blowdown and Drains - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-03 | 2027-12-16 | 74
ALP-EPC-10HSB-PI-SUP-0001 | Ammonia Storage and Supply - Pipe Support Drawings | ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-06 | 2027-12-09 | 3
ALP-EPC-10LAB-PI-SUP-0001 | Feedwater Piping - Pipe Support Drawings | ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-11-05 | 2027-12-09 | 24
ALP-EPC-10LAB-PI-SUP-0001 | Feedwater Piping - Pipe Support Drawings | ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-13 | 2027-12-09 | 63
ALP-EPC-10LAC-PI-SUP-0001 | Boiler Feed Pumps - Pipe Support Drawings | ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-11-25 | 2027-12-09 | 10
ALP-EPC-10LAC-PI-SUP-0001 | Boiler Feed Pumps - Pipe Support Drawings | ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-09 | 2027-12-09 | 65
ALP-EPC-10LAE-PI-SUP-0001 | HP Attemperation Spray Water - Pipe Support Drawings | ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-26 | 2028-01-26 | 0
ALP-EPC-10LAE-PI-SUP-0001 | HP Attemperation Spray Water - Pipe Support Drawings | ALP-EPC-10LAE-PI-STR-0001 | HP Attemperation Spray Water - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-11-19 | 2028-01-26 | 48
ALP-EPC-10LAF-PI-SUP-0001 | Reheat Attemperation Spray Water - Pipe Support Drawings | ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-26 | 2028-01-26 | 0
ALP-EPC-10LAF-PI-SUP-0001 | Reheat Attemperation Spray Water - Pipe Support Drawings | ALP-EPC-10LAF-PI-STR-0001 | Reheat Attemperation Spray Water - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-11-30 | 2028-01-26 | 41
ALP-EPC-10LBA-PI-SUP-0001 | Main Steam Piping - Pipe Support Drawings | ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-16 | 2027-12-16 | 0
ALP-EPC-10LBA-PI-SUP-0001 | Main Steam Piping - Pipe Support Drawings | ALP-EPC-10LBA-PI-STR-0001 | Main Steam Piping - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-08-24 | 2027-12-16 | 82
ALP-EPC-10LBB-PI-SUP-0001 | Hot Reheat Piping - Pipe Support Drawings | ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-16 | 2027-12-23 | 5
ALP-EPC-10LBB-PI-SUP-0001 | Hot Reheat Piping - Pipe Support Drawings | ALP-EPC-10LBB-PI-STR-0001 | Hot Reheat Piping - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-08-26 | 2027-12-23 | 85
ALP-EPC-10LBC-PI-SUP-0001 | Cold Reheat Piping - Pipe Support Drawings | ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings | EPC | IFC | IFC | NONE | 2027-12-23 | 2027-12-23 | 0
ALP-EPC-10LBC-PI-SUP-0001 | Cold Reheat Piping - Pipe Support Drawings | ALP-EPC-10LBC-PI-STR-0001 | Cold Reheat Piping - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-03 | 2027-12-23 | 79
ALP-EPC-10LBD-PI-SUP-0001 | LP Steam Piping - Pipe Support Drawings | ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-01-10 | 2028-01-10 | 0
ALP-EPC-10LBD-PI-SUP-0001 | LP Steam Piping - Pipe Support Drawings | ALP-EPC-10LBD-PI-STR-0001 | LP Steam Piping - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2027-09-07 | 2028-01-10 | 89
ALP-EPC-20LCA-PI-SUP-0001 | Main Condensate Piping - Pipe Support Drawings | ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-03-09 | 2028-03-09 | 0
ALP-EPC-20LCA-PI-SUP-0001 | Main Condensate Piping - Pipe Support Drawings | ALP-EPC-20LCA-PI-STR-0001 | Main Condensate Piping - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2028-01-27 | 2028-03-09 | 30
ALP-EPC-20LCB-PI-SUP-0001 | Condensate Extraction Pumps - Pipe Support Drawings | ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-03-08 | 2028-03-08 | 0
ALP-EPC-20LCB-PI-SUP-0001 | Condensate Extraction Pumps - Pipe Support Drawings | ALP-EPC-20LCB-PI-STR-0001 | Condensate Extraction Pumps - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2028-01-26 | 2028-03-08 | 30
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00EGA-PI-ISO-0001 | LDO Unloading - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-11-16 | 2028-03-02 | 77
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00EGB-PI-ISO-0001 | LDO Storage - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-12-07 | 2028-03-02 | 62
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-09-24 | 2028-03-02 | 114
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-09-07 | 2028-03-02 | 127
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-09-21 | 2028-03-02 | 117
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00GBA-PI-ISO-0001 | Seawater Reverse Osmosis - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-12-28 | 2028-03-02 | 47
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00GCA-PI-ISO-0001 | Demineralisation - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-01-06 | 2028-03-02 | 40
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00GHA-PI-ISO-0001 | Demineralised Water Storage and Distribution - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-01-21 | 2028-03-02 | 29
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00GKA-PI-ISO-0001 | Potable Water - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-08-19 | 2028-03-02 | 140
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00GMA-PI-ISO-0001 | Process Drains and Waste Water Collection - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-08-02 | 2028-03-02 | 153
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00GNA-PI-ISO-0001 | Waste Water Treatment - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-01-11 | 2028-03-02 | 37
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00GUA-PI-ISO-0001 | Sanitary Waste Water Treatment - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-02-01 | 2028-03-02 | 22
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-11-02 | 2028-03-02 | 87
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00LDA-PI-ISO-0001 | Condensate Polishing - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-01-13 | 2028-03-02 | 35
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00PAA-PI-ISO-0001 | CW Intake, Screens and Outfall - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-08-20 | 2028-03-02 | 139
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-08-23 | 2028-03-02 | 138
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00PAC-PI-ISO-0001 | CW Pumps - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-08-20 | 2028-03-02 | 139
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00PAH-PI-ISO-0001 | Condenser Tube Cleaning - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-02-07 | 2028-03-02 | 18
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00PBA-PI-ISO-0001 | Electro-Chlorination - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-08-23 | 2028-03-02 | 138
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-10-14 | 2028-03-02 | 100
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-11-24 | 2028-03-02 | 71
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-10-04 | 2028-03-02 | 108
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-11-11 | 2028-03-02 | 80
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-12-08 | 2028-03-02 | 61
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00QJB-PI-ISO-0001 | Hydrogen and CO2 Supply - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-01-17 | 2028-03-02 | 33
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00QUA-PI-ISO-0001 | Sampling and SWAS - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-12-24 | 2028-03-02 | 49
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-10-13 | 2028-03-02 | 101
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-10-15 | 2028-03-02 | 99
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-12-09 | 2028-03-02 | 60
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-11-29 | 2028-03-02 | 68
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-10-29 | 2028-03-02 | 89
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-11-18 | 2028-03-02 | 75
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-01-19 | 2028-03-02 | 31
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-01-19 | 2028-03-02 | 31
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-12-09 | 2028-03-02 | 60
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-12-09 | 2028-03-02 | 60
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings | EPC | IFR | IFC | NONE | 2027-12-16 | 2028-03-02 | 55
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-01-03 | 2028-03-02 | 43
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-03-02 | 2028-03-02 | 0
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-03-01 | 2028-03-02 | 1
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings | EPC | IFR | IFC | NONE | 2028-02-25 | 2028-03-02 | 4
ALP-EPC-20MAN-PI-SUP-0001 | Turbine Bypass Stations and Piping - Pipe Support Drawings | ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings | EPC | IFC | IFC | NONE | 2028-03-03 | 2028-03-03 | 0
ALP-EPC-20MAN-PI-SUP-0001 | Turbine Bypass Stations and Piping - Pipe Support Drawings | ALP-EPC-20MAN-PI-STR-0001 | Turbine Bypass Stations and Piping - Pipe Stress Analysis | EPC | IFC | IFC | NONE | 2028-01-21 | 2028-03-03 | 30
ALP-M16-00EGA-CV-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-M16-00EGA-EL-WIR-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-02-25 | 80
ALP-M16-00EGA-IC-DSH-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Instrument List and Datasheets | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-M16-00EGA-IC-IOL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-M16-00EGA-ME-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Design Calculations | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-M16-00EGA-ME-DSH-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-M16-00EGA-ME-GAD-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier GA Drawings | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-M16-00EGA-ME-ITP-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Inspection and Test Plan | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-M16-00EGA-ME-LST-0001 | LDO Unloading and Forwarding / Treatment Skids - Spare Parts and Special Tools Lists | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-10 | 92
ALP-M16-00EGA-ME-MDB-0001 | LDO Unloading and Forwarding / Treatment Skids - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-26 | 213
ALP-M16-00EGA-ME-OMM-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Operation and Maintenance Manual | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-17 | 163
ALP-M16-00EGA-ME-PRC-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Installation and Erection Manual | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-M16-00EGA-ME-TRP-0001 | LDO Unloading and Forwarding / Treatment Skids - Factory Acceptance Test Report | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-19 | 208
ALP-M16-00EGA-ME-TST-0001 | LDO Unloading and Forwarding / Treatment Skids - Factory Acceptance Test Procedure | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-13 | 138
ALP-M16-00EGA-PR-PID-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier P&IDs | ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-29 | 64
ALP-M15-00EKA-CV-CAL-0001 | Gas Receiving and Metering Station - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M15-00EKA-EL-WIR-0001 | Gas Receiving and Metering Station - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-04 | 85
ALP-M15-00EKA-IC-DSH-0001 | Gas Receiving and Metering Station - Supplier Instrument List and Datasheets | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M15-00EKA-IC-IOL-0001 | Gas Receiving and Metering Station - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M15-00EKA-ME-CAL-0001 | Gas Receiving and Metering Station - Supplier Design Calculations | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M15-00EKA-ME-DSH-0001 | Gas Receiving and Metering Station - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M15-00EKA-ME-GAD-0001 | Gas Receiving and Metering Station - Supplier GA Drawings | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M15-00EKA-ME-ITP-0001 | Gas Receiving and Metering Station - Supplier Inspection and Test Plan | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M15-00EKA-ME-LST-0001 | Gas Receiving and Metering Station - Spare Parts and Special Tools Lists | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-18 | 98
ALP-M15-00EKA-ME-MDB-0001 | Gas Receiving and Metering Station - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-23 | 233
ALP-M15-00EKA-ME-OMM-0001 | Gas Receiving and Metering Station - Supplier Operation and Maintenance Manual | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-15 | 183
ALP-M15-00EKA-ME-PRC-0001 | Gas Receiving and Metering Station - Supplier Installation and Erection Manual | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-08 | 178
ALP-M15-00EKA-ME-TRP-0001 | Gas Receiving and Metering Station - Factory Acceptance Test Report | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-16 | 228
ALP-M15-00EKA-ME-TST-0001 | Gas Receiving and Metering Station - Factory Acceptance Test Procedure | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-M15-00EKA-PR-PID-0001 | Gas Receiving and Metering Station - Supplier P&IDs | ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M13-00GHA-CV-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-29 | 64
ALP-M13-00GHA-EL-WIR-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-02-16 | 73
ALP-M13-00GHA-IC-DSH-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Instrument List and Datasheets | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-23 | 81
ALP-M13-00GHA-IC-IOL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-08 | 70
ALP-M13-00GHA-ME-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Design Calculations | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-08 | 70
ALP-M13-00GHA-ME-DSH-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-27 | 62
ALP-M13-00GHA-ME-GAD-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier GA Drawings | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-22 | 59
ALP-M13-00GHA-ME-ITP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Inspection and Test Plan | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-27 | 62
ALP-M13-00GHA-ME-LST-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Spare Parts and Special Tools Lists | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M13-00GHA-ME-MDB-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-25 | 169
ALP-M13-00GHA-ME-OMM-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Operation and Maintenance Manual | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-16 | 119
ALP-M13-00GHA-ME-PRC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Installation and Erection Manual | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-M13-00GHA-ME-TRP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Factory Acceptance Test Report | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-18 | 164
ALP-M13-00GHA-ME-TST-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Factory Acceptance Test Procedure | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-12 | 94
ALP-M13-00GHA-PR-PID-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier P&IDs | ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-M14-00GNA-CV-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-08 | 70
ALP-M14-00GNA-EL-WIR-0001 | Waste Water and Sanitary Treatment Packages - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-02 | 83
ALP-M14-00GNA-IC-DSH-0001 | Waste Water and Sanitary Treatment Packages - Supplier Instrument List and Datasheets | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-09 | 91
ALP-M14-00GNA-IC-IOL-0001 | Waste Water and Sanitary Treatment Packages - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M14-00GNA-IC-LOG-0001 | Waste Water and Sanitary Treatment Packages - Supplier Logic Diagrams | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-15 | 118
ALP-M14-00GNA-ME-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Design Calculations | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M14-00GNA-ME-DSH-0001 | Waste Water and Sanitary Treatment Packages - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M14-00GNA-ME-GAD-0001 | Waste Water and Sanitary Treatment Packages - Supplier GA Drawings | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-M14-00GNA-ME-ITP-0001 | Waste Water and Sanitary Treatment Packages - Supplier Inspection and Test Plan | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M14-00GNA-ME-LST-0001 | Waste Water and Sanitary Treatment Packages - Spare Parts and Special Tools Lists | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M14-00GNA-ME-MDB-0001 | Waste Water and Sanitary Treatment Packages - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-29 | 193
ALP-M14-00GNA-ME-OMM-0001 | Waste Water and Sanitary Treatment Packages - Supplier Operation and Maintenance Manual | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-20 | 143
ALP-M14-00GNA-ME-PRC-0001 | Waste Water and Sanitary Treatment Packages - Supplier Installation and Erection Manual | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-13 | 138
ALP-M14-00GNA-ME-TRP-0001 | Waste Water and Sanitary Treatment Packages - Factory Acceptance Test Report | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-22 | 188
ALP-M14-00GNA-ME-TST-0001 | Waste Water and Sanitary Treatment Packages - Factory Acceptance Test Procedure | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-15 | 118
ALP-M14-00GNA-PR-PID-0001 | Waste Water and Sanitary Treatment Packages - Supplier P&IDs | ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M12-00GBA-CV-CAL-0001 | Water Treatment Package - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M12-00GBA-EL-WIR-0001 | Water Treatment Package - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-18 | 95
ALP-M12-00GBA-IC-DSH-0001 | Water Treatment Package - Supplier Instrument List and Datasheets | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-25 | 103
ALP-M12-00GBA-IC-IOL-0001 | Water Treatment Package - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-M12-00GBA-IC-LOG-0001 | Water Treatment Package - Supplier Logic Diagrams | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-20 | 143
ALP-M12-00GBA-ME-CAL-0001 | Water Treatment Package - Supplier Design Calculations | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-M12-00GBA-ME-DSH-0001 | Water Treatment Package - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-11 | 73
ALP-M12-00GBA-ME-GAD-0001 | Water Treatment Package - Supplier GA Drawings | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-11 | 73
ALP-M12-00GBA-ME-ITP-0001 | Water Treatment Package - Supplier Inspection and Test Plan | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-11 | 73
ALP-M12-00GBA-ME-LST-0001 | Water Treatment Package - Spare Parts and Special Tools Lists | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-01 | 108
ALP-M12-00GBA-ME-MDB-0001 | Water Treatment Package - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-11-04 | 263
ALP-M12-00GBA-ME-OMM-0001 | Water Treatment Package - Supplier Operation and Maintenance Manual | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-26 | 213
ALP-M12-00GBA-ME-PRC-0001 | Water Treatment Package - Supplier Installation and Erection Manual | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-19 | 208
ALP-M12-00GBA-ME-TRP-0001 | Water Treatment Package - Factory Acceptance Test Report | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-28 | 258
ALP-M12-00GBA-ME-TST-0001 | Water Treatment Package - Factory Acceptance Test Procedure | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-22 | 188
ALP-M12-00GBA-PR-PID-0001 | Water Treatment Package - Supplier P&IDs | ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M04-00PAA-CV-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-02 | 86
ALP-M04-00PAA-EL-WIR-0001 | Travelling Band Screens and Trash Rakes - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-26 | 101
ALP-M04-00PAA-IC-DSH-0001 | Travelling Band Screens and Trash Rakes - Supplier Instrument List and Datasheets | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-02 | 109
ALP-M04-00PAA-IC-IOL-0001 | Travelling Band Screens and Trash Rakes - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-15 | 95
ALP-M04-00PAA-ME-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Design Calculations | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-15 | 95
ALP-M04-00PAA-ME-DSH-0001 | Travelling Band Screens and Trash Rakes - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-24 | 82
ALP-M04-00PAA-ME-GAD-0001 | Travelling Band Screens and Trash Rakes - Supplier GA Drawings | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-23 | 81
ALP-M04-00PAA-ME-ITP-0001 | Travelling Band Screens and Trash Rakes - Supplier Inspection and Test Plan | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-24 | 82
ALP-M04-00PAA-ME-LST-0001 | Travelling Band Screens and Trash Rakes - Spare Parts and Special Tools Lists | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-08 | 113
ALP-M04-00PAA-ME-MDB-0001 | Travelling Band Screens and Trash Rakes - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-24 | 234
ALP-M04-00PAA-ME-OMM-0001 | Travelling Band Screens and Trash Rakes - Supplier Operation and Maintenance Manual | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-16 | 184
ALP-M04-00PAA-ME-PRC-0001 | Travelling Band Screens and Trash Rakes - Supplier Installation and Erection Manual | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-09 | 179
ALP-M04-00PAA-ME-TRP-0001 | Travelling Band Screens and Trash Rakes - Factory Acceptance Test Report | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-17 | 229
ALP-M04-00PAA-ME-TST-0001 | Travelling Band Screens and Trash Rakes - Factory Acceptance Test Procedure | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-11 | 159
ALP-M04-00PAA-PR-PID-0001 | Travelling Band Screens and Trash Rakes - Supplier P&IDs | ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-01 | 85
ALP-P04-00PAB-ME-DSH-0001 | GRP CW Pipes and Fittings - Supplier Catalogues and Material Datasheets | ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-20 | 57
ALP-P04-00PAB-ME-ITP-0001 | GRP CW Pipes and Fittings - Supplier Inspection and Test Plan | ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-20 | 57
ALP-P04-00PAB-ME-MDB-0001 | GRP CW Pipes and Fittings - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-14 | 182
ALP-M03-00PAC-CV-CAL-0001 | CW Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M03-00PAC-EL-WIR-0001 | CW Pumps - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-04 | 85
ALP-M03-00PAC-IC-DSH-0001 | CW Pumps - Supplier Instrument List and Datasheets | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M03-00PAC-IC-IOL-0001 | CW Pumps - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M03-00PAC-ME-CAL-0001 | CW Pumps - Supplier Design Calculations | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M03-00PAC-ME-DSH-0001 | CW Pumps - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M03-00PAC-ME-GAD-0001 | CW Pumps - Supplier GA Drawings | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M03-00PAC-ME-ITP-0001 | CW Pumps - Supplier Inspection and Test Plan | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M03-00PAC-ME-LST-0001 | CW Pumps - Spare Parts and Special Tools Lists | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-18 | 98
ALP-M03-00PAC-ME-MDB-0001 | CW Pumps - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-21 | 253
ALP-M03-00PAC-ME-OMM-0001 | CW Pumps - Supplier Operation and Maintenance Manual | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-12 | 203
ALP-M03-00PAC-ME-PRC-0001 | CW Pumps - Supplier Installation and Erection Manual | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-05 | 198
ALP-M03-00PAC-ME-TRP-0001 | CW Pumps - Factory Acceptance Test Report | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-14 | 248
ALP-M03-00PAC-ME-TST-0001 | CW Pumps - Factory Acceptance Test Procedure | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-08 | 178
ALP-M03-00PAC-PR-PID-0001 | CW Pumps - Supplier P&IDs | ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M06-00PAH-EL-WIR-0001 | Condenser Tube Cleaning System - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-04-19 | 117
ALP-M06-00PAH-IC-DSH-0001 | Condenser Tube Cleaning System - Supplier Instrument List and Datasheets | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-26 | 125
ALP-M06-00PAH-IC-IOL-0001 | Condenser Tube Cleaning System - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-07 | 112
ALP-M06-00PAH-ME-CAL-0001 | Condenser Tube Cleaning System - Supplier Design Calculations | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-07 | 112
ALP-M06-00PAH-ME-DSH-0001 | Condenser Tube Cleaning System - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-24 | 102
ALP-M06-00PAH-ME-GAD-0001 | Condenser Tube Cleaning System - Supplier GA Drawings | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-19 | 99
ALP-M06-00PAH-ME-ITP-0001 | Condenser Tube Cleaning System - Supplier Inspection and Test Plan | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-24 | 102
ALP-M06-00PAH-ME-LST-0001 | Condenser Tube Cleaning System - Spare Parts and Special Tools Lists | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-28 | 127
ALP-M06-00PAH-ME-MDB-0001 | Condenser Tube Cleaning System - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-15 | 227
ALP-M06-00PAH-ME-OMM-0001 | Condenser Tube Cleaning System - Supplier Operation and Maintenance Manual | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-07 | 177
ALP-M06-00PAH-ME-PRC-0001 | Condenser Tube Cleaning System - Supplier Installation and Erection Manual | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-30 | 172
ALP-M06-00PAH-ME-TRP-0001 | Condenser Tube Cleaning System - Factory Acceptance Test Report | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-08 | 222
ALP-M06-00PAH-ME-TST-0001 | Condenser Tube Cleaning System - Factory Acceptance Test Procedure | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-02 | 152
ALP-M06-00PAH-PR-PID-0001 | Condenser Tube Cleaning System - Supplier P&IDs | ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-24 | 102
ALP-M05-00PBA-CV-CAL-0001 | Electro-Chlorination Package - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-03 | 87
ALP-M05-00PBA-EL-WIR-0001 | Electro-Chlorination Package - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-29 | 102
ALP-M05-00PBA-IC-DSH-0001 | Electro-Chlorination Package - Supplier Instrument List and Datasheets | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-05 | 110
ALP-M05-00PBA-IC-IOL-0001 | Electro-Chlorination Package - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-16 | 96
ALP-M05-00PBA-IC-LOG-0001 | Electro-Chlorination Package - Supplier Logic Diagrams | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-24 | 145
ALP-M05-00PBA-ME-CAL-0001 | Electro-Chlorination Package - Supplier Design Calculations | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-16 | 96
ALP-M05-00PBA-ME-DSH-0001 | Electro-Chlorination Package - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M05-00PBA-ME-GAD-0001 | Electro-Chlorination Package - Supplier GA Drawings | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-24 | 82
ALP-M05-00PBA-ME-ITP-0001 | Electro-Chlorination Package - Supplier Inspection and Test Plan | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M05-00PBA-ME-LST-0001 | Electro-Chlorination Package - Spare Parts and Special Tools Lists | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-09 | 114
ALP-M05-00PBA-ME-MDB-0001 | Electro-Chlorination Package - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-27 | 235
ALP-M05-00PBA-ME-OMM-0001 | Electro-Chlorination Package - Supplier Operation and Maintenance Manual | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-19 | 185
ALP-M05-00PBA-ME-PRC-0001 | Electro-Chlorination Package - Supplier Installation and Erection Manual | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-12 | 180
ALP-M05-00PBA-ME-TRP-0001 | Electro-Chlorination Package - Factory Acceptance Test Report | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-20 | 230
ALP-M05-00PBA-ME-TST-0001 | Electro-Chlorination Package - Factory Acceptance Test Procedure | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-14 | 160
ALP-M05-00PBA-PR-PID-0001 | Electro-Chlorination Package - Supplier P&IDs | ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-02 | 86
ALP-M07-00PGA-CV-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-01 | 85
ALP-M07-00PGA-EL-WIR-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-23 | 98
ALP-M07-00PGA-IC-DSH-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Instrument List and Datasheets | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-30 | 106
ALP-M07-00PGA-IC-IOL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M07-00PGA-ME-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Design Calculations | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M07-00PGA-ME-DSH-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M07-00PGA-ME-GAD-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier GA Drawings | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-22 | 80
ALP-M07-00PGA-ME-ITP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Inspection and Test Plan | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M07-00PGA-ME-LST-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Spare Parts and Special Tools Lists | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-01 | 108
ALP-M07-00PGA-ME-MDB-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-19 | 208
ALP-M07-00PGA-ME-OMM-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Operation and Maintenance Manual | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-M07-00PGA-ME-PRC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Installation and Erection Manual | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-03 | 153
ALP-M07-00PGA-ME-TRP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Factory Acceptance Test Report | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-12 | 203
ALP-M07-00PGA-ME-TST-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Factory Acceptance Test Procedure | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-06 | 133
ALP-M07-00PGA-PR-PID-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier P&IDs | ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M11-00QCA-EL-WIR-0001 | Chemical Dosing Skid - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFC | IFC | NONE | 2027-03-31 | 2027-06-04 | 47
ALP-M11-00QCA-IC-DSH-0001 | Chemical Dosing Skid - Supplier Instrument List and Datasheets | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-06-11 | 55
ALP-M11-00QCA-IC-IOL-0001 | Chemical Dosing Skid - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-05-27 | 44
ALP-M11-00QCA-ME-CAL-0001 | Chemical Dosing Skid - Supplier Design Calculations | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-05-27 | 44
ALP-M11-00QCA-ME-DSH-0001 | Chemical Dosing Skid - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-05-17 | 36
ALP-M11-00QCA-ME-GAD-0001 | Chemical Dosing Skid - Supplier GA Drawings | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-05-12 | 33
ALP-M11-00QCA-ME-ITP-0001 | Chemical Dosing Skid - Supplier Inspection and Test Plan | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-05-17 | 36
ALP-M11-00QCA-ME-LST-0001 | Chemical Dosing Skid - Spare Parts and Special Tools Lists | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-06-15 | 57
ALP-M11-00QCA-ME-MDB-0001 | Chemical Dosing Skid - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-10-13 | 143
ALP-M11-00QCA-ME-OMM-0001 | Chemical Dosing Skid - Supplier Operation and Maintenance Manual | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-08-04 | 93
ALP-M11-00QCA-ME-PRC-0001 | Chemical Dosing Skid - Supplier Installation and Erection Manual | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-07-28 | 88
ALP-M11-00QCA-ME-TRP-0001 | Chemical Dosing Skid - Factory Acceptance Test Report | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-10-06 | 138
ALP-M11-00QCA-ME-TST-0001 | Chemical Dosing Skid - Factory Acceptance Test Procedure | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-06-30 | 68
ALP-M11-00QCA-PR-PID-0001 | Chemical Dosing Skid - Supplier P&IDs | ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-26 | 2027-05-13 | 34
ALP-M08-00QEA-CV-CAL-0001 | Air Compressors and Dryers - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-01 | 85
ALP-M08-00QEA-EL-WIR-0001 | Air Compressors and Dryers - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-23 | 98
ALP-M08-00QEA-IC-DSH-0001 | Air Compressors and Dryers - Supplier Instrument List and Datasheets | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-30 | 106
ALP-M08-00QEA-IC-IOL-0001 | Air Compressors and Dryers - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M08-00QEA-IC-LOG-0001 | Air Compressors and Dryers - Supplier Logic Diagrams | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-06 | 133
ALP-M08-00QEA-ME-CAL-0001 | Air Compressors and Dryers - Supplier Design Calculations | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M08-00QEA-ME-DSH-0001 | Air Compressors and Dryers - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M08-00QEA-ME-GAD-0001 | Air Compressors and Dryers - Supplier GA Drawings | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-22 | 80
ALP-M08-00QEA-ME-ITP-0001 | Air Compressors and Dryers - Supplier Inspection and Test Plan | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M08-00QEA-ME-LST-0001 | Air Compressors and Dryers - Spare Parts and Special Tools Lists | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-01 | 108
ALP-M08-00QEA-ME-MDB-0001 | Air Compressors and Dryers - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-19 | 208
ALP-M08-00QEA-ME-OMM-0001 | Air Compressors and Dryers - Supplier Operation and Maintenance Manual | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-M08-00QEA-ME-PRC-0001 | Air Compressors and Dryers - Supplier Installation and Erection Manual | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-03 | 153
ALP-M08-00QEA-ME-TRP-0001 | Air Compressors and Dryers - Factory Acceptance Test Report | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-12 | 203
ALP-M08-00QEA-ME-TST-0001 | Air Compressors and Dryers - Factory Acceptance Test Procedure | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-06 | 133
ALP-M08-00QEA-PR-PID-0001 | Air Compressors and Dryers - Supplier P&IDs | ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-M09-00QHA-CV-CAL-0001 | Auxiliary Boiler - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M09-00QHA-EL-WIR-0001 | Auxiliary Boiler - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-04 | 85
ALP-M09-00QHA-IC-DSH-0001 | Auxiliary Boiler - Supplier Instrument List and Datasheets | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M09-00QHA-IC-IOL-0001 | Auxiliary Boiler - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M09-00QHA-IC-LOG-0001 | Auxiliary Boiler - Supplier Logic Diagrams | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-06 | 133
ALP-M09-00QHA-ME-CAL-0001 | Auxiliary Boiler - Supplier Design Calculations | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M09-00QHA-ME-DSH-0001 | Auxiliary Boiler - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M09-00QHA-ME-GAD-0001 | Auxiliary Boiler - Supplier GA Drawings | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M09-00QHA-ME-ITP-0001 | Auxiliary Boiler - Supplier Inspection and Test Plan | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M09-00QHA-ME-LST-0001 | Auxiliary Boiler - Spare Parts and Special Tools Lists | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-18 | 98
ALP-M09-00QHA-ME-MDB-0001 | Auxiliary Boiler - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-23 | 233
ALP-M09-00QHA-ME-OMM-0001 | Auxiliary Boiler - Supplier Operation and Maintenance Manual | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-15 | 183
ALP-M09-00QHA-ME-PRC-0001 | Auxiliary Boiler - Supplier Installation and Erection Manual | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-08 | 178
ALP-M09-00QHA-ME-TRP-0001 | Auxiliary Boiler - Factory Acceptance Test Report | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-16 | 228
ALP-M09-00QHA-ME-TST-0001 | Auxiliary Boiler - Factory Acceptance Test Procedure | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-M09-00QHA-PR-PID-0001 | Auxiliary Boiler - Supplier P&IDs | ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M10-00QJA-EL-WIR-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFC | IFC | NONE | 2027-03-30 | 2027-06-01 | 45
ALP-M10-00QJA-IC-DSH-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Instrument List and Datasheets | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-06-08 | 53
ALP-M10-00QJA-IC-IOL-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-05-25 | 43
ALP-M10-00QJA-ME-CAL-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Design Calculations | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-05-25 | 43
ALP-M10-00QJA-ME-DSH-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-05-18 | 38
ALP-M10-00QJA-ME-GAD-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier GA Drawings | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-05-11 | 33
ALP-M10-00QJA-ME-ITP-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Inspection and Test Plan | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-05-18 | 38
ALP-M10-00QJA-ME-LST-0001 | Nitrogen, Hydrogen and CO2 Supply - Spare Parts and Special Tools Lists | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-06-08 | 53
ALP-M10-00QJA-ME-MDB-0001 | Nitrogen, Hydrogen and CO2 Supply - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-09-07 | 118
ALP-M10-00QJA-ME-OMM-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Operation and Maintenance Manual | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-06-29 | 68
ALP-M10-00QJA-ME-PRC-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Installation and Erection Manual | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-06-22 | 63
ALP-M10-00QJA-ME-TRP-0001 | Nitrogen, Hydrogen and CO2 Supply - Factory Acceptance Test Report | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-08-31 | 113
ALP-M10-00QJA-ME-TST-0001 | Nitrogen, Hydrogen and CO2 Supply - Factory Acceptance Test Procedure | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-05-25 | 43
ALP-M10-00QJA-PR-PID-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier P&IDs | ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-25 | 2027-05-11 | 33
ALP-I03-00QUA-EL-WIR-0001 | Steam/Water Analysis System - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-04-23 | 121
ALP-I03-00QUA-IC-DSH-0001 | Steam/Water Analysis System - Supplier Instrument List and Datasheets | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-30 | 129
ALP-I03-00QUA-IC-IOL-0001 | Steam/Water Analysis System - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-13 | 116
ALP-I03-00QUA-ME-CAL-0001 | Steam/Water Analysis System - Supplier Design Calculations | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-13 | 116
ALP-I03-00QUA-ME-DSH-0001 | Steam/Water Analysis System - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-30 | 106
ALP-I03-00QUA-ME-GAD-0001 | Steam/Water Analysis System - Supplier GA Drawings | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-25 | 103
ALP-I03-00QUA-ME-ITP-0001 | Steam/Water Analysis System - Supplier Inspection and Test Plan | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-30 | 106
ALP-I03-00QUA-ME-LST-0001 | Steam/Water Analysis System - Spare Parts and Special Tools Lists | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-04 | 131
ALP-I03-00QUA-ME-MDB-0001 | Steam/Water Analysis System - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-21 | 231
ALP-I03-00QUA-ME-OMM-0001 | Steam/Water Analysis System - Supplier Operation and Maintenance Manual | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-13 | 181
ALP-I03-00QUA-ME-PRC-0001 | Steam/Water Analysis System - Supplier Installation and Erection Manual | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-06 | 176
ALP-I03-00QUA-ME-TRP-0001 | Steam/Water Analysis System - Factory Acceptance Test Report | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-14 | 226
ALP-I03-00QUA-ME-TST-0001 | Steam/Water Analysis System - Factory Acceptance Test Procedure | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-08 | 156
ALP-I03-00QUA-PR-PID-0001 | Steam/Water Analysis System - Supplier P&IDs | ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-30 | 106
ALP-H01-00SAA-EL-WIR-0001 | HVAC Plant and Equipment - Supplier Electrical Schematics and Wiring Diagrams, Part 1 of 2 | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-02 | 83
ALP-H01-00SAA-EL-WIR-0002 | HVAC Plant and Equipment - Supplier Electrical Schematics and Wiring Diagrams, Part 2 of 2 | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-02 | 83
ALP-H01-00SAA-IC-DSH-0001 | HVAC Plant and Equipment - Supplier Instrument List and Datasheets | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-09 | 91
ALP-H01-00SAA-IC-IOL-0001 | HVAC Plant and Equipment - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-H01-00SAA-ME-CAL-0001 | HVAC Plant and Equipment - Supplier Design Calculations | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-H01-00SAA-ME-DSH-0001 | HVAC Plant and Equipment - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-H01-00SAA-ME-GAD-0001 | HVAC Plant and Equipment - Supplier GA Drawings | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-H01-00SAA-ME-ITP-0001 | HVAC Plant and Equipment - Supplier Inspection and Test Plan | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-H01-00SAA-ME-LST-0001 | HVAC Plant and Equipment - Spare Parts and Special Tools Lists | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-H01-00SAA-ME-MDB-0001 | HVAC Plant and Equipment - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-29 | 193
ALP-H01-00SAA-ME-OMM-0001 | HVAC Plant and Equipment - Supplier Operation and Maintenance Manual | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-20 | 143
ALP-H01-00SAA-ME-PRC-0001 | HVAC Plant and Equipment - Supplier Installation and Erection Manual | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-13 | 138
ALP-H01-00SAA-ME-TRP-0001 | HVAC Plant and Equipment - Factory Acceptance Test Report | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-22 | 188
ALP-H01-00SAA-ME-TST-0001 | HVAC Plant and Equipment - Factory Acceptance Test Procedure | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-15 | 118
ALP-H01-00SAA-PR-PID-0001 | HVAC Plant and Equipment - Supplier P&IDs | ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M17-00EGB-GE-ITP-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Inspection and Test Plans | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-M17-00EGB-GE-MOS-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-M17-00EGB-GE-MOS-0002 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-M17-00EGB-GE-MOS-0003 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-M17-00EGB-GE-MOS-0004 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-M17-00EGB-GE-MOS-0005 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-M17-00EGB-GE-MOS-0006 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-M20-00SGA-CV-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-10 | 72
ALP-M20-00SGA-EL-WIR-0001 | Fire Pumps and Fire Protection Systems - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-04 | 85
ALP-M20-00SGA-IC-DSH-0001 | Fire Pumps and Fire Protection Systems - Supplier Instrument List and Datasheets | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M20-00SGA-IC-IOL-0001 | Fire Pumps and Fire Protection Systems - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-22 | 80
ALP-M20-00SGA-ME-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Design Calculations | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-22 | 80
ALP-M20-00SGA-ME-DSH-0001 | Fire Pumps and Fire Protection Systems - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-05 | 69
ALP-M20-00SGA-ME-GAD-0001 | Fire Pumps and Fire Protection Systems - Supplier GA Drawings | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-03 | 67
ALP-M20-00SGA-ME-ITP-0001 | Fire Pumps and Fire Protection Systems - Supplier Inspection and Test Plan | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-05 | 69
ALP-M20-00SGA-ME-LST-0001 | Fire Pumps and Fire Protection Systems - Spare Parts and Special Tools Lists | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-16 | 96
ALP-M20-00SGA-ME-MDB-0001 | Fire Pumps and Fire Protection Systems - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-12 | 203
ALP-M20-00SGA-ME-OMM-0001 | Fire Pumps and Fire Protection Systems - Supplier Operation and Maintenance Manual | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-03 | 153
ALP-M20-00SGA-ME-PRC-0001 | Fire Pumps and Fire Protection Systems - Supplier Installation and Erection Manual | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-27 | 148
ALP-M20-00SGA-ME-TRP-0001 | Fire Pumps and Fire Protection Systems - Factory Acceptance Test Report | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-05 | 198
ALP-M20-00SGA-ME-TST-0001 | Fire Pumps and Fire Protection Systems - Factory Acceptance Test Procedure | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-29 | 128
ALP-M20-00SGA-PR-PID-0001 | Fire Pumps and Fire Protection Systems - Supplier P&IDs | ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-08 | 70
ALP-M19-10HAN-CV-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-22 | 80
ALP-M19-10HAN-EL-WIR-0001 | HRSG Blowdown and Drain Tanks - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-10 | 89
ALP-M19-10HAN-IC-DSH-0001 | HRSG Blowdown and Drain Tanks - Supplier Instrument List and Datasheets | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-17 | 97
ALP-M19-10HAN-IC-IOL-0001 | HRSG Blowdown and Drain Tanks - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-02 | 86
ALP-M19-10HAN-ME-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Design Calculations | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-02 | 86
ALP-M19-10HAN-ME-DSH-0001 | HRSG Blowdown and Drain Tanks - Supplier Certified Datasheets and Performance Curves | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M19-10HAN-ME-GAD-0001 | HRSG Blowdown and Drain Tanks - Supplier GA Drawings | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-15 | 75
ALP-M19-10HAN-ME-ITP-0001 | HRSG Blowdown and Drain Tanks - Supplier Inspection and Test Plan | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M19-10HAN-ME-LST-0001 | HRSG Blowdown and Drain Tanks - Spare Parts and Special Tools Lists | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-19 | 99
ALP-M19-10HAN-ME-MDB-0001 | HRSG Blowdown and Drain Tanks - Manufacturing Record Book and Conformity Certificates | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-19 | 185
ALP-M19-10HAN-ME-OMM-0001 | HRSG Blowdown and Drain Tanks - Supplier Operation and Maintenance Manual | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-10 | 135
ALP-M19-10HAN-ME-PRC-0001 | HRSG Blowdown and Drain Tanks - Supplier Installation and Erection Manual | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-03 | 130
ALP-M19-10HAN-ME-TRP-0001 | HRSG Blowdown and Drain Tanks - Factory Acceptance Test Report | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-12 | 180
ALP-M19-10HAN-ME-TST-0001 | HRSG Blowdown and Drain Tanks - Factory Acceptance Test Procedure | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-05 | 110
ALP-M19-10HAN-PR-PID-0001 | HRSG Blowdown and Drain Tanks - Supplier P&IDs | ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-16 | 76
ALP-M18-10HSB-CV-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-03 | 87
ALP-M18-10HSB-EL-WIR-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-25 | 100
ALP-M18-10HSB-IC-DSH-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Instrument List and Datasheets | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-01 | 108
ALP-M18-10HSB-IC-IOL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-15 | 95
ALP-M18-10HSB-ME-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Design Calculations | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-15 | 95
ALP-M18-10HSB-ME-DSH-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Certified Datasheets and Performance Curves | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-01 | 85
ALP-M18-10HSB-ME-GAD-0001 | Aqueous Ammonia Storage and Forwarding - Supplier GA Drawings | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-24 | 82
ALP-M18-10HSB-ME-ITP-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Inspection and Test Plan | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-01 | 85
ALP-M18-10HSB-ME-LST-0001 | Aqueous Ammonia Storage and Forwarding - Spare Parts and Special Tools Lists | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-05 | 110
ALP-M18-10HSB-ME-MDB-0001 | Aqueous Ammonia Storage and Forwarding - Manufacturing Record Book and Conformity Certificates | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-23 | 210
ALP-M18-10HSB-ME-OMM-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Operation and Maintenance Manual | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-14 | 160
ALP-M18-10HSB-ME-PRC-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Installation and Erection Manual | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-07 | 155
ALP-M18-10HSB-ME-TRP-0001 | Aqueous Ammonia Storage and Forwarding - Factory Acceptance Test Report | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-16 | 205
ALP-M18-10HSB-ME-TST-0001 | Aqueous Ammonia Storage and Forwarding - Factory Acceptance Test Procedure | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-10 | 135
ALP-M18-10HSB-PR-PID-0001 | Aqueous Ammonia Storage and Forwarding - Supplier P&IDs | ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-01 | 85
ALP-M01-10LAC-CV-CAL-0001 | Boiler Feed Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M01-10LAC-EL-WIR-0001 | Boiler Feed Pumps - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-04 | 85
ALP-M01-10LAC-IC-DSH-0001 | Boiler Feed Pumps - Supplier Instrument List and Datasheets | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-M01-10LAC-IC-IOL-0001 | Boiler Feed Pumps - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M01-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Supplier Design Calculations | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-18 | 78
ALP-M01-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Supplier Certified Datasheets and Performance Curves | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M01-10LAC-ME-GAD-0001 | Boiler Feed Pumps - Supplier GA Drawings | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M01-10LAC-ME-ITP-0001 | Boiler Feed Pumps - Supplier Inspection and Test Plan | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-M01-10LAC-ME-LST-0001 | Boiler Feed Pumps - Spare Parts and Special Tools Lists | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-18 | 98
ALP-M01-10LAC-ME-MDB-0001 | Boiler Feed Pumps - Manufacturing Record Book and Conformity Certificates | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-23 | 233
ALP-M01-10LAC-ME-OMM-0001 | Boiler Feed Pumps - Supplier Operation and Maintenance Manual | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-15 | 183
ALP-M01-10LAC-ME-PRC-0001 | Boiler Feed Pumps - Supplier Installation and Erection Manual | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-08 | 178
ALP-M01-10LAC-ME-TRP-0001 | Boiler Feed Pumps - Factory Acceptance Test Report | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-16 | 228
ALP-M01-10LAC-ME-TST-0001 | Boiler Feed Pumps - Factory Acceptance Test Procedure | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-M01-10LAC-PR-PID-0001 | Boiler Feed Pumps - Supplier P&IDs | ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-M02-20LCB-CV-CAL-0001 | Condensate Extraction Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-10 | 92
ALP-M02-20LCB-EL-WIR-0001 | Condensate Extraction Pumps - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-04-05 | 107
ALP-M02-20LCB-IC-DSH-0001 | Condensate Extraction Pumps - Supplier Instrument List and Datasheets | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-12 | 115
ALP-M02-20LCB-IC-IOL-0001 | Condensate Extraction Pumps - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-23 | 101
ALP-M02-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Supplier Design Calculations | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-23 | 101
ALP-M02-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Supplier Certified Datasheets and Performance Curves | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-M02-20LCB-ME-GAD-0001 | Condensate Extraction Pumps - Supplier GA Drawings | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-03 | 87
ALP-M02-20LCB-ME-ITP-0001 | Condensate Extraction Pumps - Supplier Inspection and Test Plan | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-M02-20LCB-ME-LST-0001 | Condensate Extraction Pumps - Spare Parts and Special Tools Lists | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-16 | 119
ALP-M02-20LCB-ME-MDB-0001 | Condensate Extraction Pumps - Manufacturing Record Book and Conformity Certificates | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-04 | 240
ALP-M02-20LCB-ME-OMM-0001 | Condensate Extraction Pumps - Supplier Operation and Maintenance Manual | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-26 | 190
ALP-M02-20LCB-ME-PRC-0001 | Condensate Extraction Pumps - Supplier Installation and Erection Manual | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-19 | 185
ALP-M02-20LCB-ME-TRP-0001 | Condensate Extraction Pumps - Factory Acceptance Test Report | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-27 | 235
ALP-M02-20LCB-ME-TST-0001 | Condensate Extraction Pumps - Factory Acceptance Test Procedure | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-21 | 165
ALP-M02-20LCB-PR-PID-0001 | Condensate Extraction Pumps - Supplier P&IDs | ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-09 | 91
ALP-EPC-00CJA-IC-DSH-0001 | Plant DCS: Control Systems - Datasheet | ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CJA-IC-DSH-0001 | Plant DCS: Control Systems - Datasheet | ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CJA-IC-ITP-0001 | Plant DCS - Inspection and Test Plan | ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00UAC-EL-CBL-0001 | 380 kV GIS Switchyard - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-08-11 | 137
ALP-EPC-00UAC-EL-CBL-0001 | 380 kV GIS Switchyard - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-11 | 202
ALP-EPC-00UAC-EL-CBL-0001 | 380 kV GIS Switchyard - Cable Schedule and Routing | ALP-EPC-00UAC-EL-ELY-0001 | 380 kV GIS Switchyard - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-04-01 | 2027-08-11 | 94
ALP-EPC-00UBA-EL-CBL-0001 | Electrical Building and Emergency Power - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-02 | 1
ALP-EPC-00UBA-EL-CBL-0001 | Electrical Building and Emergency Power - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-02 | 66
ALP-EPC-00UBA-EL-CBL-0001 | Electrical Building and Emergency Power - Cable Schedule and Routing | ALP-EPC-00UBA-EL-ELY-0001 | Electrical Building and Emergency Power - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-02-02 | 2027-02-02 | 0
ALP-EPC-00UCA-EL-CBL-0001 | Control, Administration and Workshop Buildings - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-00UCA-EL-CBL-0001 | Control, Administration and Workshop Buildings - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-EPC-00UCA-EL-CBL-0001 | Control, Administration and Workshop Buildings - Cable Schedule and Routing | ALP-EPC-00UCA-EL-ELY-0001 | Control, Administration and Workshop Buildings - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-00UEG-EL-CBL-0001 | LDO Tank Farm and Unloading - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-08-11 | 137
ALP-EPC-00UEG-EL-CBL-0001 | LDO Tank Farm and Unloading - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-11 | 202
ALP-EPC-00UEG-EL-CBL-0001 | LDO Tank Farm and Unloading - Cable Schedule and Routing | ALP-EPC-00UEG-EL-ELY-0001 | LDO Tank Farm and Unloading - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-07-12 | 2027-08-11 | 22
ALP-EPC-00UEK-EL-CBL-0001 | Fuel Gas Station - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-07-19 | 120
ALP-EPC-00UEK-EL-CBL-0001 | Fuel Gas Station - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-19 | 185
ALP-EPC-00UEK-EL-CBL-0001 | Fuel Gas Station - Cable Schedule and Routing | ALP-EPC-00UEK-EL-ELY-0001 | Fuel Gas Station - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-03-03 | 2027-07-19 | 98
ALP-EPC-00UGA-EL-CBL-0001 | Water Treatment and Effluents - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-08-25 | 147
ALP-EPC-00UGA-EL-CBL-0001 | Water Treatment and Effluents - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-25 | 212
ALP-EPC-00UGA-EL-CBL-0001 | Water Treatment and Effluents - Cable Schedule and Routing | ALP-EPC-00UGA-EL-ELY-0001 | Water Treatment and Effluents - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-08-20 | 2027-08-25 | 3
ALP-EPC-00UPC-EL-CBL-0001 | CW Pump House and Onshore CW - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-08-12 | 138
ALP-EPC-00UPC-EL-CBL-0001 | CW Pump House and Onshore CW - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-12 | 203
ALP-EPC-00UPC-EL-CBL-0001 | CW Pump House and Onshore CW - Cable Schedule and Routing | ALP-EPC-00UPC-EL-ELY-0001 | CW Pump House and Onshore CW - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-07-16 | 2027-08-12 | 19
ALP-EPC-00UQA-EL-CBL-0001 | BOP Utilities - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-08-11 | 137
ALP-EPC-00UQA-EL-CBL-0001 | BOP Utilities - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-11 | 202
ALP-EPC-00UQA-EL-CBL-0001 | BOP Utilities - Cable Schedule and Routing | ALP-EPC-00UQA-EL-ELY-0001 | BOP Utilities - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-03-18 | 2027-08-11 | 104
ALP-EPC-00UZA-EL-CBL-0001 | Site-Wide Infrastructure - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-02-01 | 0
ALP-EPC-00UZA-EL-CBL-0001 | Site-Wide Infrastructure - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-EPC-00UZA-EL-CBL-0001 | Site-Wide Infrastructure - Cable Schedule and Routing | ALP-EPC-00UZA-EL-ELY-0001 | Site-Wide Infrastructure - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-01-28 | 2027-02-01 | 2
ALP-EPC-10UMA-EL-CBL-0001 | Power Block - GT and HRSG - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-08-13 | 139
ALP-EPC-10UMA-EL-CBL-0001 | Power Block - GT and HRSG - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-13 | 204
ALP-EPC-10UMA-EL-CBL-0001 | Power Block - GT and HRSG - Cable Schedule and Routing | ALP-EPC-10UMA-EL-ELY-0001 | Power Block - GT and HRSG - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-03-09 | 2027-08-13 | 113
ALP-EPC-20UMB-EL-CBL-0001 | Power Block - ST and Condenser - Cable Schedule and Routing | ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | EPC | IFR | IFC | NONE | 2027-02-01 | 2027-08-30 | 150
ALP-EPC-20UMB-EL-CBL-0001 | Power Block - ST and Condenser - Cable Schedule and Routing | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-30 | 215
ALP-EPC-20UMB-EL-CBL-0001 | Power Block - ST and Condenser - Cable Schedule and Routing | ALP-EPC-20UMB-EL-ELY-0001 | Power Block - ST and Condenser - Electrical Layouts | EPC | IFR | IFC | NONE | 2027-08-30 | 2027-08-30 | 0
ALP-EPC-00000-EL-LST-0003 | Protection Relay Settings List | ALP-EPC-00000-EL-STU-0002 | Protection Coordination Study and Relay Settings | EPC | IFR | IFC | NONE | 2027-02-15 | 2027-09-07 | 146
ALP-EPC-00BBA-EL-WIR-0001 | MV Schematic and Wiring Diagrams | ALP-EPC-00BBA-EL-SLD-0001 | MV Switchgear 10.5 kV - Single Line Diagram | EPC | IFC | IFC | NONE | 2027-02-05 | 2027-03-15 | 26
ALP-EPC-00BBA-EL-WIR-0001 | MV Schematic and Wiring Diagrams | ALP-EPC-00000-EL-STU-0002 | Protection Coordination Study and Relay Settings | EPC | IFC | IFC | NONE | 2027-03-15 | 2027-03-15 | 0
ALP-EPC-00ACA-EL-DSH-0001 | 380 kV GIS Switchyard: Switchgear - Datasheet | ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00ACA-EL-DSH-0001 | 380 kV GIS Switchyard: Switchgear - Datasheet | ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00ACA-EL-ITP-0001 | 380 kV GIS - Inspection and Test Plan | ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CM-TRP-0003 | Grid Code Compliance Test Report | ALP-EPC-00000-CM-CMP-0003 | Grid Code Compliance Test Programme | EPC | IFR | IFC | NONE | 2027-10-27 | 2029-01-29 | 328
ALP-EPC-00000-GE-RPT-0005 | Electrical and I&C Installation - Technical Bid Evaluation | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-05-19 | 43
ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | ALP-EPC-00BBA-EL-DSH-0001 | MV Switchgear 10.5 kV - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | ALP-EPC-00BFT-EL-DSH-0001 | LV Transformers - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | ALP-EPC-00BFA-EL-DSH-0001 | LV Switchgear 0.4 kV - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | ALP-EPC-00BMA-EL-DSH-0001 | Emergency LV Switchgear - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | ALP-EPC-00BRA-EL-DSH-0002 | UPS: Switchgear - Datasheet | EPC | IFR | IFC | NONE | 2026-11-16 | 2026-11-02 | -10
ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | ALP-EPC-00BTA-EL-DSH-0001 | Batteries and DC 220 V: Battery - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-16 | 10
ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | ALP-EPC-00BRA-EL-DSH-0002 | UPS: Switchgear - Datasheet | EPC | IFR | IFC | NONE | 2026-11-16 | 2026-11-16 | 0
ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | ALP-EPC-00XJA-EL-DSH-0001 | Emergency Diesel Generator - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | ALP-EPC-00XJA-ME-DSH-0001 | Emergency Diesel Generator: Tank - Datasheet | EPC | IFR | IFC | NONE | 2027-01-25 | 2026-11-02 | -60
ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | ALP-EPC-10BBT-EL-DSH-0001 | GT Unit Auxiliary Transformer - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | ALP-EPC-20BBT-EL-DSH-0001 | ST Unit Auxiliary Transformer - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-10UMA-CV-EFD-0001 | Gas Turbine Hall - Equipment Foundation Drawings | ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-12 | 2027-04-09 | 20
ALP-EPC-10UMA-CV-EFD-0001 | Gas Turbine Hall - Equipment Foundation Drawings | ALP-IEC-10MKA-CV-CAL-0001 | Generators, Excitation, GCB and Busducts - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-EPC-10UMA-CV-EFD-0001 | Gas Turbine Hall - Equipment Foundation Drawings | ALP-M21-00SMA-CV-CAL-0001 | EOT Cranes - Supplier Foundation Loads and Anchor Bolt Drawings | M21 | IFR | ACCEPTED | NONE | 2027-02-22 | 2027-04-09 | 34
ALP-EPC-10UMA-CV-EFD-0001 | Gas Turbine Hall - Equipment Foundation Drawings | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-EPC-10UMA-CV-EFD-0001 | Gas Turbine Hall - Equipment Foundation Drawings | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-09 | 84
ALP-I06-00SGY-EL-WIR-0001 | Fire Detection and Alarm System - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFC | IFC | NONE | 2027-03-29 | 2027-06-14 | 55
ALP-I06-00SGY-IC-IOL-0001 | Fire Detection and Alarm System - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-06-07 | 53
ALP-I06-00SGY-ME-CAL-0001 | Fire Detection and Alarm System - Supplier Design Calculations | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-06-07 | 53
ALP-I06-00SGY-ME-DSH-0001 | Fire Detection and Alarm System - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-05-31 | 48
ALP-I06-00SGY-ME-GAD-0001 | Fire Detection and Alarm System - Supplier GA Drawings | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-05-24 | 43
ALP-I06-00SGY-ME-ITP-0001 | Fire Detection and Alarm System - Supplier Inspection and Test Plan | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-05-31 | 48
ALP-I06-00SGY-ME-LST-0001 | Fire Detection and Alarm System - Spare Parts and Special Tools Lists | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-06-21 | 63
ALP-I06-00SGY-ME-MDB-0001 | Fire Detection and Alarm System - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-09-20 | 128
ALP-I06-00SGY-ME-OMM-0001 | Fire Detection and Alarm System - Supplier Operation and Maintenance Manual | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-07-12 | 78
ALP-I06-00SGY-ME-PRC-0001 | Fire Detection and Alarm System - Supplier Installation and Erection Manual | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-07-05 | 73
ALP-I06-00SGY-ME-TRP-0001 | Fire Detection and Alarm System - Factory Acceptance Test Report | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-09-13 | 123
ALP-I06-00SGY-ME-TST-0001 | Fire Detection and Alarm System - Factory Acceptance Test Procedure | ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-24 | 2027-06-07 | 53
ALP-M24-00UZF-GE-ITP-0001 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Inspection and Test Plans | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-30 | 48
ALP-M24-00UZF-GE-MOS-0001 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-30 | 48
ALP-M24-00UZF-GE-MOS-0002 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-30 | 48
ALP-M24-00UZF-GE-MOS-0003 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-30 | 48
ALP-M24-00UZF-GE-MOS-0004 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-30 | 48
ALP-M24-00UZF-GE-MOS-0005 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-30 | 48
ALP-M24-00UZF-GE-MOS-0006 | Heavy Transport, Barge Landing and Marine Logistics - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | EPC | IFR | IFC | NONE | 2027-06-23 | 2027-08-30 | 48
ALP-E11-00000-ME-ITP-0001 | Construction Power Supply - Supplier Inspection and Test Plan | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-09 | 5
ALP-EPC-00000-GE-RPT-0004 | Construction Power Supply - Technical Bid Evaluation | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-PI-M3D-0004 | Plant 3D Model and IFC4 Export - As-Built | ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | EPC | IFR | IFC | NONE | 2028-03-23 | 2028-03-23 | 0
ALP-EPC-00UEG-CV-EFD-0001 | LDO Tank Farm Structures - Equipment Foundation Drawings | ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-04-22 | 2027-04-27 | 3
ALP-EPC-00UEG-CV-EFD-0001 | LDO Tank Farm Structures - Equipment Foundation Drawings | ALP-M16-00EGA-CV-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Foundation Loads and Anchor Bolt Drawings | M16 | IFR | ACCEPTED | NONE | 2027-02-22 | 2027-04-27 | 46
ALP-EPC-00UEK-CV-EFD-0001 | Gas Station Structures - Equipment Foundation Drawings | ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-05-31 | 2027-05-31 | 0
ALP-EPC-00UEK-CV-EFD-0001 | Gas Station Structures - Equipment Foundation Drawings | ALP-M15-00EKA-CV-CAL-0001 | Gas Receiving and Metering Station - Supplier Foundation Loads and Anchor Bolt Drawings | M15 | IFR | ACCEPTED | NONE | 2027-02-25 | 2027-05-31 | 67
ALP-EPC-00UGA-CV-EFD-0001 | Water Treatment Building and Basins - Equipment Foundation Drawings | ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-24 | 2027-04-02 | 27
ALP-EPC-00UGA-CV-EFD-0001 | Water Treatment Building and Basins - Equipment Foundation Drawings | ALP-M12-00GBA-CV-CAL-0001 | Water Treatment Package - Supplier Foundation Loads and Anchor Bolt Drawings | M12 | IFR | ACCEPTED | NONE | 2027-03-11 | 2027-04-02 | 16
ALP-EPC-00UGA-CV-EFD-0001 | Water Treatment Building and Basins - Equipment Foundation Drawings | ALP-M13-00GHA-CV-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | M13 | IFR | ACCEPTED | NONE | 2027-02-19 | 2027-04-02 | 30
ALP-EPC-00UGA-CV-EFD-0001 | Water Treatment Building and Basins - Equipment Foundation Drawings | ALP-M14-00GNA-CV-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Foundation Loads and Anchor Bolt Drawings | M14 | IFR | ACCEPTED | NONE | 2027-03-01 | 2027-04-02 | 24
ALP-EPC-00UPC-CV-EFD-0001 | CW Pump House - Equipment Foundation Drawings | ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-25 | 2027-04-06 | 28
ALP-EPC-00UPC-CV-EFD-0001 | CW Pump House - Equipment Foundation Drawings | ALP-M03-00PAC-CV-CAL-0001 | CW Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | M03 | IFR | ACCEPTED | NONE | 2027-02-25 | 2027-04-06 | 28
ALP-EPC-00UPC-CV-EFD-0001 | CW Pump House - Equipment Foundation Drawings | ALP-M04-00PAA-CV-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Foundation Loads and Anchor Bolt Drawings | M04 | IFR | ACCEPTED | NONE | 2027-03-23 | 2027-04-06 | 10
ALP-EPC-00UPC-CV-EFD-0001 | CW Pump House - Equipment Foundation Drawings | ALP-M05-00PBA-CV-CAL-0001 | Electro-Chlorination Package - Supplier Foundation Loads and Anchor Bolt Drawings | M05 | IFR | ACCEPTED | NONE | 2027-03-24 | 2027-04-06 | 9
ALP-EPC-10UHA-CV-EFD-0001 | HRSG Foundations and Structures - Equipment Foundation Drawings | ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-04 | 2027-04-16 | 31
ALP-EPC-10UHA-CV-EFD-0001 | HRSG Foundations and Structures - Equipment Foundation Drawings | ALP-M19-10HAN-CV-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Foundation Loads and Anchor Bolt Drawings | M19 | IFR | ACCEPTED | NONE | 2027-03-15 | 2027-04-16 | 24
ALP-EPC-10UHA-CV-EFD-0001 | HRSG Foundations and Structures - Equipment Foundation Drawings | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-16 | 89
ALP-EPC-10UHA-CV-EFD-0001 | HRSG Foundations and Structures - Equipment Foundation Drawings | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-16 | 89
ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-17 | 2027-04-09 | 17
ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | ALP-M01-10LAC-CV-CAL-0001 | Boiler Feed Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | M01 | IFR | ACCEPTED | NONE | 2027-02-25 | 2027-04-09 | 31
ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | ALP-M07-00PGA-CV-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Foundation Loads and Anchor Bolt Drawings | M07 | IFR | ACCEPTED | NONE | 2027-03-22 | 2027-04-09 | 14
ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | ALP-M08-00QEA-CV-CAL-0001 | Air Compressors and Dryers - Supplier Foundation Loads and Anchor Bolt Drawings | M08 | IFR | ACCEPTED | NONE | 2027-03-22 | 2027-04-09 | 14
ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | ALP-M09-00QHA-CV-CAL-0001 | Auxiliary Boiler - Supplier Foundation Loads and Anchor Bolt Drawings | M09 | IFR | ACCEPTED | NONE | 2027-02-25 | 2027-04-09 | 31
ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | ALP-M18-10HSB-CV-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Foundation Loads and Anchor Bolt Drawings | M18 | IFR | ACCEPTED | NONE | 2027-03-24 | 2027-04-09 | 12
ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | ALP-M20-00SGA-CV-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Foundation Loads and Anchor Bolt Drawings | M20 | IFR | ACCEPTED | NONE | 2027-03-03 | 2027-04-09 | 27
ALP-EPC-20UMB-CV-EFD-0001 | Steam Turbine Hall - Equipment Foundation Drawings | ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-16 | 2027-04-27 | 30
ALP-EPC-20UMB-CV-EFD-0001 | Steam Turbine Hall - Equipment Foundation Drawings | ALP-M02-20LCB-CV-CAL-0001 | Condensate Extraction Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | M02 | IFR | ACCEPTED | NONE | 2027-03-31 | 2027-04-27 | 19
ALP-EPC-20UMB-CV-EFD-0001 | Steam Turbine Hall - Equipment Foundation Drawings | ALP-IEC-20MAA-CV-CAL-0001 | Steam Turbine and Condenser - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-28 | 2027-04-27 | 86
ALP-EPC-20UMB-CV-EFD-0001 | Steam Turbine Hall - Equipment Foundation Drawings | ALP-IEC-10MKA-CV-CAL-0001 | Generators, Excitation, GCB and Busducts - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-27 | 96
ALP-EPC-20UMB-CV-EFD-0001 | Steam Turbine Hall - Equipment Foundation Drawings | ALP-M21-00SMA-CV-CAL-0001 | EOT Cranes - Supplier Foundation Loads and Anchor Bolt Drawings | M21 | IFR | ACCEPTED | NONE | 2027-02-22 | 2027-04-27 | 46
ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | ALP-EPC-00CJA-IC-DSH-0001 | Plant DCS: Control Systems - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00000-PR-LST-0001 | Equipment List | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00ACA-EL-DSH-0001 | 380 kV GIS Switchyard: Switchgear - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00BBA-EL-DSH-0001 | MV Switchgear 10.5 kV - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00BFA-EL-DSH-0001 | LV Switchgear 0.4 kV - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00BFT-EL-DSH-0001 | LV Transformers - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00BMA-EL-DSH-0001 | Emergency LV Switchgear - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00BTA-EL-DSH-0001 | Batteries and DC 220 V: Battery - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00CJA-IC-DSH-0001 | Plant DCS: Control Systems - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00CQA-IC-DSH-0001 | Continuous Emission Monitoring: Analyser - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00EGA-ME-DSH-0001 | LDO Unloading: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00EGB-ME-DSH-0001 | LDO Storage: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00EGC-ME-DSH-0001 | LDO Forwarding and Treatment: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00EKA-ME-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00GBA-ME-DSH-0001 | Seawater Reverse Osmosis: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00GCA-ME-DSH-0001 | Demineralisation: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00GHA-ME-DSH-0001 | Demineralised Water Storage and Distribution: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00GHA-ME-DSH-0002 | Demineralised Water Storage and Distribution: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00GKA-ME-DSH-0001 | Potable Water: Tank - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00GNA-ME-DSH-0001 | Waste Water Treatment: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00GUA-ME-DSH-0001 | Sanitary Waste Water Treatment: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00LDA-ME-DSH-0001 | Condensate Polishing: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00PAA-ME-DSH-0001 | CW Intake, Screens and Outfall: Filters - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00PAC-ME-DSH-0001 | CW Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00PAH-ME-DSH-0001 | Condenser Tube Cleaning: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00PBA-ME-DSH-0001 | Electro-Chlorination: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00PGA-ME-DSH-0001 | Closed Cooling Water: Heat Exchangers - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00PGA-ME-DSH-0002 | Closed Cooling Water: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00PGA-ME-DSH-0003 | Closed Cooling Water: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00QCA-ME-DSH-0001 | Chemical Dosing: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00QEA-ME-DSH-0001 | Compressed Air: Compressors - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00QEA-ME-DSH-0002 | Compressed Air: Filters - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00QEA-ME-DSH-0003 | Compressed Air: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00QHA-ME-DSH-0001 | Auxiliary Boiler - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00QJA-ME-DSH-0001 | Nitrogen Supply: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00QJB-ME-DSH-0001 | Hydrogen and CO2 Supply: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00QUA-ME-DSH-0001 | Sampling and SWAS: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00SAA-HV-DSH-0001 | HVAC: Package - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00SMA-ME-DSH-0001 | Cranes and Hoists - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-00XJA-EL-DSH-0001 | Emergency Diesel Generator - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-10BBT-EL-DSH-0001 | GT Unit Auxiliary Transformer - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-10HAN-ME-DSH-0001 | HRSG Blowdown and Drains - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-10HNE-ME-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-10HSB-ME-DSH-0001 | Ammonia Storage and Supply: Tanks - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-10HSB-ME-DSH-0002 | Ammonia Storage and Supply: Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-20BBT-EL-DSH-0001 | ST Unit Auxiliary Transformer - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | ALP-EPC-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-18 | 12
ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | ALP-EPC-00ACA-EL-DSH-0001 | 380 kV GIS Switchyard: Switchgear - Datasheet | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-E12-00000-GE-ITP-0001 | Electrical and I&C Installation - Subcontractor Inspection and Test Plans | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-06-09 | 58
ALP-E12-00000-GE-MOS-0001 | Electrical and I&C Installation - Subcontractor Method Statements, Part 1 of 6 | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-06-09 | 58
ALP-E12-00000-GE-MOS-0002 | Electrical and I&C Installation - Subcontractor Method Statements, Part 2 of 6 | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-06-09 | 58
ALP-E12-00000-GE-MOS-0003 | Electrical and I&C Installation - Subcontractor Method Statements, Part 3 of 6 | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-06-09 | 58
ALP-E12-00000-GE-MOS-0004 | Electrical and I&C Installation - Subcontractor Method Statements, Part 4 of 6 | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-06-09 | 58
ALP-E12-00000-GE-MOS-0005 | Electrical and I&C Installation - Subcontractor Method Statements, Part 5 of 6 | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-06-09 | 58
ALP-E12-00000-GE-MOS-0006 | Electrical and I&C Installation - Subcontractor Method Statements, Part 6 of 6 | ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | EPC | IFR | IFC | NONE | 2027-03-19 | 2027-06-09 | 58
ALP-EPC-00BBA-GE-RPT-0001 | MV Switchgear 10.5 kV - Technical Bid Evaluation | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-17 | 33
ALP-EPC-00BFT-GE-RPT-0001 | LV Transformers - Technical Bid Evaluation | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-04 | 53
ALP-EPC-00BFA-GE-RPT-0001 | LV Switchboards and MCCs - Technical Bid Evaluation | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-14 | 53
ALP-EPC-00BRA-GE-RPT-0001 | UPS, Batteries and DC Systems - Technical Bid Evaluation | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-02-12 | 59
ALP-EPC-00XJA-GE-RPT-0001 | Emergency Diesel Generator - Technical Bid Evaluation | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-17 | 33
ALP-EPC-10BBT-GE-RPT-0001 | Unit Auxiliary Transformers - Technical Bid Evaluation | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-28 | 63
ALP-E11-00000-IC-IOL-0001 | Construction Power Supply - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-23 | 15
ALP-E11-00000-ME-LST-0001 | Construction Power Supply - Spare Parts and Special Tools Lists | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-07 | 25
ALP-E11-00000-ME-MDB-0001 | Construction Power Supply - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-14 | 30
ALP-E11-00000-ME-OMM-0001 | Construction Power Supply - Supplier Operation and Maintenance Manual | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-E11-00000-ME-PRC-0001 | Construction Power Supply - Supplier Installation and Erection Manual | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-E11-00000-ME-TRP-0001 | Construction Power Supply - Factory Acceptance Test Report | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-07 | 25
ALP-E11-00000-ME-TST-0001 | Construction Power Supply - Factory Acceptance Test Procedure | ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-02 | 0
ALP-EPC-00CJA-GE-RPT-0001 | Plant DCS - Technical Bid Evaluation | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-22 | 36
ALP-EPC-00000-CM-LST-0004 | Special Tools List | ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | EPC | IFR | IFC | NONE | 2027-11-03 | 2027-11-03 | 0
ALP-EPC-00ACA-GE-RPT-0001 | 380 kV GIS - Technical Bid Evaluation | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-11-05 | 3
ALP-E03-00BBA-IC-IOL-0001 | MV Switchgear 10.5 kV - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-E03-00BBA-ME-CAL-0001 | MV Switchgear 10.5 kV - Supplier Design Calculations | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-E03-00BBA-ME-DSH-0001 | MV Switchgear 10.5 kV - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-E03-00BBA-ME-GAD-0001 | MV Switchgear 10.5 kV - Supplier GA Drawings | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-E03-00BBA-ME-ITP-0001 | MV Switchgear 10.5 kV - Supplier Inspection and Test Plan | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-E03-00BBA-ME-LST-0001 | MV Switchgear 10.5 kV - Spare Parts and Special Tools Lists | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-10 | 92
ALP-E03-00BBA-ME-MDB-0001 | MV Switchgear 10.5 kV - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-26 | 213
ALP-E03-00BBA-ME-OMM-0001 | MV Switchgear 10.5 kV - Supplier Operation and Maintenance Manual | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-17 | 163
ALP-E03-00BBA-ME-PRC-0001 | MV Switchgear 10.5 kV - Supplier Installation and Erection Manual | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-E03-00BBA-ME-TRP-0001 | MV Switchgear 10.5 kV - Factory Acceptance Test Report | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-19 | 208
ALP-E03-00BBA-ME-TST-0001 | MV Switchgear 10.5 kV - Factory Acceptance Test Procedure | ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-13 | 138
ALP-E04-00BFT-IC-IOL-0001 | LV Transformers - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-17 | 82
ALP-E04-00BFT-ME-CAL-0001 | LV Transformers - Supplier Design Calculations | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-17 | 82
ALP-E04-00BFT-ME-DSH-0001 | LV Transformers - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-05 | 74
ALP-E04-00BFT-ME-GAD-0001 | LV Transformers - Supplier GA Drawings | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-02 | 71
ALP-E04-00BFT-ME-ITP-0001 | LV Transformers - Supplier Inspection and Test Plan | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-05 | 74
ALP-E04-00BFT-ME-LST-0001 | LV Transformers - Spare Parts and Special Tools Lists | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-05 | 95
ALP-E04-00BFT-ME-MDB-0001 | LV Transformers - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-08-03 | 181
ALP-E04-00BFT-ME-OMM-0001 | LV Transformers - Supplier Operation and Maintenance Manual | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-25 | 131
ALP-E04-00BFT-ME-PRC-0001 | LV Transformers - Supplier Installation and Erection Manual | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-18 | 126
ALP-E04-00BFT-ME-TRP-0001 | LV Transformers - Factory Acceptance Test Report | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-07-27 | 176
ALP-E04-00BFT-ME-TST-0001 | LV Transformers - Factory Acceptance Test Procedure | ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-20 | 106
ALP-E05-00BFA-EL-WIR-0001 | LV Switchboards and MCCs - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-09 | 88
ALP-E05-00BFA-IC-IOL-0001 | LV Switchboards and MCCs - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-E05-00BFA-ME-CAL-0001 | LV Switchboards and MCCs - Supplier Design Calculations | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-E05-00BFA-ME-DSH-0001 | LV Switchboards and MCCs - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-11 | 73
ALP-E05-00BFA-ME-GAD-0001 | LV Switchboards and MCCs - Supplier GA Drawings | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-08 | 70
ALP-E05-00BFA-ME-ITP-0001 | LV Switchboards and MCCs - Supplier Inspection and Test Plan | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-11 | 73
ALP-E05-00BFA-ME-LST-0001 | LV Switchboards and MCCs - Spare Parts and Special Tools Lists | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-18 | 98
ALP-E05-00BFA-ME-MDB-0001 | LV Switchboards and MCCs - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-05 | 198
ALP-E05-00BFA-ME-OMM-0001 | LV Switchboards and MCCs - Supplier Operation and Maintenance Manual | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-27 | 148
ALP-E05-00BFA-ME-PRC-0001 | LV Switchboards and MCCs - Supplier Installation and Erection Manual | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-20 | 143
ALP-E05-00BFA-ME-TRP-0001 | LV Switchboards and MCCs - Factory Acceptance Test Report | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-29 | 193
ALP-E05-00BFA-ME-TST-0001 | LV Switchboards and MCCs - Factory Acceptance Test Procedure | ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-22 | 123
ALP-E07-00BRA-EL-WIR-0001 | UPS, Batteries and DC Systems - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-26 | 2027-04-02 | 91
ALP-E07-00BRA-IC-IOL-0001 | UPS, Batteries and DC Systems - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-E07-00BRA-ME-CAL-0001 | UPS, Batteries and DC Systems - Supplier Design Calculations | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-25 | 88
ALP-E07-00BRA-ME-DSH-0001 | UPS, Batteries and DC Systems - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-15 | 80
ALP-E07-00BRA-ME-GAD-0001 | UPS, Batteries and DC Systems - Supplier GA Drawings | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-10 | 77
ALP-E07-00BRA-ME-ITP-0001 | UPS, Batteries and DC Systems - Supplier Inspection and Test Plan | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-03-15 | 80
ALP-E07-00BRA-ME-LST-0001 | UPS, Batteries and DC Systems - Spare Parts and Special Tools Lists | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-13 | 101
ALP-E07-00BRA-ME-MDB-0001 | UPS, Batteries and DC Systems - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-08-11 | 187
ALP-E07-00BRA-ME-OMM-0001 | UPS, Batteries and DC Systems - Supplier Operation and Maintenance Manual | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-06-02 | 137
ALP-E07-00BRA-ME-PRC-0001 | UPS, Batteries and DC Systems - Supplier Installation and Erection Manual | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-05-26 | 132
ALP-E07-00BRA-ME-TRP-0001 | UPS, Batteries and DC Systems - Factory Acceptance Test Report | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-08-04 | 182
ALP-E07-00BRA-ME-TST-0001 | UPS, Batteries and DC Systems - Factory Acceptance Test Procedure | ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-23 | 2027-04-28 | 112
ALP-E06-00XJA-CV-CAL-0001 | Emergency Diesel Generator - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-01 | 65
ALP-E06-00XJA-EL-WIR-0001 | Emergency Diesel Generator - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-02-25 | 80
ALP-E06-00XJA-IC-DSH-0001 | Emergency Diesel Generator - Supplier Instrument List and Datasheets | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-E06-00XJA-IC-IOL-0001 | Emergency Diesel Generator - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-E06-00XJA-ME-CAL-0001 | Emergency Diesel Generator - Supplier Design Calculations | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-12 | 74
ALP-E06-00XJA-ME-DSH-0001 | Emergency Diesel Generator - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-E06-00XJA-ME-GAD-0001 | Emergency Diesel Generator - Supplier GA Drawings | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-25 | 60
ALP-E06-00XJA-ME-ITP-0001 | Emergency Diesel Generator - Supplier Inspection and Test Plan | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-26 | 61
ALP-E06-00XJA-ME-LST-0001 | Emergency Diesel Generator - Spare Parts and Special Tools Lists | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-10 | 92
ALP-E06-00XJA-ME-MDB-0001 | Emergency Diesel Generator - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-26 | 213
ALP-E06-00XJA-ME-OMM-0001 | Emergency Diesel Generator - Supplier Operation and Maintenance Manual | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-17 | 163
ALP-E06-00XJA-ME-PRC-0001 | Emergency Diesel Generator - Supplier Installation and Erection Manual | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-10 | 158
ALP-E06-00XJA-ME-TRP-0001 | Emergency Diesel Generator - Factory Acceptance Test Report | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-19 | 208
ALP-E06-00XJA-ME-TST-0001 | Emergency Diesel Generator - Factory Acceptance Test Procedure | ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-05-13 | 138
ALP-E02-10BBT-CV-CAL-0001 | Unit Auxiliary Transformers - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-11 | 93
ALP-E02-10BBT-EL-WIR-0001 | Unit Auxiliary Transformers - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-04-08 | 110
ALP-E02-10BBT-IC-DSH-0001 | Unit Auxiliary Transformers - Supplier Instrument List and Datasheets | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-15 | 118
ALP-E02-10BBT-IC-IOL-0001 | Unit Auxiliary Transformers - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-25 | 103
ALP-E02-10BBT-ME-CAL-0001 | Unit Auxiliary Transformers - Supplier Design Calculations | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-25 | 103
ALP-E02-10BBT-ME-DSH-0001 | Unit Auxiliary Transformers - Supplier Certified Datasheets and Performance Curves | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-E02-10BBT-ME-GAD-0001 | Unit Auxiliary Transformers - Supplier GA Drawings | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-E02-10BBT-ME-ITP-0001 | Unit Auxiliary Transformers - Supplier Inspection and Test Plan | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-04 | 88
ALP-E02-10BBT-ME-LST-0001 | Unit Auxiliary Transformers - Spare Parts and Special Tools Lists | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-04-22 | 123
ALP-E02-10BBT-ME-MDB-0001 | Unit Auxiliary Transformers - Manufacturing Record Book and Conformity Certificates | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-28 | 258
ALP-E02-10BBT-ME-OMM-0001 | Unit Auxiliary Transformers - Supplier Operation and Maintenance Manual | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-19 | 208
ALP-E02-10BBT-ME-PRC-0001 | Unit Auxiliary Transformers - Supplier Installation and Erection Manual | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-12 | 203
ALP-E02-10BBT-ME-TRP-0001 | Unit Auxiliary Transformers - Factory Acceptance Test Report | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-10-21 | 253
ALP-E02-10BBT-ME-TST-0001 | Unit Auxiliary Transformers - Factory Acceptance Test Procedure | ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-15 | 183
ALP-I01-00CJA-EL-WIR-0001 | Plant DCS - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-03-11 | 90
ALP-I01-00CJA-IC-IOL-0001 | Plant DCS - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-I01-00CJA-ME-CAL-0001 | Plant DCS - Supplier Design Calculations | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-25 | 83
ALP-I01-00CJA-ME-DSH-0001 | Plant DCS - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-I01-00CJA-ME-GAD-0001 | Plant DCS - Supplier GA Drawings | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-I01-00CJA-ME-ITP-0001 | Plant DCS - Supplier Inspection and Test Plan | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-04 | 68
ALP-I01-00CJA-ME-LST-0001 | Plant DCS - Spare Parts and Special Tools Lists | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-03-25 | 103
ALP-I01-00CJA-ME-MDB-0001 | Plant DCS - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-30 | 238
ALP-I01-00CJA-ME-OMM-0001 | Plant DCS - Supplier Operation and Maintenance Manual | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-22 | 188
ALP-I01-00CJA-ME-PRC-0001 | Plant DCS - Supplier Installation and Erection Manual | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-07-15 | 183
ALP-I01-00CJA-ME-TRP-0001 | Plant DCS - Factory Acceptance Test Report | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-23 | 233
ALP-I01-00CJA-ME-TST-0001 | Plant DCS - Factory Acceptance Test Procedure | ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-06-17 | 163
ALP-E01-00ACA-CV-CAL-0001 | 380 kV GIS - Supplier Foundation Loads and Anchor Bolt Drawings | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-05 | 46
ALP-E01-00ACA-EL-WIR-0001 | 380 kV GIS - Supplier Electrical Schematics and Wiring Diagrams | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFC | IFC | NONE | 2026-11-05 | 2027-02-02 | 63
ALP-E01-00ACA-IC-DSH-0001 | 380 kV GIS - Supplier Instrument List and Datasheets | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-09 | 71
ALP-E01-00ACA-IC-IOL-0001 | 380 kV GIS - Supplier I/O List, Control Philosophy and Interface Signals | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-19 | 56
ALP-E01-00ACA-ME-CAL-0001 | 380 kV GIS - Supplier Design Calculations | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-01-19 | 56
ALP-E01-00ACA-ME-DSH-0001 | 380 kV GIS - Supplier Certified Datasheets and Performance Curves | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-29 | 41
ALP-E01-00ACA-ME-GAD-0001 | 380 kV GIS - Supplier GA Drawings | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-29 | 41
ALP-E01-00ACA-ME-ITP-0001 | 380 kV GIS - Supplier Inspection and Test Plan | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2026-12-29 | 41
ALP-E01-00ACA-ME-LST-0001 | 380 kV GIS - Spare Parts and Special Tools Lists | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-02-16 | 76
ALP-E01-00ACA-ME-MDB-0001 | 380 kV GIS - Manufacturing Record Book and Conformity Certificates | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-11-16 | 271
ALP-E01-00ACA-ME-OMM-0001 | 380 kV GIS - Supplier Operation and Maintenance Manual | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-09-07 | 221
ALP-E01-00ACA-ME-PRC-0001 | 380 kV GIS - Supplier Installation and Erection Manual | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-31 | 216
ALP-E01-00ACA-ME-TRP-0001 | 380 kV GIS - Factory Acceptance Test Report | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-11-09 | 266
ALP-E01-00ACA-ME-TST-0001 | 380 kV GIS - Factory Acceptance Test Procedure | ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | EPC | IFR | IFC | NONE | 2026-11-02 | 2027-08-03 | 196
ALP-EPC-00UBA-CV-EFD-0001 | Electrical Building - Equipment Foundation Drawings | ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-02-22 | 2
ALP-EPC-00UBA-CV-EFD-0001 | Electrical Building - Equipment Foundation Drawings | ALP-E06-00XJA-CV-CAL-0001 | Emergency Diesel Generator - Supplier Foundation Loads and Anchor Bolt Drawings | E06 | IFR | ACCEPTED | NONE | 2027-02-22 | 2027-02-22 | 0
ALP-EPC-00UBF-CV-EFD-0001 | Transformer Bays - Equipment Foundation Drawings | ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-03-09 | 2027-04-19 | 29
ALP-EPC-00UBF-CV-EFD-0001 | Transformer Bays - Equipment Foundation Drawings | ALP-E02-10BBT-CV-CAL-0001 | Unit Auxiliary Transformers - Supplier Foundation Loads and Anchor Bolt Drawings | E02 | IFR | ACCEPTED | NONE | 2027-04-01 | 2027-04-19 | 12
ALP-EPC-00UBF-CV-EFD-0001 | Transformer Bays - Equipment Foundation Drawings | ALP-IEC-10BAT-CV-CAL-0001 | Generator Step-Up Transformers - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-19 | 90
ALP-EPC-00UBF-CV-EFD-0001 | Transformer Bays - Equipment Foundation Drawings | ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-19 | 90
ALP-EPC-00UBF-CV-EFD-0001 | Transformer Bays - Equipment Foundation Drawings | ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | IEC | IFR | ACCEPTED | NONE | 2026-12-14 | 2027-04-19 | 90
ALP-EPC-00UAC-CV-EFD-0001 | GIS Building - Equipment Foundation Drawings | ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings | EPC | IFR | IFC | NONE | 2027-02-18 | 2027-02-18 | 0
ALP-EPC-00UAC-CV-EFD-0001 | GIS Building - Equipment Foundation Drawings | ALP-E01-00ACA-CV-CAL-0001 | 380 kV GIS - Supplier Foundation Loads and Anchor Bolt Drawings | E01 | IFR | ACCEPTED | NONE | 2027-01-26 | 2027-02-18 | 17

## Impacts
Alpilla 600 MW Combined Cycle Power Plant - Impact of a revision: documents downstream (transitive) and gates affected
engine release_control v1.2.0 ¦ generated 2026-09-29T02:52:27Z by SETUP ¦ data 6d73bc5813f68e2b ¦ planned dates from the levelled workflow network and the CPM (working days)
Document | Title | Direct users | All downstream | Disciplines | Gate instances | Gates
ALP-EPC-00000-GE-DBR-0001 | Plant Design Basis Report | 63 | 2074 | 11 | 550 | G-COM-MC-EL, G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-EL, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PR-HMB-0001 | Plant Heat and Mass Balances | 11 | 1835 | 11 | 504 | G-COM-MC-EL, G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-EL, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PR-PFD-0001 | Plant Process Flow Diagrams | 51 | 1729 | 11 | 476 | G-COM-MC-EL, G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-EL, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PR-DBR-0001 | Process Design Criteria | 135 | 1214 | 11 | 345 | G-COM-MC-EL, G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-EL, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-SPC-0001 | Piping Material Classes | 49 | 638 | 9 | 196 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-ME-DBR-0001 | Mechanical Design Criteria | 107 | 579 | 10 | 256 | G-COM-MC-EL, G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-EL, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-IC-DBR-0001 | I&C Design Criteria and Control Philosophy | 71 | 538 | 6 | 214 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-ME-SPC-0001 | General Mechanical Specification | 22 | 484 | 7 | 213 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-10MBA-ME-LAY-0001 | Power Island Arrangement - Installation and Maintenance Spaces | 1 | 422 | 10 | 180 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-PLT-0001 | Plot Plan | 27 | 421 | 10 | 179 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-CV-DBR-0001 | Civil and Structural Design Criteria | 7 | 258 | 8 | 90 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OWN-BDP, G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-EL-DBR-0001 | Electrical Design Criteria | 18 | 251 | 6 | 117 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PR-PFD-0002 | Utility Flow Diagrams | 1 | 214 | 7 | 98 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PR-LST-0001 | Equipment List | 2 | 213 | 6 | 98 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-10MBA-EL-LST-0001 | Power Island Electrical Load List | 1 | 213 | 6 | 98 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-EL-LST-0001 | Electrical Load List | 28 | 212 | 6 | 98 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-CV-RPT-0001 | Geotechnical Interpretation Report and Pile Design Basis | 58 | 210 | 6 | 81 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-IEC-10BAA-EL-SLD-0001 | Power Island Single Line Diagram | 1 | 210 | 6 | 98 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-EL-SLD-0001 | Overall Key Single Line Diagram | 54 | 209 | 6 | 98 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-EL, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-CM-PLN-0001 | Commissioning Plan | 67 | 192 | 1 | 188 | G-COM-MC-EL, G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-EL, G-COM-SC-FF, G-COM-SC-WS, G-OPS-HO-EL, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC
ALP-EPC-00GMA-PR-SDS-0001 | Process Drains and Waste Water Collection - System Design Description | 7 | 160 | 9 | 62 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GKA-PR-SDS-0001 | Potable Water - System Design Description | 7 | 156 | 9 | 61 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGA-PR-SDS-0001 | Fire Water System - System Design Description | 4 | 156 | 9 | 51 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGB-PR-SDS-0001 | LDO Storage - System Design Description | 3 | 155 | 9 | 54 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGC-PR-SDS-0001 | LDO Forwarding and Treatment - System Design Description | 3 | 154 | 9 | 50 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-PR-SDS-0001 | LDO Unloading - System Design Description | 3 | 152 | 9 | 48 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00LDA-PR-SDS-0001 | Condensate Polishing - System Design Description | 3 | 151 | 9 | 52 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-PR-SDS-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Design Description | 3 | 150 | 9 | 47 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-BDP2, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGC-PR-SDS-0001 | Deluge, Spray and Foam Systems - System Design Description | 3 | 150 | 9 | 52 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GBA-PR-SDS-0001 | Seawater Reverse Osmosis - System Design Description | 3 | 148 | 9 | 50 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GCA-PR-SDS-0001 | Demineralisation - System Design Description | 3 | 148 | 9 | 51 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HSB-PR-SDS-0001 | Ammonia Storage and Supply - System Design Description | 3 | 147 | 9 | 46 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GNA-PR-SDS-0001 | Waste Water Treatment - System Design Description | 3 | 146 | 9 | 50 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GUA-PR-SDS-0001 | Sanitary Waste Water Treatment - System Design Description | 3 | 145 | 9 | 51 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GHA-PR-SDS-0001 | Demineralised Water Storage and Distribution - System Design Description | 3 | 144 | 9 | 49 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HAN-PR-SDS-0001 | HRSG Blowdown and Drains - System Design Description | 3 | 144 | 9 | 47 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-PR-SDS-0001 | Closed Cooling Water - System Design Description | 3 | 143 | 9 | 46 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-PR-SDS-0001 | Auxiliary Boiler - System Design Description | 3 | 143 | 9 | 46 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAC-PR-SDS-0001 | Boiler Feed Pumps - System Design Description | 3 | 143 | 9 | 48 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QEA-PR-SDS-0001 | Compressed Air - System Design Description | 3 | 142 | 9 | 46 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20LCB-PR-SDS-0001 | Condensate Extraction Pumps - System Design Description | 3 | 142 | 9 | 48 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJA-PR-SDS-0001 | Nitrogen Supply - System Design Description | 3 | 140 | 8 | 46 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJB-PR-SDS-0001 | Hydrogen and CO2 Supply - System Design Description | 3 | 140 | 8 | 47 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QCA-PR-SDS-0001 | Chemical Dosing - System Design Description | 3 | 139 | 8 | 44 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-SPC-0002 | Piping Design and Layout Criteria | 14 | 136 | 4 | 86 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-IEC-10HAA-ME-GAD-0001 | HRSG incl. SCR - Supplier GA Drawings | 1 | 132 | 7 | 76 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-BDP, G-OWN-TO, G-PRC-FAB
ALP-IEC-10MBA-ME-GAD-0001 | Gas Turbine Package incl. Auxiliaries - Supplier GA Drawings | 1 | 132 | 7 | 77 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-BDP, G-OWN-TO, G-PRC-FAB
ALP-EPC-10UMA-PI-LAY-0001 | Power Block - GT and HRSG - Equipment Layout | 16 | 131 | 7 | 74 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-BDP, G-OWN-TO
ALP-EPC-00000-PI-M3D-0001 | 30 % 3D Model Review Report | 12 | 129 | 2 | 83 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00EKC-PR-SDS-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Design Description | 2 | 126 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LBA-PR-SDS-0001 | Main Steam Piping - System Design Description | 3 | 126 | 8 | 42 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LBB-PR-SDS-0001 | Hot Reheat Piping - System Design Description | 3 | 126 | 8 | 42 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LBC-PR-SDS-0001 | Cold Reheat Piping - System Design Description | 3 | 126 | 8 | 42 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LBD-PR-SDS-0001 | LP Steam Piping - System Design Description | 3 | 126 | 8 | 42 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGC-PR-PID-0001 | LDO Forwarding and Treatment - P&ID | 15 | 125 | 8 | 38 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-PR-PID-0001 | Gas Receiving, Filtration and Fiscal Metering Station - P&ID | 14 | 124 | 8 | 38 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-BDP2, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKC-PR-PID-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - P&ID | 14 | 124 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-10MBA-CV-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Foundation Loads and Anchor Bolt Drawings | 14 | 124 | 3 | 63 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-IEC-20MAA-CV-CAL-0001 | Steam Turbine and Condenser - Supplier Foundation Loads and Anchor Bolt Drawings | 5 | 124 | 3 | 63 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-EPC-00EGA-PR-PID-0001 | LDO Unloading - P&ID | 14 | 123 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HSB-PR-PID-0001 | Ammonia Storage and Supply - P&ID | 14 | 123 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-10HAA-CV-CAL-0001 | HRSG incl. SCR - Supplier Foundation Loads and Anchor Bolt Drawings | 13 | 123 | 3 | 61 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-EPC-00000-CV-CAL-0001 | Design Loads: Wind, Seismic, Equipment and Crane Loads | 48 | 122 | 3 | 60 | G-CON-CWP, G-CON-IWP
ALP-EPC-00EGB-PR-PID-0001 | LDO Storage - P&ID | 13 | 122 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00LBG-PR-SDS-0001 | Auxiliary Steam - System Design Description | 2 | 122 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAB-PR-SDS-0001 | Feedwater Piping - System Design Description | 2 | 122 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20LCA-PR-SDS-0001 | Main Condensate Piping - System Design Description | 2 | 122 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20MAN-PR-SDS-0001 | Turbine Bypass Stations and Piping - System Design Description | 2 | 122 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAE-PR-SDS-0001 | HP Attemperation Spray Water - System Design Description | 2 | 121 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAF-PR-SDS-0001 | Reheat Attemperation Spray Water - System Design Description | 2 | 121 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00LBG-PR-PID-0001 | Auxiliary Steam - P&ID | 15 | 120 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HAN-PR-PID-0001 | HRSG Blowdown and Drains - P&ID | 15 | 120 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAB-PR-PID-0001 | Feedwater Piping - P&ID | 15 | 120 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAC-PR-PID-0001 | Boiler Feed Pumps - P&ID | 15 | 120 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20LCA-PR-PID-0001 | Main Condensate Piping - P&ID | 15 | 120 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20MAN-PR-PID-0001 | Turbine Bypass Stations and Piping - P&ID | 15 | 120 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00LDA-PR-PID-0001 | Condensate Polishing - P&ID | 14 | 119 | 8 | 38 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAE-PR-PID-0001 | HP Attemperation Spray Water - P&ID | 14 | 119 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAF-PR-PID-0001 | Reheat Attemperation Spray Water - P&ID | 14 | 119 | 8 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20LCB-PR-PID-0001 | Condensate Extraction Pumps - P&ID | 14 | 119 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGA-PR-PID-0001 | Fire Water System - P&ID | 14 | 118 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LBA-PR-PID-0001 | Main Steam Piping - P&ID | 13 | 118 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LBB-PR-PID-0001 | Hot Reheat Piping - P&ID | 13 | 118 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LBC-PR-PID-0001 | Cold Reheat Piping - P&ID | 13 | 118 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LBD-PR-PID-0001 | LP Steam Piping - P&ID | 13 | 118 | 8 | 39 | G-COM-MC-FF, G-COM-MC-WS, G-COM-SC-FF, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OPS-HO-WS, G-OWN-BDP2, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GHA-PR-PID-0001 | Demineralised Water Storage and Distribution - P&ID | 14 | 117 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-PR-PID-0001 | Closed Cooling Water - P&ID | 14 | 117 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJA-PR-PID-0001 | Nitrogen Supply - P&ID | 14 | 117 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJB-PR-PID-0001 | Hydrogen and CO2 Supply - P&ID | 14 | 117 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GBA-PR-PID-0001 | Seawater Reverse Osmosis - P&ID | 13 | 116 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GCA-PR-PID-0001 | Demineralisation - P&ID | 13 | 116 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GKA-PR-PID-0001 | Potable Water - P&ID | 13 | 116 | 8 | 35 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GMA-PR-PID-0001 | Process Drains and Waste Water Collection - P&ID | 13 | 116 | 8 | 35 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QCA-PR-PID-0001 | Chemical Dosing - P&ID | 13 | 116 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QEA-PR-PID-0001 | Compressed Air - P&ID | 13 | 116 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-PR-PID-0001 | Auxiliary Boiler - P&ID | 13 | 116 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GNA-PR-PID-0001 | Waste Water Treatment - P&ID | 12 | 115 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAA-PR-SDS-0001 | CW Intake, Screens and Outfall - System Design Description | 5 | 115 | 8 | 48 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGC-PR-PID-0001 | Deluge, Spray and Foam Systems - P&ID | 12 | 115 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GUA-PR-PID-0001 | Sanitary Waste Water Treatment - P&ID | 11 | 114 | 8 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-HV-SDS-0001 | HVAC - System Design Description | 3 | 113 | 8 | 46 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-PR-SDS-0001 | Electro-Chlorination - System Design Description | 3 | 112 | 8 | 46 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00UQA-PI-LAY-0001 | BOP Utilities - Equipment Layout | 8 | 109 | 7 | 68 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PAC-PR-SDS-0001 | CW Pumps - System Design Description | 3 | 108 | 8 | 47 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-BDP2, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAH-PR-SDS-0001 | Condenser Tube Cleaning - System Design Description | 3 | 107 | 7 | 42 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QUA-PR-SDS-0001 | Sampling and SWAS - System Design Description | 3 | 107 | 7 | 42 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00UEK-PI-LAY-0001 | Fuel Gas Station - Equipment Layout | 7 | 107 | 7 | 67 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-TO
ALP-IEC-20MAA-ME-GAD-0001 | Steam Turbine and Condenser - Supplier GA Drawings | 1 | 106 | 7 | 75 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-BDP, G-PRC-FAB
ALP-EPC-20UMB-PI-LAY-0001 | Power Block - ST and Condenser - Equipment Layout | 7 | 105 | 7 | 71 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-BDP
ALP-EPC-00UPC-PI-LAY-0001 | CW Pump House and Onshore CW - Equipment Layout | 7 | 103 | 7 | 66 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UEG-PI-LAY-0001 | LDO Tank Farm and Unloading - Equipment Layout | 6 | 102 | 6 | 67 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-TO
ALP-EPC-00UGA-PI-LAY-0001 | Water Treatment and Effluents - Equipment Layout | 6 | 102 | 7 | 68 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00000-IC-RPT-0002 | OT Cybersecurity Concept | 7 | 99 | 5 | 46 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00UZA-PI-LAY-0001 | Site-Wide Infrastructure - Equipment Layout | 5 | 97 | 5 | 64 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PAB-PR-SDS-0001 | CW Piping - System Design Description | 3 | 95 | 7 | 40 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10UMA-PI-PPL-0001 | Power Block - GT and HRSG - Piping General Arrangement | 18 | 93 | 2 | 60 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UQA-PI-PPL-0001 | BOP Utilities - Piping General Arrangement, Part 1 of 3 | 19 | 92 | 2 | 60 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-20UMB-PI-PPL-0001 | Power Block - ST and Condenser - Piping General Arrangement | 9 | 89 | 2 | 60 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UEK-PI-PPL-0001 | Fuel Gas Station - Piping General Arrangement | 6 | 88 | 2 | 60 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UEG-PI-PPL-0001 | LDO Tank Farm and Unloading - Piping General Arrangement | 6 | 87 | 2 | 60 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UPC-PI-PPL-0001 | CW Pump House and Onshore CW - Piping General Arrangement | 7 | 87 | 2 | 60 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UGA-PI-PPL-0001 | Water Treatment and Effluents - Piping General Arrangement | 8 | 86 | 2 | 60 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UZA-PI-PPL-0001 | Site-Wide Infrastructure - Piping General Arrangement | 4 | 86 | 2 | 60 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PAB-PR-PID-0001 | CW Piping - P&ID | 12 | 85 | 7 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QUA-PR-PID-0001 | Sampling and SWAS - P&ID | 11 | 85 | 7 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-HV-PID-0001 | HVAC - P&ID | 14 | 85 | 7 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-M3D-0002 | 60 % 3D Model Review Report | 41 | 84 | 1 | 58 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PAA-PR-PID-0001 | CW Intake, Screens and Outfall - P&ID | 11 | 84 | 7 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAC-PR-PID-0001 | CW Pumps - P&ID | 11 | 84 | 7 | 38 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-BDP2, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAH-PR-PID-0001 | Condenser Tube Cleaning - P&ID | 11 | 84 | 7 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-PR-PID-0001 | Electro-Chlorination - P&ID | 11 | 84 | 7 | 37 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-HV-DBR-0001 | HVAC Design Criteria | 23 | 75 | 10 | 64 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-IC-LST-0001 | Instrument Index | 36 | 68 | 5 | 31 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-RPT-0001 | Pipe Stress Analysis Criteria and Critical Line List | 21 | 68 | 3 | 38 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-IC-SPC-0001 | Field Instrument Specification | 60 | 65 | 3 | 25 | G-CON-CWP, G-CON-IWP, G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-EL-STU-0003 | Earthing Study | 34 | 56 | 1 | 24 | G-CON-CWP, G-CON-IWP
ALP-EPC-00000-SS-SPC-0001 | Structural Steel Specification | 17 | 56 | 5 | 31 | G-CON-CWP, G-CON-IWP, G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-IC-RPT-0001 | Alarm Management Philosophy | 51 | 51 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-CV-SPC-0002 | Piling Specification | 9 | 46 | 3 | 21 | G-CON-CWP, G-CON-IWP, G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-HS-DBR-0001 | HSE Design Criteria | 14 | 46 | 6 | 47 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-BDP, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-10MBY-IC-IOL-0001 | Turbine Control System - Supplier I/O List, Control Philosophy and Interface Signals | 3 | 46 | 5 | 31 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-IC-IOL-0001 | Plant I/O List | 27 | 45 | 5 | 31 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-HS-HAZ-0009 | Fire Protection Concept and Fire Risk Assessment | 24 | 40 | 5 | 44 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-10MBA-PR-PID-0001 | Gas Turbine Package incl. Auxiliaries - Supplier P&IDs | 2 | 40 | 4 | 4 | G-OPS-AB, G-OWN-TO, G-OWN-TOC, G-PRC-FAB
ALP-EPC-00000-HS-HAZ-0002 | GT Fuel Gas System and Gas Station - HAZOP Report | 4 | 37 | 3 | 1 | G-OWN-TO
ALP-EPC-00UCA-PI-LAY-0001 | Control, Administration and Workshop Buildings - Equipment Layout | 13 | 37 | 7 | 11 | G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00000-HS-HAZ-0004 | LDO and Ammonia Systems - HAZOP Report | 3 | 36 | 3 | 1 | G-OWN-TO
ALP-EPC-00BFA-EL-SPC-0001 | LV Switchboards and MCCs - Technical Specification | 6 | 35 | 5 | 23 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BRA-EL-SPC-0001 | UPS, Batteries and DC Systems - Technical Specification | 5 | 34 | 5 | 23 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGA-ME-SPC-0001 | Fire Pumps and Fire Protection Systems - Technical Specification | 6 | 34 | 7 | 19 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-10HAA-PR-PID-0001 | HRSG incl. SCR - Supplier P&IDs | 2 | 34 | 3 | 4 | G-OPS-AB, G-OWN-TO, G-OWN-TOC, G-PRC-FAB
ALP-EPC-00EGB-ME-SPC-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Specification | 4 | 32 | 7 | 19 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGA-ME-CAL-0001 | Fire Water System - Sizing and Hydraulic Calculation | 3 | 32 | 7 | 19 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-20MAA-PR-PID-0001 | Steam Turbine and Condenser - Supplier P&IDs | 1 | 32 | 2 | 3 | G-OPS-AB, G-OWN-TO, G-PRC-FAB
ALP-EPC-00000-HS-HAZ-0003 | Water-Steam Cycle - HAZOP Report | 2 | 31 | 2 | 1 | G-OWN-TO
ALP-EPC-00LDA-ME-SPC-0001 | Water Treatment Package - Technical Specification | 11 | 31 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00UQA-PI-PPL-0002 | BOP Utilities - Piping General Arrangement, Part 2 of 3 | 18 | 31 | 2 | 18 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UQA-PI-PPL-0003 | BOP Utilities - Piping General Arrangement, Part 3 of 3 | 18 | 31 | 2 | 18 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00000-CV-SPC-0001 | Concrete and Civil Works Specification | 3 | 30 | 2 | 6 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-HS-HAZ-0005 | Water Treatment and Chemicals - HAZOP Report | 1 | 30 | 2 | 1 | G-OWN-TO
ALP-EPC-00000-HS-HAZ-0006 | BOP Utilities - HAZOP Report | 1 | 30 | 2 | 1 | G-OWN-TO
ALP-EPC-00BRA-EL-DSH-0001 | UPS - Datasheet | 3 | 30 | 5 | 23 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GNA-ME-SPC-0001 | Waste Water and Sanitary Treatment Packages - Technical Specification | 10 | 30 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-HS-HAZ-0007 | SIL Determination and Verification | 29 | 29 | 1 | 1 | G-OWN-TO
ALP-EPC-00SGA-ME-DSH-0001 | Fire Water System: Pumps - Datasheet | 3 | 29 | 7 | 19 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGA-ME-DSH-0002 | Fire Water System: Tanks - Datasheet | 3 | 29 | 7 | 19 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-00000-PI-LST-0001 | Terminal Point Nozzle Loads | 9 | 29 | 1 | 19 | G-COM-MC-FF, G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-TO
ALP-EPC-00BRA-EL-DSH-0002 | UPS: Switchgear - Datasheet | 2 | 28 | 4 | 22 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-ME-SPC-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Specification | 9 | 28 | 7 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-ME-SPC-0001 | Electro-Chlorination Package - Technical Specification | 7 | 27 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-IC-SPC-0002 | Control Valve Specification | 26 | 26 | 1 | 0
ALP-EPC-00GHA-ME-SPC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Specification | 7 | 26 | 7 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-ME-CAL-0001 | Electro-Chlorination - Sizing and Hydraulic Calculation | 5 | 26 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-ME-SPC-0001 | Auxiliary Boiler - Technical Specification | 6 | 26 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-HV-CAL-0001 | HVAC - Sizing and Hydraulic Calculation | 7 | 26 | 7 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-HS-RPT-0001 | EIA Conditions Compliance Matrix | 3 | 25 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-ME-SPC-0001 | Gas Receiving and Metering Station - Technical Specification | 6 | 25 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GBA-ME-CAL-0001 | Seawater Reverse Osmosis - Sizing and Hydraulic Calculation | 4 | 25 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-ME-SPC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Specification | 6 | 25 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QEA-ME-SPC-0001 | Air Compressors and Dryers - Technical Specification | 5 | 25 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-ME-CAL-0001 | Auxiliary Boiler - Sizing and Hydraulic Calculation | 4 | 25 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-ME-CAL-0001 | LDO Unloading - Sizing and Hydraulic Calculation | 4 | 24 | 7 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-ME-CAL-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Sizing and Hydraulic Calculation | 4 | 24 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GCA-ME-CAL-0001 | Demineralisation - Sizing and Hydraulic Calculation | 3 | 24 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GNA-ME-CAL-0001 | Waste Water Treatment - Sizing and Hydraulic Calculation | 3 | 24 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAA-ME-SPC-0001 | Travelling Band Screens and Trash Rakes - Technical Specification | 5 | 24 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-ME-CAL-0001 | Closed Cooling Water - Sizing and Hydraulic Calculation | 4 | 24 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QEA-ME-CAL-0001 | Compressed Air - Sizing and Hydraulic Calculation | 3 | 24 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-HV-SPC-0001 | HVAC Plant and Equipment - Technical Specification | 6 | 24 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CQA-IC-BLK-0001 | Continuous Emission Monitoring - System Architecture | 1 | 23 | 5 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGC-ME-CAL-0001 | LDO Forwarding and Treatment - Sizing and Hydraulic Calculation | 3 | 23 | 7 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GKA-ME-CAL-0001 | Potable Water - Sizing and Hydraulic Calculation | 3 | 23 | 7 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GUA-ME-CAL-0001 | Sanitary Waste Water Treatment - Sizing and Hydraulic Calculation | 2 | 23 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00LDA-ME-CAL-0001 | Condensate Polishing - Sizing and Hydraulic Calculation | 2 | 23 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAA-ME-CAL-0001 | CW Intake, Screens and Outfall - Sizing and Hydraulic Calculation | 3 | 23 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HAN-ME-SPC-0001 | HRSG Blowdown and Drain Tanks - Technical Specification | 4 | 23 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HSB-ME-SPC-0001 | Aqueous Ammonia Storage and Forwarding - Technical Specification | 4 | 23 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-EL-STU-0004 | Lightning Protection Risk Assessment | 22 | 22 | 1 | 24 | G-CON-CWP, G-CON-IWP
ALP-EPC-00000-EL-STU-0005 | Insulation Coordination Study | 1 | 22 | 6 | 13 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CQA-IC-SPC-0001 | Continuous Emission Monitoring System - Technical Specification | 5 | 22 | 5 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-OWN-TOC, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GHA-ME-CAL-0001 | Demineralised Water Storage and Distribution - Sizing and Hydraulic Calculation | 2 | 22 | 7 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GMA-ME-CAL-0001 | Process Drains and Waste Water Collection - Sizing and Hydraulic Calculation | 3 | 22 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAC-ME-CAL-0001 | CW Pumps - Sizing and Hydraulic Calculation | 2 | 22 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAC-ME-SPC-0001 | CW Pumps - Technical Specification | 3 | 22 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAH-ME-SPC-0001 | Condenser Tube Cleaning System - Technical Specification | 5 | 22 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QCA-ME-SPC-0001 | Chemical Dosing Skid - Technical Specification | 5 | 22 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJA-ME-SPC-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Specification | 5 | 22 | 6 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00XJA-EL-SPC-0001 | Emergency Diesel Generator - Technical Specification | 4 | 22 | 6 | 13 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10BBT-EL-SPC-0001 | Unit Auxiliary Transformers - Technical Specification | 4 | 22 | 6 | 16 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HAN-ME-CAL-0001 | HRSG Blowdown and Drains - Sizing and Hydraulic Calculation | 2 | 22 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HSB-ME-CAL-0001 | Ammonia Storage and Supply - Sizing and Hydraulic Calculation | 2 | 22 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAC-ME-SPC-0001 | Boiler Feed Pumps - Technical Specification | 3 | 22 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20LCB-ME-SPC-0001 | Condensate Extraction Pumps - Technical Specification | 3 | 22 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00ACA-EL-SPC-0001 | 380 kV GIS - Technical Specification | 3 | 21 | 6 | 13 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GBA-ME-DSH-0001 | Seawater Reverse Osmosis: Package - Datasheet | 2 | 21 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GCA-ME-DSH-0001 | Demineralisation: Package - Datasheet | 2 | 21 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GNA-ME-DSH-0001 | Waste Water Treatment: Package - Datasheet | 2 | 21 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GUA-ME-DSH-0001 | Sanitary Waste Water Treatment: Package - Datasheet | 2 | 21 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00LDA-ME-DSH-0001 | Condensate Polishing: Package - Datasheet | 2 | 21 | 7 | 18 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAH-ME-CAL-0001 | Condenser Tube Cleaning - Sizing and Hydraulic Calculation | 3 | 21 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-ME-DSH-0001 | Electro-Chlorination: Package - Datasheet | 2 | 21 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QCA-ME-CAL-0001 | Chemical Dosing - Sizing and Hydraulic Calculation | 3 | 21 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QEA-ME-DSH-0001 | Compressed Air: Compressors - Datasheet | 2 | 21 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QEA-ME-DSH-0002 | Compressed Air: Filters - Datasheet | 2 | 21 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QEA-ME-DSH-0003 | Compressed Air: Tanks - Datasheet | 2 | 21 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-ME-DSH-0001 | Auxiliary Boiler - Datasheet | 2 | 21 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QUA-IC-SPC-0001 | Steam/Water Analysis System - Technical Specification | 4 | 21 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SMA-ME-SPC-0001 | EOT Cranes - Technical Specification | 3 | 21 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Sizing and Hydraulic Calculation | 1 | 21 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Sizing and Hydraulic Calculation | 1 | 21 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-ME-DSH-0001 | LDO Unloading: Package - Datasheet | 2 | 20 | 7 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGC-ME-DSH-0001 | LDO Forwarding and Treatment: Package - Datasheet | 2 | 20 | 7 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-ME-DSH-0001 | Gas Receiving, Filtration and Fiscal Metering Station: Package - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GHA-ME-DSH-0001 | Demineralised Water Storage and Distribution: Tanks - Datasheet | 2 | 20 | 7 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GHA-ME-DSH-0002 | Demineralised Water Storage and Distribution: Pumps - Datasheet | 2 | 20 | 7 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GKA-ME-DSH-0001 | Potable Water: Tank - Datasheet | 2 | 20 | 7 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAA-ME-DSH-0001 | CW Intake, Screens and Outfall: Filters - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAC-ME-DSH-0001 | CW Pumps - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-ME-DSH-0001 | Closed Cooling Water: Heat Exchangers - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-ME-DSH-0002 | Closed Cooling Water: Pumps - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-ME-DSH-0003 | Closed Cooling Water: Tanks - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJA-ME-CAL-0001 | Nitrogen Supply - Sizing and Hydraulic Calculation | 2 | 20 | 6 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QUA-ME-CAL-0001 | Sampling and SWAS - Sizing and Hydraulic Calculation | 2 | 20 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGC-ME-CAL-0001 | Deluge, Spray and Foam Systems - Sizing and Hydraulic Calculation | 2 | 20 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00UBA-PI-LAY-0001 | Electrical Building and Emergency Power - Equipment Layout | 7 | 20 | 7 | 10 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10HAN-ME-DSH-0001 | HRSG Blowdown and Drains - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HSB-ME-DSH-0001 | Ammonia Storage and Supply: Tanks - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HSB-ME-DSH-0002 | Ammonia Storage and Supply: Pumps - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Datasheet | 2 | 20 | 7 | 14 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-IEC-10MBY-IC-BLK-0001 | TCS Architecture and DCS Integration | 1 | 20 | 5 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-BDP, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00ACA-EL-DSH-0001 | 380 kV GIS Switchyard: Switchgear - Datasheet | 2 | 19 | 6 | 13 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CJA-IC-BLK-0001 | Plant DCS - System Architecture | 1 | 19 | 5 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-BDP, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GBA-ME-DSH-0002 | Seawater Reverse Osmosis: Filters - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GBA-ME-DSH-0003 | Seawater Reverse Osmosis: Pumps - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GBA-ME-DSH-0004 | Seawater Reverse Osmosis: Tank - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GCA-ME-DSH-0002 | Demineralisation: Filters - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GCA-ME-DSH-0003 | Demineralisation: Pumps - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GMA-ME-DSH-0004 | Process Drains and Waste Water Collection: Filter - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GMA-ME-DSH-0005 | Process Drains and Waste Water Collection: Pumps - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GMA-ME-DSH-0006 | Process Drains and Waste Water Collection: Tank - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GNA-ME-DSH-0002 | Waste Water Treatment: Pumps - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GNA-ME-DSH-0003 | Waste Water Treatment: Tanks - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GUA-ME-DSH-0002 | Sanitary Waste Water Treatment: Pumps - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00LDA-ME-DSH-0002 | Condensate Polishing: Filters - Datasheet | 1 | 19 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-ME-DSH-0002 | Electro-Chlorination: Fans - Datasheet | 1 | 19 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-ME-DSH-0003 | Electro-Chlorination: Filters - Datasheet | 1 | 19 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-ME-DSH-0004 | Electro-Chlorination: Pumps - Datasheet | 1 | 19 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-ME-DSH-0005 | Electro-Chlorination: Tanks - Datasheet | 1 | 19 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-ME-DSH-0002 | Auxiliary Boiler: Fan - Datasheet | 1 | 19 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-ME-DSH-0003 | Auxiliary Boiler: Pumps - Datasheet | 1 | 19 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-ME-DSH-0004 | Auxiliary Boiler: Tanks - Datasheet | 1 | 19 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJB-ME-CAL-0001 | Hydrogen and CO2 Supply - Sizing and Hydraulic Calculation | 1 | 19 | 6 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-HV-DSH-0001 | HVAC: Package - Datasheet | 2 | 19 | 7 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SMA-ME-DSH-0001 | Cranes and Hoists - Datasheet | 2 | 19 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00XJA-EL-DSH-0001 | Emergency Diesel Generator - Datasheet | 2 | 19 | 6 | 13 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10BBT-EL-DSH-0001 | GT Unit Auxiliary Transformer - Datasheet | 2 | 19 | 6 | 16 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20BBT-EL-DSH-0001 | ST Unit Auxiliary Transformer - Datasheet | 2 | 19 | 6 | 16 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CJA-IC-SPC-0001 | Plant DCS - Technical Specification | 3 | 18 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CJG-IC-BLK-0001 | Safety Instrumented Systems - System Architecture | 1 | 18 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-ME-DSH-0002 | LDO Unloading: Filters - Datasheet | 1 | 18 | 6 | 15 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-ME-DSH-0003 | LDO Unloading: Pumps - Datasheet | 1 | 18 | 6 | 15 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-ME-DSH-0004 | LDO Unloading: Tank - Datasheet | 1 | 18 | 6 | 15 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGC-ME-DSH-0002 | LDO Forwarding and Treatment: Filters - Datasheet | 1 | 18 | 6 | 15 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGC-ME-DSH-0003 | LDO Forwarding and Treatment: Pumps - Datasheet | 1 | 18 | 6 | 15 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-ME-DSH-0002 | Gas Receiving, Filtration and Fiscal Metering Station: Filters - Datasheet | 1 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-ME-DSH-0003 | Gas Receiving, Filtration and Fiscal Metering Station: Heat Exchangers - Datasheet | 1 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-ME-DSH-0004 | Gas Receiving, Filtration and Fiscal Metering Station: Tank - Datasheet | 1 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GKA-ME-DSH-0002 | Potable Water: Filters - Datasheet | 1 | 18 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GKA-ME-DSH-0003 | Potable Water: Pumps - Datasheet | 1 | 18 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GNA-ME-MRQ-0001 | Waste Water and Sanitary Treatment Packages - Material Requisition | 17 | 18 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00LDA-ME-MRQ-0001 | Water Treatment Package - Material Requisition | 17 | 18 | 6 | 17 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAA-ME-DSH-0002 | CW Intake, Screens and Outfall: Pumps - Datasheet | 1 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAA-ME-DSH-0003 | CW Intake, Screens and Outfall: Valves - Datasheet | 1 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAH-ME-DSH-0001 | Condenser Tube Cleaning: Package - Datasheet | 2 | 18 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PBA-ME-MRQ-0001 | Electro-Chlorination Package - Material Requisition | 17 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-ME-DSH-0004 | Closed Cooling Water: Filter - Datasheet | 1 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QCA-ME-DSH-0001 | Chemical Dosing: Package - Datasheet | 2 | 18 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QEA-ME-MRQ-0001 | Air Compressors and Dryers - Material Requisition | 17 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QHA-ME-MRQ-0001 | Auxiliary Boiler - Material Requisition | 17 | 18 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJA-ME-DSH-0001 | Nitrogen Supply: Package - Datasheet | 2 | 18 | 6 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJB-ME-DSH-0001 | Hydrogen and CO2 Supply: Package - Datasheet | 2 | 18 | 6 | 14 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QUA-ME-DSH-0001 | Sampling and SWAS: Package - Datasheet | 2 | 18 | 6 | 12 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGC-ME-DSH-0001 | Deluge, Spray and Foam Systems: Tank - Datasheet | 1 | 18 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGC-ME-DSH-0002 | Deluge, Spray and Foam Systems: Valves - Datasheet | 1 | 18 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HAN-ME-DSH-0002 | HRSG Blowdown and Drains: Pumps - Datasheet | 1 | 18 | 6 | 13 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-ME-STU-0001 | Heavy Transport, Lifting and Erection Study | 7 | 17 | 5 | 7 | G-CON-CWP, G-CON-IWP, G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00BBA-EL-SPC-0001 | MV Switchgear 10.5 kV - Technical Specification | 3 | 17 | 5 | 11 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BFT-EL-SPC-0001 | LV Transformers - Technical Specification | 3 | 17 | 5 | 11 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CJG-GE-SPC-0001 | BOP Safety Instrumented System - Technical Specification | 3 | 17 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CKA-IC-BLK-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Architecture | 1 | 17 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CQA-IC-DSH-0001 | Continuous Emission Monitoring: Analyser - Datasheet | 2 | 17 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CYA-IC-BLK-0001 | Telecom, CCTV, Access Control, Security - System Architecture | 1 | 17 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-ME-MRQ-0001 | LDO Unloading and Forwarding / Treatment Skids - Material Requisition | 16 | 17 | 6 | 15 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EKA-ME-MRQ-0001 | Gas Receiving and Metering Station - Material Requisition | 16 | 17 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GHA-ME-MRQ-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Material Requisition | 16 | 17 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAA-ME-MRQ-0001 | Travelling Band Screens and Trash Rakes - Material Requisition | 16 | 17 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAC-ME-MRQ-0001 | CW Pumps - Material Requisition | 16 | 17 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PGA-ME-MRQ-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Material Requisition | 16 | 17 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-ME-DSH-0001 | HVAC: Compressors - Datasheet | 1 | 17 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-ME-DSH-0002 | HVAC: Fans - Datasheet | 1 | 17 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-ME-DSH-0003 | HVAC: Pumps - Datasheet | 1 | 17 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGA-ME-MRQ-0001 | Fire Pumps and Fire Protection Systems - Material Requisition | 16 | 17 | 6 | 16 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGY-IC-BLK-0001 | Fire Detection and Alarm - System Architecture | 1 | 17 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00XJA-ME-DSH-0001 | Emergency Diesel Generator: Tank - Datasheet | 1 | 17 | 5 | 12 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HAN-ME-MRQ-0001 | HRSG Blowdown and Drain Tanks - Material Requisition | 16 | 17 | 6 | 13 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HSB-ME-MRQ-0001 | Aqueous Ammonia Storage and Forwarding - Material Requisition | 16 | 17 | 6 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10LAC-ME-MRQ-0001 | Boiler Feed Pumps - Material Requisition | 16 | 17 | 6 | 13 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-20LCB-ME-MRQ-0001 | Condensate Extraction Pumps - Material Requisition | 16 | 17 | 6 | 13 | G-COM-MC-WS, G-COM-SC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-WS, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00ACA-EL-MRQ-0001 | 380 kV GIS - Material Requisition | 15 | 16 | 5 | 12 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BFA-EL-DSH-0001 | LV Switchgear 0.4 kV - Datasheet | 2 | 16 | 5 | 13 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BMA-EL-DSH-0001 | Emergency LV Switchgear - Datasheet | 2 | 16 | 5 | 13 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BTA-EL-DSH-0001 | Batteries and DC 220 V: Battery - Datasheet | 2 | 16 | 5 | 13 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CJA-IC-DSH-0001 | Plant DCS: Control Systems - Datasheet | 2 | 16 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CKA-GE-SPC-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Specification | 3 | 16 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CYA-GE-SPC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Specification | 3 | 16 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAH-ME-DSH-0002 | Condenser Tube Cleaning: Filters - Datasheet | 1 | 16 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAH-ME-DSH-0003 | Condenser Tube Cleaning: Pumps - Datasheet | 1 | 16 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QCA-ME-DSH-0002 | Chemical Dosing: Pumps - Datasheet | 1 | 16 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QCA-ME-DSH-0003 | Chemical Dosing: Tanks - Datasheet | 1 | 16 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJA-ME-DSH-0002 | Nitrogen Supply: Tank - Datasheet | 1 | 16 | 5 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QUA-ME-DSH-0002 | Sampling and SWAS: Heat Exchanger - Datasheet | 1 | 16 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SAA-HV-MRQ-0001 | HVAC Plant and Equipment - Material Requisition | 16 | 16 | 5 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGY-GE-SPC-0001 | Fire Detection and Alarm System - Technical Specification | 3 | 16 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SMA-ME-MRQ-0001 | EOT Cranes - Material Requisition | 14 | 16 | 5 | 15 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00UAC-PI-LAY-0001 | 380 kV GIS Switchyard - Equipment Layout | 5 | 16 | 6 | 7 | G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00XJA-EL-MRQ-0001 | Emergency Diesel Generator - Material Requisition | 15 | 16 | 5 | 12 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10BBT-EL-MRQ-0001 | Unit Auxiliary Transformers - Material Requisition | 15 | 16 | 5 | 15 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-EL-STU-0001 | Load Flow, Short-Circuit and Motor Starting Study | 2 | 15 | 1 | 24 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-OWN-TO
ALP-EPC-00000-HS-STU-0002 | Stack Dispersion Confirmation | 1 | 15 | 5 | 5 | G-CON-CWP, G-CON-IWP, G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-PR-STU-0003 | CW Thermal Plume and Outfall Dispersion Study | 2 | 15 | 3 | 4 | G-CON-CWP, G-CON-IWP, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00BBA-EL-DSH-0001 | MV Switchgear 10.5 kV - Datasheet | 2 | 15 | 5 | 11 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BFT-EL-DSH-0001 | LV Transformers - Datasheet | 2 | 15 | 5 | 11 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CJG-IC-DSH-0001 | Safety Instrumented Systems: Control System - Datasheet | 1 | 15 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAH-ME-MRQ-0001 | Condenser Tube Cleaning System - Material Requisition | 15 | 15 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QCA-ME-MRQ-0001 | Chemical Dosing Skid - Material Requisition | 15 | 15 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QJA-ME-MRQ-0001 | Nitrogen, Hydrogen and CO2 Supply - Material Requisition | 15 | 15 | 5 | 13 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00QUA-IC-MRQ-0001 | Steam/Water Analysis System - Material Requisition | 15 | 15 | 5 | 11 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CJG-GE-MRQ-0001 | BOP Safety Instrumented System - Material Requisition | 14 | 14 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CKA-IC-DSH-0001 | Historian, Performance Monitoring and Operator Training Simulator: Control System - Datasheet | 1 | 14 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CQA-IC-MRQ-0001 | Continuous Emission Monitoring System - Material Requisition | 14 | 14 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CYA-IC-DSH-0001 | Telecom, CCTV, Access Control, Security - Datasheet | 1 | 14 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGY-IC-DSH-0001 | Fire Detection and Alarm: Control System - Datasheet | 1 | 14 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00UZA-CV-CVL-0001 | Temporary Facilities and Construction Site Layout | 1 | 14 | 4 | 9 | G-CON-CWP, G-CON-IWP, G-OPS-AB, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HNE-SS-SPC-0001 | Stack 65 m with Silencer - Technical Specification | 2 | 14 | 5 | 5 | G-CON-CWP, G-CON-IWP, G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-EL-LST-0002 | Construction Power Load List | 1 | 13 | 4 | 8 | G-CON-CWP, G-OPS-AB, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-ME-RPT-0002 | Materials Selection and Corrosion Control Report | 1 | 13 | 4 | 7 | G-COM-SC-EL, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BFA-EL-MRQ-0001 | LV Switchboards and MCCs - Material Requisition | 13 | 13 | 4 | 12 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BFA-EL-SLD-0001 | LV Switchgear 0.4 kV - Single Line Diagram | 13 | 13 | 1 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00BRA-EL-MRQ-0001 | UPS, Batteries and DC Systems - Material Requisition | 13 | 13 | 4 | 12 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CJA-IC-MRQ-0001 | Plant DCS - Material Requisition | 13 | 13 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CKA-GE-MRQ-0001 | Operator Training Simulator, Historian and Performance Monitoring - Material Requisition | 13 | 13 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00CYA-GE-MRQ-0001 | Telecom, CCTV, Access Control and Perimeter Security - Material Requisition | 13 | 13 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGY-GE-MRQ-0001 | Fire Detection and Alarm System - Material Requisition | 13 | 13 | 4 | 10 | G-COM-MC-FF, G-COM-SC-FF, G-CON-CWP, G-CON-IWP, G-OPS-HO-FF, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-10HNE-ME-DSH-0001 | Stack 65 m with CEMS Platform and Silencer - Datasheet | 2 | 13 | 4 | 5 | G-CON-CWP, G-CON-IWP, G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-EL-CAL-0005 | Cathodic Protection Design | 1 | 12 | 3 | 7 | G-COM-SC-EL, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-EL-SLD-0002 | Construction Power Supply Single Line Diagram and RMU Design | 1 | 12 | 3 | 8 | G-CON-CWP, G-OPS-AB, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BBA-EL-MRQ-0001 | MV Switchgear 10.5 kV - Material Requisition | 12 | 12 | 3 | 10 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00BFT-EL-MRQ-0001 | LV Transformers - Material Requisition | 12 | 12 | 3 | 10 | G-COM-MC-EL, G-COM-SC-EL, G-CON-CWP, G-CON-IWP, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGB-ME-CAL-0001 | LDO Storage - Sizing and Hydraulic Calculation | 1 | 12 | 3 | 3 | G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-EL-CAL-0001 | Cable Sizing Calculation | 11 | 11 | 1 | 22 | G-CON-CWP, G-CON-IWP
ALP-EPC-00000-GE-SPC-0001 | Construction Power Supply - Technical Specification | 2 | 11 | 3 | 7 | G-CON-CWP, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-SPC-0003 | Welding, Heat Treatment and NDE Specification | 2 | 11 | 2 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00BXA-GE-SPC-0001 | Cathodic Protection - Technical Specification | 2 | 11 | 3 | 7 | G-COM-SC-EL, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGB-ME-DSH-0001 | LDO Storage: Tanks - Datasheet | 2 | 11 | 3 | 3 | G-OWN-TO, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-ME-PLN-0001 | Marine Operations Plan | 1 | 10 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-ME-SPC-0002 | Painting and Coating Specification | 1 | 10 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-ME-SPC-0003 | Insulation Specification | 1 | 10 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00UZF-CV-RPT-0001 | Temporary Barge Landing Design Report and Removal Plan | 1 | 10 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-10HNE-SS-MRQ-0001 | Stack 65 m with Silencer - Material Requisition | 9 | 10 | 2 | 4 | G-CON-CWP, G-CON-IWP, G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-CV-SPC-0003 | Piling Works - Technical Specification | 1 | 9 | 2 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-CV-SPC-0004 | Civil and Building Works - Technical Specification | 1 | 9 | 2 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-CV-SPC-0005 | Marine Works - Technical Specification | 1 | 9 | 2 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-GE-MRQ-0001 | Construction Power Supply - Material Requisition | 9 | 9 | 3 | 7 | G-CON-CWP, G-OWN-TO, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-PRC-0002 | Document Numbering and Document Control Procedure | 4 | 9 | 2 | 1 | G-OWN-TO
ALP-EPC-00000-GE-SPC-0002 | Electrical and I&C Installation - Technical Specification | 1 | 9 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-GE-SPC-0004 | Painting and Insulation - Technical Specification | 1 | 9 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-GE-SPC-0005 | Mechanical and Piping Erection - Technical Specification | 1 | 9 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-SS-SPC-0002 | Structural Steel Supply and Fabrication - Technical Specification | 1 | 9 | 2 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00BXA-GE-MRQ-0001 | Cathodic Protection - Material Requisition | 9 | 9 | 3 | 7 | G-COM-SC-EL, G-OPS-HO-EL, G-PRC-ENQ, G-PRC-FAB, G-PRC-FAT, G-PRC-PO, G-PRC-SHP
ALP-EPC-00UZF-GE-SPC-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Specification | 1 | 9 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-CV-MRQ-0001 | Piling Works - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-CV-MRQ-0002 | Civil and Building Works - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-CV-MRQ-0003 | Marine Works - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-GE-MRQ-0002 | Electrical and I&C Installation - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-GE-MRQ-0004 | Painting and Insulation - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-GE-MRQ-0005 | Mechanical and Piping Erection - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00000-SS-MRQ-0001 | Structural Steel Supply and Fabrication - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00EGB-ME-MRQ-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00UZF-GE-MRQ-0001 | Heavy Transport, Barge Landing and Marine Logistics - Material Requisition | 8 | 8 | 1 | 2 | G-PRC-ENQ, G-PRC-PO
ALP-EPC-00PAB-ME-CAL-0001 | CW Piping - Sizing and Hydraulic Calculation | 2 | 7 | 4 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00SGA-IC-CNR-0001 | Fire Water System - Control Narrative | 4 | 7 | 2 | 4 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF, G-OWN-TO
ALP-EPC-00UPA-PI-LAY-0001 | Marine Works - Equipment Layout | 4 | 7 | 3 | 3 | G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00000-EL-SPC-0001 | Power and Control Cable Specification | 1 | 6 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-SPC-0007 | GRP CW Pipes and Fittings - Technical Specification | 2 | 6 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGA-IC-CNR-0001 | LDO Unloading - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGB-IC-CNR-0001 | LDO Storage - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGC-IC-CNR-0001 | LDO Forwarding and Treatment - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EKA-IC-CNR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EKC-IC-CNR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00LBG-IC-CNR-0001 | Auxiliary Steam - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-00QCA-IC-CNR-0001 | Chemical Dosing - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QJA-IC-CNR-0001 | Nitrogen Supply - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QJB-IC-CNR-0001 | Hydrogen and CO2 Supply - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QUA-IC-CNR-0001 | Sampling and SWAS - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SAA-IC-CNR-0001 | HVAC - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGC-IC-CNR-0001 | Deluge, Spray and Foam Systems - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00UZC-CV-CVL-0001 | Site Drainage and Culverts - Civil Drawings | 6 | 6 | 3 | 14 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-10HAN-IC-CNR-0001 | HRSG Blowdown and Drains - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10HSB-IC-CNR-0001 | Ammonia Storage and Supply - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10LAB-IC-CNR-0001 | Feedwater Piping - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAC-IC-CNR-0001 | Boiler Feed Pumps - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAE-IC-CNR-0001 | HP Attemperation Spray Water - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAF-IC-CNR-0001 | Reheat Attemperation Spray Water - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBA-IC-CNR-0001 | Main Steam Piping - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBB-IC-CNR-0001 | Hot Reheat Piping - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBC-IC-CNR-0001 | Cold Reheat Piping - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBD-IC-CNR-0001 | LP Steam Piping - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20LCA-IC-CNR-0001 | Main Condensate Piping - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20LCB-IC-CNR-0001 | Condensate Extraction Pumps - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAN-IC-CNR-0001 | Turbine Bypass Stations and Piping - Control Narrative | 4 | 6 | 2 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-00000-EL-SPC-0004 | Power and Control Cables - Technical Specification | 1 | 5 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-EL-SPC-0005 | Cable Trays, Earthing and Lighting Materials - Technical Specification | 1 | 5 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-SPC-0003 | Instrument Installation Materials - Technical Specification | 1 | 5 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-SPC-0006 | Pipe Supports, Spring Hangers and Snubbers - Technical Specification | 1 | 5 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-SPC-0007 | Piping Specialty Items - Technical Specification | 1 | 5 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-SPC-0008 | Safety and Relief Valves - Technical Specification | 1 | 5 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-IC-SPC-0003 | Field Instruments - Technical Specification | 1 | 5 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-IC-SPC-0004 | Control Valves - Technical Specification | 1 | 5 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-SPC-0004 | Piping Bulk Materials - Technical Specification | 1 | 5 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-SPC-0005 | Alloy Piping P91 / P22 - Technical Specification | 1 | 5 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-SPC-0006 | Valves - Technical Specification | 1 | 5 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00GHA-IC-CNR-0001 | Demineralised Water Storage and Distribution - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GKA-IC-CNR-0001 | Potable Water - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GMA-IC-CNR-0001 | Process Drains and Waste Water Collection - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAA-IC-CNR-0001 | CW Intake, Screens and Outfall - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAB-IC-CNR-0001 | CW Piping - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAB-ME-DSH-0001 | CW Piping: Valves - Datasheet | 1 | 5 | 3 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00PAC-IC-CNR-0001 | CW Pumps - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAH-IC-CNR-0001 | Condenser Tube Cleaning - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PGA-IC-CNR-0001 | Closed Cooling Water - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QEA-IC-CNR-0001 | Compressed Air - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QHA-IC-CNR-0001 | Auxiliary Boiler - Control Narrative | 3 | 5 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-IEC-10MBY-IC-CNR-0001 | Power Island Operating and Control Description | 2 | 5 | 2 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-EL-MRQ-0001 | Power and Control Cables - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-EL-MRQ-0002 | Cable Trays, Earthing and Lighting Materials - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-MRQ-0003 | Instrument Installation Materials - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-MRQ-0006 | Pipe Supports, Spring Hangers and Snubbers - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-MRQ-0007 | Piping Specialty Items - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-MRQ-0008 | Safety and Relief Valves - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-GE-PRC-0001 | KKS Identification Manual | 1 | 4 | 2 | 1 | G-OWN-BDP
ALP-EPC-00000-IC-MRQ-0001 | Field Instruments - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-IC-MRQ-0002 | Control Valves - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-MRQ-0001 | Piping Bulk Materials - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-MRQ-0002 | Alloy Piping P91 / P22 - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-MRQ-0003 | Valves - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00000-PI-MRQ-0004 | GRP CW Pipes and Fittings - Material Requisition | 4 | 4 | 2 | 3 | G-PRC-ENQ, G-PRC-PO, G-PRC-SHP
ALP-EPC-00EGC-PI-STR-0001 | LDO Forwarding and Treatment - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00EKA-PI-STR-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00EKC-PI-STR-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00GBA-IC-CNR-0001 | Seawater Reverse Osmosis - Control Narrative | 2 | 4 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GCA-IC-CNR-0001 | Demineralisation - Control Narrative | 2 | 4 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GNA-IC-CNR-0001 | Waste Water Treatment - Control Narrative | 2 | 4 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GUA-IC-CNR-0001 | Sanitary Waste Water Treatment - Control Narrative | 2 | 4 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00LBG-PI-STR-0001 | Auxiliary Steam - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00LDA-IC-CNR-0001 | Condensate Polishing - Control Narrative | 2 | 4 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAB-PI-STR-0001 | CW Piping - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PBA-IC-CNR-0001 | Electro-Chlorination - Control Narrative | 2 | 4 | 2 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PGA-PI-STR-0001 | Closed Cooling Water - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00QHA-PI-STR-0001 | Auxiliary Boiler - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00SGA-PI-STR-0001 | Fire Water System - Pipe Stress Analysis | 2 | 4 | 1 | 6 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UAC-CV-ARC-0001 | GIS Building - Architectural Drawings | 4 | 4 | 4 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-CV-ARC-0001 | Electrical Building - Architectural Drawings | 4 | 4 | 4 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBF-CV-FND-0002 | Transformer Bays - Piling Layout and Pile Schedule | 1 | 4 | 2 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-CV-ARC-0001 | Control Building - Architectural Drawings | 4 | 4 | 4 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-CV-ARC-0001 | Water Treatment Building and Basins - Architectural Drawings | 4 | 4 | 4 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPA-CV-CAL-0002 | Marine Structures Design: Hydrodynamics, Scour and Rock Protection | 1 | 4 | 2 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-CV-FND-0002 | CW Pump House - Piling Layout and Pile Schedule | 1 | 4 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-CV-ARC-0001 | Workshop and Warehouse - Architectural Drawings | 4 | 4 | 4 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-CV-ARC-0001 | Administration Building - Architectural Drawings | 4 | 4 | 4 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-10HAN-PI-STR-0001 | HRSG Blowdown and Drains - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LAB-PI-STR-0001 | Feedwater Piping - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LAC-PI-STR-0001 | Boiler Feed Pumps - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LAE-PI-STR-0001 | HP Attemperation Spray Water - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LAF-PI-STR-0001 | Reheat Attemperation Spray Water - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LBA-PI-STR-0001 | Main Steam Piping - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LBB-PI-STR-0001 | Hot Reheat Piping - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LBC-PI-STR-0001 | Cold Reheat Piping - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LBD-PI-STR-0001 | LP Steam Piping - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10UHA-CV-FND-0002 | HRSG Foundations and Structures - Piling Layout and Pile Schedule | 1 | 4 | 2 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UHN-CV-FND-0002 | Stack Foundation - Piling Layout and Pile Schedule | 1 | 4 | 2 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-CV-FND-0001 | Gas Turbine Hall - Piling Layout and Pile Schedule | 1 | 4 | 2 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-20LCA-PI-STR-0001 | Main Condensate Piping - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-20LCB-PI-STR-0001 | Condensate Extraction Pumps - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-20MAN-PI-STR-0001 | Turbine Bypass Stations and Piping - Pipe Stress Analysis | 2 | 4 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-20UMB-CV-FND-0001 | Steam Turbine Hall - Piling Layout and Pile Schedule | 1 | 4 | 2 | 6 | G-CON-CWP, G-CON-IWP
ALP-IEC-10BAT-EL-GAD-0001 | Generator Step-Up Transformers - Supplier GA Drawings | 1 | 4 | 2 | 7 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-EPC-00000-GE-PLN-0001 | Engineering Execution Plan | 2 | 3 | 2 | 0
ALP-EPC-00000-HS-HAZ-0008 | Hazardous Area Classification Report and Drawings | 3 | 3 | 2 | 1 | G-OWN-TO
ALP-EPC-00000-PR-CAL-0001 | Performance Guarantee Calculation and Correction Curves | 2 | 3 | 2 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00EGA-PI-ISO-0001 | LDO Unloading - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00EGB-PI-ISO-0001 | LDO Storage - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00EGC-PI-ISO-0001 | LDO Forwarding and Treatment - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00EKA-PI-ISO-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00EKC-PI-ISO-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00GBA-PI-ISO-0001 | Seawater Reverse Osmosis - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00GCA-PI-ISO-0001 | Demineralisation - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00GHA-PI-ISO-0001 | Demineralised Water Storage and Distribution - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00GKA-PI-ISO-0001 | Potable Water - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00GMA-PI-ISO-0001 | Process Drains and Waste Water Collection - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00GNA-PI-ISO-0001 | Waste Water Treatment - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00GUA-PI-ISO-0001 | Sanitary Waste Water Treatment - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00LBG-PI-ISO-0001 | Auxiliary Steam - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00LDA-PI-ISO-0001 | Condensate Polishing - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PAA-PI-ISO-0001 | CW Intake, Screens and Outfall - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PAB-PI-ISO-0001 | CW Piping - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PAC-PI-ISO-0001 | CW Pumps - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PAH-PI-ISO-0001 | Condenser Tube Cleaning - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PBA-PI-ISO-0001 | Electro-Chlorination - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00PGA-PI-ISO-0001 | Closed Cooling Water - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00QCA-PI-ISO-0001 | Chemical Dosing - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00QEA-PI-ISO-0001 | Compressed Air - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00QHA-PI-ISO-0001 | Auxiliary Boiler - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00QJA-PI-ISO-0001 | Nitrogen Supply - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00QJB-PI-ISO-0001 | Hydrogen and CO2 Supply - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00QUA-PI-ISO-0001 | Sampling and SWAS - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00SGA-CM-CMP-0001 | Fire Water System - System Commissioning Procedure | 3 | 3 | 1 | 4 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF, G-OWN-TO
ALP-EPC-00SGA-PI-ISO-0001 | Fire Water System - Isometric Drawings | 2 | 3 | 1 | 6 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00SGC-PI-ISO-0001 | Deluge, Spray and Foam Systems - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UAC-CV-CAL-0001 | GIS Building - Structural and Foundation Calculation | 2 | 3 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-CV-FND-0001 | GIS Building - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-CV-CAL-0001 | Electrical Building - Structural and Foundation Calculation | 2 | 3 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-CV-FND-0001 | Electrical Building - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-PI-PPL-0001 | Electrical Building and Emergency Power - Piping General Arrangement | 2 | 3 | 2 | 6 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00UBF-CV-FND-0001 | Transformer Bays - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-CV-CAL-0001 | Control Building - Structural and Foundation Calculation | 2 | 3 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-CV-FND-0001 | LDO Tank Farm Structures - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-CV-ARC-0001 | Gas Station Structures - Architectural Drawings | 3 | 3 | 3 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-CV-FND-0001 | Gas Station Structures - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-CV-CAL-0001 | Water Treatment Building and Basins - Structural and Foundation Calculation | 2 | 3 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-CV-FND-0001 | Water Treatment Building and Basins - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPA-CV-CVL-0001 | CW Intake and Outfall Marine Structures - Civil Drawings | 3 | 3 | 2 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-CV-ARC-0001 | CW Pump House - Architectural Drawings | 3 | 3 | 3 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-CV-FND-0001 | CW Pump House - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-CV-ARC-0001 | Utility Building - Architectural Drawings | 3 | 3 | 3 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-CV-FND-0001 | Utility Building - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-CV-CAL-0001 | Workshop and Warehouse - Structural and Foundation Calculation | 2 | 3 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-CV-CAL-0001 | Administration Building - Structural and Foundation Calculation | 2 | 3 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZD-CV-CAL-0001 | Pipe Racks and Pipe Sleepers - Structural and Foundation Calculation | 1 | 3 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZF-CV-FND-0002 | Temporary Barge Landing - Piling Layout and Pile Schedule | 1 | 3 | 2 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10HAN-PI-ISO-0001 | HRSG Blowdown and Drains - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10HSB-PI-ISO-0001 | Ammonia Storage and Supply - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LAB-PI-ISO-0001 | Feedwater Piping - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LAC-PI-ISO-0001 | Boiler Feed Pumps - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LAE-PI-ISO-0001 | HP Attemperation Spray Water - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LAF-PI-ISO-0001 | Reheat Attemperation Spray Water - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LBA-PI-ISO-0001 | Main Steam Piping - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LBB-PI-ISO-0001 | Hot Reheat Piping - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LBC-PI-ISO-0001 | Cold Reheat Piping - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10LBD-PI-ISO-0001 | LP Steam Piping - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-10UHA-CV-FND-0001 | HRSG Foundations and Structures - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UHN-CV-FND-0001 | Stack Foundation - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-CV-ARC-0001 | Gas Turbine Hall - Architectural Drawings | 3 | 3 | 3 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-CV-FND-0002 | Gas Turbine Hall - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-20LCA-PI-ISO-0001 | Main Condensate Piping - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-20LCB-PI-ISO-0001 | Condensate Extraction Pumps - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-20MAN-PI-ISO-0001 | Turbine Bypass Stations and Piping - Isometric Drawings | 2 | 3 | 1 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-20UMB-CV-ARC-0001 | Steam Turbine Hall - Architectural Drawings | 3 | 3 | 3 | 6 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-CV-FND-0002 | Steam Turbine Hall - Foundation and Underground Drawings | 3 | 3 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-IEC-10MBA-HS-RPT-0001 | Power Island Noise Data | 1 | 3 | 2 | 2 | G-OWN-TO, G-OWN-TOC
ALP-IEC-10MKA-EL-DSH-0001 | Generators, Excitation, GCB and Busducts - Supplier Certified Datasheets and Performance Curves | 1 | 3 | 2 | 3 | G-OWN-TO, G-OWN-TOC, G-PRC-FAB
ALP-EPC-00000-EL-STU-0002 | Protection Coordination Study and Relay Settings | 2 | 2 | 1 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-OWN-TO
ALP-EPC-00000-EL-STU-0006 | Grid Code Compliance and Reactive Capability Study | 1 | 2 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-HS-STU-0001 | Noise Study | 1 | 2 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-IC-CNR-0001 | Unit Coordination, Load Control, Export Limiter and Fuel Transfer | 1 | 2 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00ACA-CM-CMP-0001 | 380 kV GIS Switchyard - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BBA-CM-CMP-0001 | MV Switchgear 10.5 kV - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BFA-CM-CMP-0001 | LV Switchgear 0.4 kV - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BFT-CM-CMP-0001 | LV Transformers - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BLA-CM-CMP-0001 | Lighting and Small Power - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BMA-CM-CMP-0001 | Emergency LV Switchgear - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BRA-CM-CMP-0001 | UPS - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BTA-CM-CMP-0001 | Batteries and DC 220 V - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00CJA-CM-CMP-0001 | Plant DCS - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CJG-CM-CMP-0001 | Safety Instrumented Systems - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CKA-CM-CMP-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CQA-CM-CMP-0001 | Continuous Emission Monitoring - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CYA-CM-CMP-0001 | Telecom, CCTV, Access Control, Security - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGA-CM-CMP-0001 | LDO Unloading - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGB-CM-CMP-0001 | LDO Storage - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGC-CM-CMP-0001 | LDO Forwarding and Treatment - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EKA-CM-CMP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EKC-CM-CMP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GBA-CM-CMP-0001 | Seawater Reverse Osmosis - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GCA-CM-CMP-0001 | Demineralisation - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GHA-CM-CMP-0001 | Demineralised Water Storage and Distribution - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GKA-CM-CMP-0001 | Potable Water - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GMA-CM-CMP-0001 | Process Drains and Waste Water Collection - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GNA-CM-CMP-0001 | Waste Water Treatment - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GUA-CM-CMP-0001 | Sanitary Waste Water Treatment - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00LBG-CM-CMP-0001 | Auxiliary Steam - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-00LDA-CM-CMP-0001 | Condensate Polishing - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAA-CM-CMP-0001 | CW Intake, Screens and Outfall - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAB-CM-CMP-0001 | CW Piping - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAC-CM-CMP-0001 | CW Pumps - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAH-CM-CMP-0001 | Condenser Tube Cleaning - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PBA-CM-CMP-0001 | Electro-Chlorination - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PGA-CM-CMP-0001 | Closed Cooling Water - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QCA-CM-CMP-0001 | Chemical Dosing - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QEA-CM-CMP-0001 | Compressed Air - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QHA-CM-CMP-0001 | Auxiliary Boiler - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QJA-CM-CMP-0001 | Nitrogen Supply - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QJB-CM-CMP-0001 | Hydrogen and CO2 Supply - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QUA-CM-CMP-0001 | Sampling and SWAS - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SAA-CM-CMP-0001 | HVAC - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGC-CM-CMP-0001 | Deluge, Spray and Foam Systems - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGY-CM-CMP-0001 | Fire Detection and Alarm - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00UAC-EL-ELY-0001 | 380 kV GIS Switchyard - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-EL-ELY-0001 | Electrical Building and Emergency Power - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBF-CV-CAL-0001 | Transformer Bays - Structural and Foundation Calculation | 1 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-CV-FND-0001 | Control Building - Foundation and Underground Drawings | 2 | 2 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-EL-ELY-0001 | Control, Administration and Workshop Buildings - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-CV-CAL-0001 | LDO Tank Farm Structures - Structural and Foundation Calculation | 1 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-EL-ELY-0001 | LDO Tank Farm and Unloading - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-CV-CAL-0001 | Gas Station Structures - Structural and Foundation Calculation | 1 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-EL-ELY-0001 | Fuel Gas Station - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-EL-ELY-0001 | Water Treatment and Effluents - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-CV-CAL-0001 | CW Pump House - Structural and Foundation Calculation | 1 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-EL-ELY-0001 | CW Pump House and Onshore CW - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-CV-CAL-0001 | Utility Building - Structural and Foundation Calculation | 1 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-EL-ELY-0001 | BOP Utilities - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-CV-FND-0001 | Workshop and Warehouse - Foundation and Underground Drawings | 2 | 2 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-CV-FND-0001 | Administration Building - Foundation and Underground Drawings | 2 | 2 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-EL-ELY-0001 | Site-Wide Infrastructure - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZD-CV-FND-0001 | Pipe Racks and Pipe Sleepers - Foundation and Underground Drawings | 2 | 2 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Structure Drawings | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZE-CV-CVL-0001 | Cable Trenches and Duct Banks - Civil Drawings | 2 | 2 | 2 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZF-CV-CAL-0001 | Temporary Barge Landing - Structural and Foundation Calculation | 1 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZF-CV-FND-0001 | Temporary Barge Landing - Foundation and Underground Drawings | 2 | 2 | 2 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00XJA-CM-CMP-0001 | Emergency Diesel Generator - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-10BBT-CM-CMP-0001 | GT Unit Auxiliary Transformer - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-10HAN-CM-CMP-0001 | HRSG Blowdown and Drains - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10HSB-CM-CMP-0001 | Ammonia Storage and Supply - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10LAB-CM-CMP-0001 | Feedwater Piping - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAC-CM-CMP-0001 | Boiler Feed Pumps - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAE-CM-CMP-0001 | HP Attemperation Spray Water - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAF-CM-CMP-0001 | Reheat Attemperation Spray Water - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBA-CM-CMP-0001 | Main Steam Piping - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBB-CM-CMP-0001 | Hot Reheat Piping - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBC-CM-CMP-0001 | Cold Reheat Piping - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBD-CM-CMP-0001 | LP Steam Piping - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10UMA-CV-CAL-0001 | Gas Turbine Hall - Structural and Foundation Calculation | 1 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-EL-ELY-0001 | Power Block - GT and HRSG - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20BBT-CM-CMP-0001 | ST Unit Auxiliary Transformer - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-20LCA-CM-CMP-0001 | Main Condensate Piping - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20LCB-CM-CMP-0001 | Condensate Extraction Pumps - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAN-CM-CMP-0001 | Turbine Bypass Stations and Piping - System Commissioning Procedure | 2 | 2 | 1 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20UMB-CV-CAL-0001 | Steam Turbine Hall - Structural and Foundation Calculation | 1 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-EL-ELY-0001 | Power Block - ST and Condenser - Electrical Layouts | 2 | 2 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-IEC-00000-GE-LST-0001 | Power Island - Terminal Points and Interface Data | 1 | 2 | 1 | 1 | G-OWN-TO
ALP-IEC-10MBA-PR-HMB-0001 | Power Island Thermal Performance Data | 1 | 2 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-IEC-10MBY-IC-CBL-0001 | Power Island Cable List | 2 | 2 | 1 | 6 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-IEC-10MKA-CV-CAL-0001 | Generators, Excitation, GCB and Busducts - Supplier Foundation Loads and Anchor Bolt Drawings | 2 | 2 | 1 | 5 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-IEC-10MKA-EL-RPT-0001 | Generator Capability Curves and Dynamic Models | 1 | 2 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-M21-00SMA-CV-CAL-0001 | EOT Cranes - Supplier Foundation Loads and Anchor Bolt Drawings | 2 | 2 | 1 | 5 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E01-00ACA-CV-CAL-0001 | 380 kV GIS - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E02-10BBT-CV-CAL-0001 | Unit Auxiliary Transformers - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E06-00XJA-CV-CAL-0001 | Emergency Diesel Generator - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-EPC-00000-CM-CMP-0001 | Steam Blowing and Chemical Cleaning Procedure | 1 | 1 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-CM-CMP-0002 | Performance Test Procedure | 1 | 1 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-CM-CMP-0003 | Grid Code Compliance Test Programme | 1 | 1 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-CM-CMP-0004 | Operational Demonstration and Reliability Run Procedure | 1 | 1 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-CM-CMP-0005 | Tests on LDO Procedure | 1 | 1 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-CM-CMP-0006 | Emission and Noise Test Procedure | 1 | 1 | 1 | 2 | G-OWN-TO, G-OWN-TOC
ALP-EPC-00000-CM-LST-0002 | Commissioning and Two-Year Operating Spares List | 1 | 1 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-CM-PLN-0002 | Training Plan | 1 | 1 | 1 | 0
ALP-EPC-00000-CM-PRC-0001 | Punch List and Completion Procedure | 1 | 1 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-CV-TST-0001 | Pile Load Test Procedure | 1 | 1 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-EL-SPC-0003 | Revenue Metering and TSO SCADA Interface Specification | 1 | 1 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-GE-LST-0003 | Tie-in and Terminal Point Register | 1 | 1 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-GE-MDL-0001 | Master Document List | 1 | 1 | 1 | 0
ALP-EPC-00000-GE-PLN-0002 | Advanced Work Packaging Execution Plan | 1 | 1 | 1 | 0
ALP-EPC-00000-GE-PLN-0003 | Project Quality Plan | 1 | 1 | 1 | 0
ALP-EPC-00000-GE-PRC-0003 | As-Built Documentation and Engineering Database Handover Procedure | 1 | 1 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-HS-HAZ-0001 | HAZID Report | 1 | 1 | 1 | 0
ALP-EPC-00000-HS-HAZ-0010 | Major Accident Assessment and QRA | 1 | 1 | 1 | 0
ALP-EPC-00000-HS-PLN-0001 | HSE in Design Plan and Safety-in-Design Register | 1 | 1 | 1 | 0
ALP-EPC-00000-IC-TST-0002 | OT Cybersecurity Acceptance Test Procedure | 1 | 1 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-PI-M3D-0003 | 90 % 3D Model Review Report | 1 | 1 | 1 | 1 | G-OPS-AB
ALP-EPC-00000-PR-STU-0001 | Plant Water Balance | 1 | 1 | 1 | 1 | G-OWN-TO
ALP-EPC-00000-PR-STU-0002 | Reliability, Availability and Maintainability Study | 1 | 1 | 1 | 0
ALP-EPC-00BBA-EL-SLD-0001 | MV Switchgear 10.5 kV - Single Line Diagram | 1 | 1 | 1 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00BXA-CM-CMP-0001 | Earthing and Lightning Protection - System Commissioning Procedure | 1 | 1 | 1 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00SAA-PI-ISO-0001 | HVAC - Isometric Drawings | 1 | 1 | 1 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-OPS-AB
ALP-EPC-00SMA-CM-CMP-0001 | Cranes and Hoists - System Commissioning Procedure | 1 | 1 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00UAC-IC-ELY-0002 | 380 kV GIS Switchyard - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-SS-STL-0002 | GIS Building - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-IC-ELY-0002 | Electrical Building and Emergency Power - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-SS-STL-0002 | Electrical Building - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBF-SS-STL-0001 | Transformer Bays - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-IC-ELY-0001 | Control, Administration and Workshop Buildings - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-PI-PPL-0001 | Control, Administration and Workshop Buildings - Piping General Arrangement | 1 | 1 | 1 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-SS-STL-0002 | Control Building - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-IC-ELY-0001 | LDO Tank Farm and Unloading - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-IC-ELY-0001 | Fuel Gas Station - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-SS-STL-0001 | Gas Station Structures - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-IC-ELY-0001 | Water Treatment and Effluents - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-SS-STL-0002 | Water Treatment Building and Basins - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-IC-ELY-0001 | CW Pump House and Onshore CW - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-SS-STL-0001 | CW Pump House - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-IC-ELY-0001 | BOP Utilities - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-SS-STL-0001 | Utility Building - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-SS-STL-0002 | Workshop and Warehouse - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-SS-STL-0002 | Administration Building - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-CV-CVL-0002 | Roads and Paving - Civil Drawings | 1 | 1 | 1 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-IC-ELY-0001 | Site-Wide Infrastructure - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZB-CV-CVL-0001 | Fencing and Gates - Civil Drawings | 1 | 1 | 1 | 4 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10HNE-CM-CMP-0001 | Stack 65 m with CEMS Platform and Silencer - System Commissioning Procedure | 1 | 1 | 1 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10UMA-IC-ELY-0001 | Power Block - GT and HRSG - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-IC-ELY-0001 | Power Block - ST and Condenser - Instrument Location and I&C Cable Routing | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Structure Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-IEC-10BAT-CV-CAL-0001 | Generator Step-Up Transformers - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M01-10LAC-CV-CAL-0001 | Boiler Feed Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M02-20LCB-CV-CAL-0001 | Condensate Extraction Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M03-00PAC-CV-CAL-0001 | CW Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M04-00PAA-CV-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M05-00PBA-CV-CAL-0001 | Electro-Chlorination Package - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M07-00PGA-CV-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M08-00QEA-CV-CAL-0001 | Air Compressors and Dryers - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M09-00QHA-CV-CAL-0001 | Auxiliary Boiler - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M12-00GBA-CV-CAL-0001 | Water Treatment Package - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M13-00GHA-CV-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M14-00GNA-CV-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M15-00EKA-CV-CAL-0001 | Gas Receiving and Metering Station - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M16-00EGA-CV-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M18-10HSB-CV-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M19-10HAN-CV-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M20-00SGA-CV-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 3 | G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-S02-10HNE-CV-CAL-0001 | Stack 65 m with Silencer - Supplier Foundation Loads and Anchor Bolt Drawings | 1 | 1 | 1 | 2 | G-CON-CWP, G-CON-IWP
ALP-E01-00ACA-EL-WIR-0001 | 380 kV GIS - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-E01-00ACA-ME-CAL-0001 | 380 kV GIS - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E01-00ACA-ME-DSH-0001 | 380 kV GIS - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E01-00ACA-ME-GAD-0001 | 380 kV GIS - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E01-00ACA-ME-ITP-0001 | 380 kV GIS - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E01-00ACA-ME-MDB-0001 | 380 kV GIS - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E01-00ACA-ME-OMM-0001 | 380 kV GIS - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-E01-00ACA-ME-PRC-0001 | 380 kV GIS - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-E01-00ACA-ME-TRP-0001 | 380 kV GIS - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E01-00ACA-ME-TST-0001 | 380 kV GIS - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-E02-10BBT-EL-WIR-0001 | Unit Auxiliary Transformers - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-E02-10BBT-ME-CAL-0001 | Unit Auxiliary Transformers - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E02-10BBT-ME-DSH-0001 | Unit Auxiliary Transformers - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E02-10BBT-ME-GAD-0001 | Unit Auxiliary Transformers - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E02-10BBT-ME-ITP-0001 | Unit Auxiliary Transformers - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E02-10BBT-ME-MDB-0001 | Unit Auxiliary Transformers - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E02-10BBT-ME-OMM-0001 | Unit Auxiliary Transformers - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-EL, G-OPS-HO-EL
ALP-E02-10BBT-ME-PRC-0001 | Unit Auxiliary Transformers - Supplier Installation and Erection Manual | 0 | 0 | 0 | 2 | G-CON-CWP
ALP-E02-10BBT-ME-TRP-0001 | Unit Auxiliary Transformers - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E02-10BBT-ME-TST-0001 | Unit Auxiliary Transformers - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-E03-00BBA-ME-CAL-0001 | MV Switchgear 10.5 kV - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E03-00BBA-ME-DSH-0001 | MV Switchgear 10.5 kV - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E03-00BBA-ME-GAD-0001 | MV Switchgear 10.5 kV - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E03-00BBA-ME-ITP-0001 | MV Switchgear 10.5 kV - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E03-00BBA-ME-MDB-0001 | MV Switchgear 10.5 kV - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E03-00BBA-ME-OMM-0001 | MV Switchgear 10.5 kV - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-E03-00BBA-ME-PRC-0001 | MV Switchgear 10.5 kV - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-E03-00BBA-ME-TRP-0001 | MV Switchgear 10.5 kV - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E03-00BBA-ME-TST-0001 | MV Switchgear 10.5 kV - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-E04-00BFT-ME-CAL-0001 | LV Transformers - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E04-00BFT-ME-DSH-0001 | LV Transformers - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E04-00BFT-ME-GAD-0001 | LV Transformers - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E04-00BFT-ME-ITP-0001 | LV Transformers - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E04-00BFT-ME-MDB-0001 | LV Transformers - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E04-00BFT-ME-OMM-0001 | LV Transformers - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-E04-00BFT-ME-PRC-0001 | LV Transformers - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-E04-00BFT-ME-TRP-0001 | LV Transformers - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E04-00BFT-ME-TST-0001 | LV Transformers - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-E05-00BFA-EL-WIR-0001 | LV Switchboards and MCCs - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-E05-00BFA-ME-CAL-0001 | LV Switchboards and MCCs - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E05-00BFA-ME-DSH-0001 | LV Switchboards and MCCs - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E05-00BFA-ME-GAD-0001 | LV Switchboards and MCCs - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E05-00BFA-ME-ITP-0001 | LV Switchboards and MCCs - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E05-00BFA-ME-MDB-0001 | LV Switchboards and MCCs - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E05-00BFA-ME-OMM-0001 | LV Switchboards and MCCs - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-EL, G-OPS-HO-EL
ALP-E05-00BFA-ME-PRC-0001 | LV Switchboards and MCCs - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-E05-00BFA-ME-TRP-0001 | LV Switchboards and MCCs - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E05-00BFA-ME-TST-0001 | LV Switchboards and MCCs - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-E06-00XJA-EL-WIR-0001 | Emergency Diesel Generator - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-E06-00XJA-ME-CAL-0001 | Emergency Diesel Generator - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E06-00XJA-ME-DSH-0001 | Emergency Diesel Generator - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E06-00XJA-ME-GAD-0001 | Emergency Diesel Generator - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E06-00XJA-ME-ITP-0001 | Emergency Diesel Generator - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E06-00XJA-ME-MDB-0001 | Emergency Diesel Generator - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E06-00XJA-ME-OMM-0001 | Emergency Diesel Generator - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-E06-00XJA-ME-PRC-0001 | Emergency Diesel Generator - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-E06-00XJA-ME-TRP-0001 | Emergency Diesel Generator - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E06-00XJA-ME-TST-0001 | Emergency Diesel Generator - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-E07-00BRA-EL-WIR-0001 | UPS, Batteries and DC Systems - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-E07-00BRA-ME-CAL-0001 | UPS, Batteries and DC Systems - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E07-00BRA-ME-DSH-0001 | UPS, Batteries and DC Systems - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E07-00BRA-ME-GAD-0001 | UPS, Batteries and DC Systems - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-E07-00BRA-ME-ITP-0001 | UPS, Batteries and DC Systems - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E07-00BRA-ME-MDB-0001 | UPS, Batteries and DC Systems - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E07-00BRA-ME-OMM-0001 | UPS, Batteries and DC Systems - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-EL, G-OPS-HO-EL
ALP-E07-00BRA-ME-PRC-0001 | UPS, Batteries and DC Systems - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-E07-00BRA-ME-TRP-0001 | UPS, Batteries and DC Systems - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E07-00BRA-ME-TST-0001 | UPS, Batteries and DC Systems - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-E08-00000-ME-MDB-0001 | Power and Control Cables - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E09-00BLA-ME-MDB-0001 | Cable Trays, Earthing and Lighting Materials - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E10-00BXA-ME-ITP-0001 | Cathodic Protection - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E10-00BXA-ME-MDB-0001 | Cathodic Protection - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E10-00BXA-ME-OMM-0001 | Cathodic Protection - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-E10-00BXA-ME-TRP-0001 | Cathodic Protection - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E10-00BXA-ME-TST-0001 | Cathodic Protection - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-E11-00000-ME-ITP-0001 | Construction Power Supply - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-E11-00000-ME-LST-0001 | Construction Power Supply - Spare Parts and Special Tools Lists | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-E11-00000-ME-MDB-0001 | Construction Power Supply - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-E11-00000-ME-PRC-0001 | Construction Power Supply - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-E11-00000-ME-TRP-0001 | Construction Power Supply - Factory Acceptance Test Report | 0 | 0 | 0 | 2 | G-OWN-TO, G-PRC-SHP
ALP-E11-00000-ME-TST-0001 | Construction Power Supply - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-EPC-00000-CM-LST-0001 | Commissioning Systems and Turnover Boundaries List | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-LST-0003 | Punch List at Taking-Over | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-LST-0004 | Special Tools List | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-OMM-0001 | Plant Operation and Maintenance Manual | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-TRP-0001 | Steam Blowing and Chemical Cleaning Report | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-TRP-0002 | Performance Test Report incl. Uncertainty Analysis | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-TRP-0003 | Grid Code Compliance Test Report | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-TRP-0004 | Operational Demonstration and Reliability Run Report | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-TRP-0005 | Tests on LDO Report | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-TRP-0006 | Emission Test and Noise Survey Reports | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CM-TRP-0007 | Fire Protection System Test Certificates | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-CV-TRP-0001 | Pile Load Test Report and Pile Design Confirmation | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-EL-LST-0003 | Protection Relay Settings List | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-EL-LST-0004 | Hazardous Area Electrical Equipment Register | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-EL-TRP-0001 | Revenue Metering and TSO SCADA Interface Test Report | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-GE-ITP-0001 | Construction Power Supply - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-LST-0001 | Codes, Standards and Regulations Register | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-GE-LST-0002 | Permits and Authorities Register | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-GE-LST-0004 | Variation and Change Register | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-GE-LST-0005 | As-Built Documentation Index | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-GE-RPT-0001 | Piling Works - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0002 | Civil and Building Works - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0003 | Power and Control Cables - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0004 | Construction Power Supply - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0005 | Electrical and I&C Installation - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0006 | Field Instruments - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0007 | Control Valves - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0008 | Instrument Installation Materials - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0009 | Painting and Insulation - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0010 | Mechanical and Piping Erection - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0011 | Piping Bulk Materials - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0012 | Valves - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0013 | Pipe Supports, Spring Hangers and Snubbers - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0014 | Piping Specialty Items - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0015 | Safety and Relief Valves - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-GE-RPT-0016 | Structural Steel Supply and Fabrication - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00000-IC-LST-0002 | Alarm List | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-IC-LST-0003 | Interlock and Trip List | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-IC-TRP-0001 | OT Cybersecurity Acceptance Test Report | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-ME-LST-0001 | Heavy and Oversized Piece List | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-PI-LST-0001 | Valve List | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-PI-M3D-0004 | Plant 3D Model and IFC4 Export - As-Built | 0 | 0 | 0 | 1 | G-OPS-AB
ALP-EPC-00000-PR-LST-0002 | Line List | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00000-PR-LST-0003 | Chemical Consumption, Effluent and Emission Inventory | 0 | 0 | 0 | 1 | G-OWN-TO
ALP-EPC-00ACA-CM-MDB-0001 | 380 kV GIS Switchyard - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00ACA-CM-OMM-0001 | 380 kV GIS Switchyard - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00ACA-EL-ITP-0001 | 380 kV GIS - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00ACA-EL-SLD-0001 | 380 kV GIS Switchyard - Single Line Diagram | 0 | 0 | 0 | 1 | G-OPS-AB
ALP-EPC-00ACA-GE-RPT-0001 | 380 kV GIS - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BBA-CM-MDB-0001 | MV Switchgear 10.5 kV - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BBA-CM-OMM-0001 | MV Switchgear 10.5 kV - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BBA-EL-ITP-0001 | MV Switchgear 10.5 kV - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BBA-EL-WIR-0001 | MV Schematic and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BBA-GE-RPT-0001 | MV Switchgear 10.5 kV - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BFA-CM-MDB-0001 | LV Switchgear 0.4 kV - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BFA-CM-OMM-0001 | LV Switchgear 0.4 kV - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BFA-EL-ITP-0001 | LV Switchboards and MCCs - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BFA-EL-WIR-0001 | LV Schematic and Wiring Diagrams, Part 1 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0002 | LV Schematic and Wiring Diagrams, Part 10 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0003 | LV Schematic and Wiring Diagrams, Part 11 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0004 | LV Schematic and Wiring Diagrams, Part 12 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0005 | LV Schematic and Wiring Diagrams, Part 13 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0006 | LV Schematic and Wiring Diagrams, Part 2 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0007 | LV Schematic and Wiring Diagrams, Part 3 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0008 | LV Schematic and Wiring Diagrams, Part 4 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0009 | LV Schematic and Wiring Diagrams, Part 5 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0010 | LV Schematic and Wiring Diagrams, Part 6 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0011 | LV Schematic and Wiring Diagrams, Part 7 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0012 | LV Schematic and Wiring Diagrams, Part 8 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-EL-WIR-0013 | LV Schematic and Wiring Diagrams, Part 9 of 13 | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-EPC-00BFA-GE-RPT-0001 | LV Switchboards and MCCs - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BFT-CM-MDB-0001 | LV Transformers - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BFT-CM-OMM-0001 | LV Transformers - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BFT-EL-ITP-0001 | LV Transformers - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BFT-GE-RPT-0001 | LV Transformers - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BLA-CM-MDB-0001 | Lighting and Small Power - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BLA-CM-OMM-0001 | Lighting and Small Power - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BLA-EL-SLD-0001 | Lighting and Small Power - Single Line Diagram | 0 | 0 | 0 | 1 | G-OPS-AB
ALP-EPC-00BLA-GE-RPT-0001 | Cable Trays, Earthing and Lighting Materials - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BMA-CM-MDB-0001 | Emergency LV Switchgear - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BMA-CM-OMM-0001 | Emergency LV Switchgear - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BMA-EL-SLD-0001 | Emergency LV Switchgear - Single Line Diagram | 0 | 0 | 0 | 1 | G-OPS-AB
ALP-EPC-00BRA-CM-MDB-0001 | UPS - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BRA-CM-OMM-0001 | UPS - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BRA-EL-ITP-0001 | UPS, Batteries and DC Systems - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BRA-EL-SLD-0001 | UPS - Single Line Diagram | 0 | 0 | 0 | 1 | G-OPS-AB
ALP-EPC-00BRA-GE-RPT-0001 | UPS, Batteries and DC Systems - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BTA-CM-MDB-0001 | Batteries and DC 220 V - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BTA-CM-OMM-0001 | Batteries and DC 220 V - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BXA-CM-MDB-0001 | Earthing and Lightning Protection - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00BXA-GE-ITP-0001 | Cathodic Protection - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00BXA-GE-RPT-0001 | Cathodic Protection - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CJA-CM-MDB-0001 | Plant DCS - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CJA-CM-OMM-0001 | Plant DCS - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CJA-GE-RPT-0001 | Plant DCS - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CJA-IC-ITP-0001 | Plant DCS - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CJG-CM-MDB-0001 | Safety Instrumented Systems - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CJG-CM-OMM-0001 | Safety Instrumented Systems - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CJG-GE-ITP-0001 | BOP Safety Instrumented System - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CJG-GE-RPT-0001 | BOP Safety Instrumented System - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CKA-CM-MDB-0001 | Historian, Performance Monitoring and Operator Training Simulator - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CKA-CM-OMM-0001 | Historian, Performance Monitoring and Operator Training Simulator - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CKA-GE-ITP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CKA-GE-RPT-0001 | Operator Training Simulator, Historian and Performance Monitoring - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CQA-CM-MDB-0001 | Continuous Emission Monitoring - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CQA-CM-OMM-0001 | Continuous Emission Monitoring - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CQA-GE-RPT-0001 | Continuous Emission Monitoring System - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CQA-IC-ITP-0001 | Continuous Emission Monitoring System - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CYA-CM-MDB-0001 | Telecom, CCTV, Access Control, Security - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CYA-CM-OMM-0001 | Telecom, CCTV, Access Control, Security - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00CYA-GE-ITP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00CYA-GE-RPT-0001 | Telecom, CCTV, Access Control and Perimeter Security - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00EGA-CM-MDB-0001 | LDO Unloading - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGA-CM-OMM-0001 | LDO Unloading - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGA-GE-RPT-0001 | LDO Unloading and Forwarding / Treatment Skids - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00EGA-ME-ITP-0001 | LDO Unloading and Forwarding / Treatment Skids - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00EGA-PI-SUP-0001 | LDO Unloading - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00EGB-CM-MDB-0001 | LDO Storage - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGB-CM-OMM-0001 | LDO Storage - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGB-GE-RPT-0001 | Field-Erected Storage Tanks: LDO Storage and Fire Water - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00EGB-PI-SUP-0001 | LDO Storage - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00EGC-CM-MDB-0001 | LDO Forwarding and Treatment - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGC-CM-OMM-0001 | LDO Forwarding and Treatment - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EGC-PI-SUP-0001 | LDO Forwarding and Treatment - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00EKA-CM-MDB-0001 | Gas Receiving, Filtration and Fiscal Metering Station - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EKA-CM-OMM-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EKA-GE-RPT-0001 | Gas Receiving and Metering Station - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00EKA-ME-ITP-0001 | Gas Receiving and Metering Station - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00EKA-PI-SUP-0001 | Gas Receiving, Filtration and Fiscal Metering Station - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00EKC-CM-MDB-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EKC-CM-OMM-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00EKC-PI-SUP-0001 | Fuel Gas Distribution to GT and Auxiliary Boiler - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GBA-CM-MDB-0001 | Seawater Reverse Osmosis - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GBA-CM-OMM-0001 | Seawater Reverse Osmosis - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GBA-GE-RPT-0001 | Water Treatment Package - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00GBA-PI-SUP-0001 | Seawater Reverse Osmosis - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GCA-CM-MDB-0001 | Demineralisation - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GCA-CM-OMM-0001 | Demineralisation - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GCA-PI-SUP-0001 | Demineralisation - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GHA-CM-MDB-0001 | Demineralised Water Storage and Distribution - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GHA-CM-OMM-0001 | Demineralised Water Storage and Distribution - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GHA-GE-RPT-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00GHA-ME-ITP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00GHA-PI-SUP-0001 | Demineralised Water Storage and Distribution - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GKA-CM-MDB-0001 | Potable Water - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GKA-CM-OMM-0001 | Potable Water - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GKA-PI-PPL-0001 | Potable Water - Underground Piping Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GKA-PI-SUP-0001 | Potable Water - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GMA-CM-MDB-0001 | Process Drains and Waste Water Collection - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GMA-CM-OMM-0001 | Process Drains and Waste Water Collection - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GMA-PI-PPL-0001 | Process Drains and Waste Water Collection - Underground Piping Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GMA-PI-SUP-0001 | Process Drains and Waste Water Collection - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GNA-CM-MDB-0001 | Waste Water Treatment - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GNA-CM-OMM-0001 | Waste Water Treatment - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GNA-GE-RPT-0001 | Waste Water and Sanitary Treatment Packages - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00GNA-ME-ITP-0001 | Waste Water and Sanitary Treatment Packages - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00GNA-PI-SUP-0001 | Waste Water Treatment - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00GUA-CM-MDB-0001 | Sanitary Waste Water Treatment - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GUA-CM-OMM-0001 | Sanitary Waste Water Treatment - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00GUA-PI-SUP-0001 | Sanitary Waste Water Treatment - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00LBG-CM-MDB-0001 | Auxiliary Steam - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-00LBG-CM-OMM-0001 | Auxiliary Steam - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-00LBG-PI-SUP-0001 | Auxiliary Steam - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-00LDA-CM-MDB-0001 | Condensate Polishing - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00LDA-CM-OMM-0001 | Condensate Polishing - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00LDA-ME-ITP-0001 | Water Treatment Package - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00LDA-PI-SUP-0001 | Condensate Polishing - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00PAA-CM-MDB-0001 | CW Intake, Screens and Outfall - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAA-CM-OMM-0001 | CW Intake, Screens and Outfall - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAA-GE-RPT-0001 | Travelling Band Screens and Trash Rakes - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PAA-ME-ITP-0001 | Travelling Band Screens and Trash Rakes - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PAA-PI-SUP-0001 | CW Intake, Screens and Outfall - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00PAB-CM-MDB-0001 | CW Piping - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAB-CM-OMM-0001 | CW Piping - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAB-GE-RPT-0001 | GRP CW Pipes and Fittings - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PAB-PI-PPL-0001 | CW Piping - Underground Piping Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00PAB-PI-SUP-0001 | CW Piping - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00PAC-CM-MDB-0001 | CW Pumps - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAC-CM-OMM-0001 | CW Pumps - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAC-GE-RPT-0001 | CW Pumps - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PAC-ME-ITP-0001 | CW Pumps - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PAC-PI-SUP-0001 | CW Pumps - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00PAH-CM-MDB-0001 | Condenser Tube Cleaning - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAH-CM-OMM-0001 | Condenser Tube Cleaning - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PAH-GE-RPT-0001 | Condenser Tube Cleaning System - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PAH-ME-ITP-0001 | Condenser Tube Cleaning System - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PAH-PI-SUP-0001 | Condenser Tube Cleaning - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00PBA-CM-MDB-0001 | Electro-Chlorination - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PBA-CM-OMM-0001 | Electro-Chlorination - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PBA-GE-RPT-0001 | Electro-Chlorination Package - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PBA-ME-ITP-0001 | Electro-Chlorination Package - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PBA-PI-SUP-0001 | Electro-Chlorination - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00PGA-CM-MDB-0001 | Closed Cooling Water - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PGA-CM-OMM-0001 | Closed Cooling Water - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00PGA-GE-RPT-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PGA-ME-ITP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00PGA-PI-SUP-0001 | Closed Cooling Water - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00QCA-CM-MDB-0001 | Chemical Dosing - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QCA-CM-OMM-0001 | Chemical Dosing - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QCA-GE-RPT-0001 | Chemical Dosing Skid - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QCA-ME-ITP-0001 | Chemical Dosing Skid - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QCA-PI-SUP-0001 | Chemical Dosing - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00QEA-CM-MDB-0001 | Compressed Air - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QEA-CM-OMM-0001 | Compressed Air - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QEA-GE-RPT-0001 | Air Compressors and Dryers - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QEA-ME-ITP-0001 | Air Compressors and Dryers - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QEA-PI-SUP-0001 | Compressed Air - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00QHA-CM-MDB-0001 | Auxiliary Boiler - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QHA-CM-OMM-0001 | Auxiliary Boiler - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QHA-GE-RPT-0001 | Auxiliary Boiler - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QHA-ME-ITP-0001 | Auxiliary Boiler - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QHA-PI-SUP-0001 | Auxiliary Boiler - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00QJA-CM-MDB-0001 | Nitrogen Supply - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QJA-CM-OMM-0001 | Nitrogen Supply - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QJA-GE-RPT-0001 | Nitrogen, Hydrogen and CO2 Supply - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QJA-ME-ITP-0001 | Nitrogen, Hydrogen and CO2 Supply - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QJA-PI-SUP-0001 | Nitrogen Supply - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00QJB-CM-MDB-0001 | Hydrogen and CO2 Supply - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QJB-CM-OMM-0001 | Hydrogen and CO2 Supply - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QJB-PI-SUP-0001 | Hydrogen and CO2 Supply - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00QUA-CM-MDB-0001 | Sampling and SWAS - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QUA-CM-OMM-0001 | Sampling and SWAS - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00QUA-GE-RPT-0001 | Steam/Water Analysis System - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QUA-IC-ITP-0001 | Steam/Water Analysis System - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00QUA-PI-SUP-0001 | Sampling and SWAS - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00SAA-CM-MDB-0001 | HVAC - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SAA-CM-OMM-0001 | HVAC - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SAA-GE-RPT-0001 | HVAC Plant and Equipment - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00SAA-HV-ITP-0001 | HVAC Plant and Equipment - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00SAA-PI-SUP-0001 | HVAC - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00SGA-CM-MDB-0001 | Fire Water System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGA-CM-OMM-0001 | Fire Water System - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGA-GE-RPT-0001 | Fire Pumps and Fire Protection Systems - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00SGA-ME-ITP-0001 | Fire Pumps and Fire Protection Systems - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00SGA-PI-PPL-0001 | Fire Water System - Underground Piping Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00SGA-PI-SUP-0001 | Fire Water System - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00SGC-CM-MDB-0001 | Deluge, Spray and Foam Systems - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGC-CM-OMM-0001 | Deluge, Spray and Foam Systems - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGC-PI-SUP-0001 | Deluge, Spray and Foam Systems - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-00SGY-CM-MDB-0001 | Fire Detection and Alarm - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGY-CM-OMM-0001 | Fire Detection and Alarm - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SGY-GE-ITP-0001 | Fire Detection and Alarm System - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00SGY-GE-RPT-0001 | Fire Detection and Alarm System - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00SMA-CM-MDB-0001 | Cranes and Hoists - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-00SMA-GE-RPT-0001 | EOT Cranes - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00SMA-ME-ITP-0001 | EOT Cranes - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00UAC-CV-EFD-0001 | GIS Building - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-CV-RBR-0001 | GIS Building - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-EL-CBL-0001 | 380 kV GIS Switchyard - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-EL-ELY-0002 | 380 kV GIS Switchyard - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-EL-ELY-0003 | GIS Building - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-HS-GAD-0001 | GIS Building - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-HV-GAD-0001 | GIS Building - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-IC-ELY-0001 | GIS Building - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-IC-HUP-0001 | 380 kV GIS Switchyard - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-IC-LOP-0001 | 380 kV GIS Switchyard - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-IC-LOP-0002 | 380 kV GIS Switchyard - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UAC-SS-STL-0001 | GIS Building - Structural Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-CV-EFD-0001 | Electrical Building - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-CV-RBR-0001 | Electrical Building - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-EL-CBL-0001 | Electrical Building and Emergency Power - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-EL-ELY-0002 | Electrical Building and Emergency Power - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-EL-ELY-0003 | Electrical Building - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-HS-GAD-0001 | Electrical Building - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-HV-GAD-0001 | Electrical Building and Emergency Power - HVAC Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-HV-GAD-0002 | Electrical Building - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-IC-ELY-0001 | Electrical Building - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-IC-HUP-0001 | Electrical Building and Emergency Power - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-IC-LOP-0001 | Electrical Building and Emergency Power - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-IC-LOP-0002 | Electrical Building and Emergency Power - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBA-SS-STL-0001 | Electrical Building - Structural Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBF-CV-EFD-0001 | Transformer Bays - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBF-CV-RBR-0001 | Transformer Bays - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UBF-EL-ELY-0001 | Transformer Bays - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-CV-RBR-0001 | Control Building - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-EL-CBL-0001 | Control, Administration and Workshop Buildings - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-EL-ELY-0002 | Control, Administration and Workshop Buildings - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-EL-ELY-0003 | Control Building - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-HS-GAD-0001 | Control Building - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-HV-GAD-0001 | Control, Administration and Workshop Buildings - HVAC Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-HV-GAD-0002 | Control Building - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-IC-ELY-0002 | Control Building - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-IC-HUP-0001 | Control, Administration and Workshop Buildings - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-IC-LOP-0001 | Control, Administration and Workshop Buildings - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-IC-LOP-0002 | Control, Administration and Workshop Buildings - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UCA-SS-STL-0001 | Control Building - Structural Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-CV-EFD-0001 | LDO Tank Farm Structures - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-CV-RBR-0001 | LDO Tank Farm Structures - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-EL-CBL-0001 | LDO Tank Farm and Unloading - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-EL-ELY-0002 | LDO Tank Farm and Unloading - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-EL-ELY-0003 | LDO Tank Farm Structures - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-IC-HUP-0001 | LDO Tank Farm and Unloading - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-IC-LOP-0001 | LDO Tank Farm and Unloading - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEG-IC-LOP-0002 | LDO Tank Farm and Unloading - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-CV-EFD-0001 | Gas Station Structures - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-CV-RBR-0001 | Gas Station Structures - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-EL-CBL-0001 | Fuel Gas Station - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-EL-ELY-0002 | Fuel Gas Station - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-EL-ELY-0003 | Gas Station Structures - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-HS-GAD-0001 | Gas Station Structures - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-HV-GAD-0001 | Gas Station Structures - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-IC-ELY-0002 | Gas Station Structures - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-IC-HUP-0001 | Fuel Gas Station - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-IC-LOP-0001 | Fuel Gas Station - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UEK-IC-LOP-0002 | Fuel Gas Station - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-CV-EFD-0001 | Water Treatment Building and Basins - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-CV-RBR-0001 | Water Treatment Building and Basins - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-EL-CBL-0001 | Water Treatment and Effluents - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-EL-ELY-0002 | Water Treatment and Effluents - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-EL-ELY-0003 | Water Treatment Building and Basins - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-HS-GAD-0001 | Water Treatment Building and Basins - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-HV-GAD-0001 | Water Treatment Building and Basins - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-IC-ELY-0002 | Water Treatment Building and Basins - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-IC-HUP-0001 | Water Treatment and Effluents - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-IC-LOP-0001 | Water Treatment and Effluents - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-IC-LOP-0002 | Water Treatment and Effluents - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Structural Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPA-CV-RBR-0001 | CW Intake and Outfall Marine Structures - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPA-EL-ELY-0001 | CW Intake and Outfall Marine Structures - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPA-EL-ELY-0002 | Marine Works - Electrical Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPA-GE-RPT-0001 | Marine Works - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00UPC-CV-EFD-0001 | CW Pump House - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-CV-RBR-0001 | CW Pump House - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-EL-CBL-0001 | CW Pump House and Onshore CW - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-EL-ELY-0002 | CW Pump House and Onshore CW - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-EL-ELY-0003 | CW Pump House - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-HS-GAD-0001 | CW Pump House - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-HV-GAD-0001 | CW Pump House - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-IC-ELY-0002 | CW Pump House - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-IC-HUP-0001 | CW Pump House and Onshore CW - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-IC-LOP-0001 | CW Pump House and Onshore CW - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UPC-IC-LOP-0002 | CW Pump House and Onshore CW - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-CV-EFD-0001 | Utility Building - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-CV-RBR-0001 | Utility Building - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-EL-CBL-0001 | BOP Utilities - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-EL-ELY-0002 | BOP Utilities - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-EL-ELY-0003 | Utility Building - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-HS-GAD-0001 | Utility Building - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-HV-GAD-0001 | Utility Building - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-IC-ELY-0002 | Utility Building - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-IC-HUP-0001 | BOP Utilities - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-IC-LOP-0001 | BOP Utilities - Loop and Connection Diagrams, Part 1 of 2 | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-IC-LOP-0002 | BOP Utilities - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UQA-IC-LOP-0003 | BOP Utilities - Loop and Connection Diagrams, Part 2 of 2 | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-CV-RBR-0001 | Workshop and Warehouse - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-EL-ELY-0001 | Workshop and Warehouse - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-HS-GAD-0001 | Workshop and Warehouse - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-HV-GAD-0001 | Workshop and Warehouse - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-IC-ELY-0001 | Workshop and Warehouse - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00USA-SS-STL-0001 | Workshop and Warehouse - Structural Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-CV-RBR-0001 | Administration Building - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-EL-ELY-0001 | Administration Building - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-HS-GAD-0001 | Administration Building - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-HV-GAD-0001 | Administration Building - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-IC-ELY-0001 | Administration Building - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UYA-SS-STL-0001 | Administration Building - Structural Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-EL-CBL-0001 | Site-Wide Infrastructure - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-EL-ELY-0002 | Site-Wide Infrastructure - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-EL-ELY-0003 | Roads and Paving - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-IC-HUP-0001 | Site-Wide Infrastructure - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-IC-LOP-0001 | Site-Wide Infrastructure - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZA-IC-LOP-0002 | Site-Wide Infrastructure - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZB-EL-ELY-0001 | Fencing and Gates - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZC-CV-RBR-0001 | Site Drainage and Culverts - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZC-EL-ELY-0001 | Site Drainage and Culverts - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZD-CV-RBR-0001 | Pipe Racks and Pipe Sleepers - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZD-EL-ELY-0001 | Pipe Racks and Pipe Sleepers - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZE-CV-RBR-0001 | Cable Trenches and Duct Banks - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZE-EL-ELY-0001 | Cable Trenches and Duct Banks - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZF-CV-RBR-0001 | Temporary Barge Landing - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZF-EL-ELY-0001 | Temporary Barge Landing - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-00UZF-GE-RPT-0001 | Heavy Transport, Barge Landing and Marine Logistics - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00XJA-CM-MDB-0001 | Emergency Diesel Generator - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00XJA-CM-OMM-0001 | Emergency Diesel Generator - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-00XJA-EL-ITP-0001 | Emergency Diesel Generator - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-00XJA-GE-RPT-0001 | Emergency Diesel Generator - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10BAA-CM-MDB-0001 | GT Generator Busduct - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-10BAC-CM-MDB-0001 | GT Generator Circuit Breaker - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-10BAT-CM-MDB-0001 | GT Generator Step-Up Transformer - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-10BBT-CM-MDB-0001 | GT Unit Auxiliary Transformer - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-10BBT-CM-OMM-0001 | GT Unit Auxiliary Transformer - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-10BBT-EL-ITP-0001 | Unit Auxiliary Transformers - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10BBT-GE-RPT-0001 | Unit Auxiliary Transformers - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10HAA-CM-MDB-0001 | HRSG Pressure System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10HAN-CM-MDB-0001 | HRSG Blowdown and Drains - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10HAN-CM-OMM-0001 | HRSG Blowdown and Drains - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10HAN-GE-RPT-0001 | HRSG Blowdown and Drain Tanks - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10HAN-ME-ITP-0001 | HRSG Blowdown and Drain Tanks - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10HAN-PI-SUP-0001 | HRSG Blowdown and Drains - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10HNA-CM-MDB-0001 | HRSG Flue Gas Ducting - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10HNE-CM-MDB-0001 | Stack 65 m with CEMS Platform and Silencer - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10HNE-GE-RPT-0001 | Stack 65 m with Silencer - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10HSA-CM-MDB-0001 | SCR Catalyst and Ammonia Injection - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10HSB-CM-MDB-0001 | Ammonia Storage and Supply - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10HSB-CM-OMM-0001 | Ammonia Storage and Supply - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10HSB-GE-RPT-0001 | Aqueous Ammonia Storage and Forwarding - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10HSB-ME-ITP-0001 | Aqueous Ammonia Storage and Forwarding - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10HSB-PI-SUP-0001 | Ammonia Storage and Supply - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-EPC-10LAB-CM-MDB-0001 | Feedwater Piping - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAB-CM-OMM-0001 | Feedwater Piping - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAB-PI-SUP-0001 | Feedwater Piping - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10LAC-CM-MDB-0001 | Boiler Feed Pumps - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAC-CM-OMM-0001 | Boiler Feed Pumps - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAC-GE-RPT-0001 | Boiler Feed Pumps - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10LAC-ME-ITP-0001 | Boiler Feed Pumps - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10LAC-PI-SUP-0001 | Boiler Feed Pumps - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10LAE-CM-MDB-0001 | HP Attemperation Spray Water - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAE-CM-OMM-0001 | HP Attemperation Spray Water - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAE-PI-SUP-0001 | HP Attemperation Spray Water - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10LAF-CM-MDB-0001 | Reheat Attemperation Spray Water - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAF-CM-OMM-0001 | Reheat Attemperation Spray Water - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LAF-PI-SUP-0001 | Reheat Attemperation Spray Water - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10LBA-CM-MDB-0001 | Main Steam Piping - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBA-CM-OMM-0001 | Main Steam Piping - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBA-GE-RPT-0001 | Alloy Piping P91 / P22 - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-10LBA-PI-SUP-0001 | Main Steam Piping - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10LBB-CM-MDB-0001 | Hot Reheat Piping - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBB-CM-OMM-0001 | Hot Reheat Piping - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBB-PI-SUP-0001 | Hot Reheat Piping - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10LBC-CM-MDB-0001 | Cold Reheat Piping - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBC-CM-OMM-0001 | Cold Reheat Piping - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBC-PI-SUP-0001 | Cold Reheat Piping - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10LBD-CM-MDB-0001 | LP Steam Piping - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBD-CM-OMM-0001 | LP Steam Piping - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-10LBD-PI-SUP-0001 | LP Steam Piping - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-10MBA-CM-MDB-0001 | Gas Turbine - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MBL-CM-MDB-0001 | GT Inlet Air System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MBN-CM-MDB-0001 | GT Liquid Fuel and Water Injection - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MBP-CM-MDB-0001 | GT Fuel Gas System incl. Performance Heater - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MBU-CM-MDB-0001 | GT Compressor Washing - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MBV-CM-MDB-0001 | GT Lube Oil System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MBY-CM-MDB-0001 | GT Control and Protection - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MKA-CM-MDB-0001 | GT Generator - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MKC-CM-MDB-0001 | GT Excitation and Static Frequency Converter - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10MKG-CM-MDB-0001 | GT Generator Gas System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-10UHA-CV-EFD-0001 | HRSG Foundations and Structures - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UHA-CV-RBR-0001 | HRSG Foundations and Structures - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UHA-EL-ELY-0001 | HRSG Foundations and Structures - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UHN-CV-EFD-0001 | Stack Foundation - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UHN-CV-RBR-0001 | Stack Foundation - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UHN-EL-ELY-0001 | Stack Foundation - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-CV-EFD-0001 | Gas Turbine Hall - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-CV-RBR-0001 | Gas Turbine Hall - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-EL-CBL-0001 | Power Block - GT and HRSG - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-EL-ELY-0002 | Power Block - GT and HRSG - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-EL-ELY-0003 | Gas Turbine Hall - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-HS-GAD-0001 | Gas Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-HV-GAD-0001 | Power Block - GT and HRSG - HVAC Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-HV-GAD-0002 | Gas Turbine Hall - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-IC-ELY-0002 | Gas Turbine Hall - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-IC-HUP-0001 | Power Block - GT and HRSG - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-IC-LOP-0001 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 1 of 2 | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-IC-LOP-0002 | Power Block - GT and HRSG - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-10UMA-IC-LOP-0003 | Power Block - GT and HRSG - Loop and Connection Diagrams, Part 2 of 2 | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20BAA-CM-MDB-0001 | ST Generator Busduct - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-20BAC-CM-MDB-0001 | ST Generator Circuit Breaker - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-20BAT-CM-MDB-0001 | ST Generator Step-Up Transformer - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-20BBT-CM-MDB-0001 | ST Unit Auxiliary Transformer - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-20BBT-CM-OMM-0001 | ST Unit Auxiliary Transformer - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL, G-OPS-HO-EL
ALP-EPC-20LCA-CM-MDB-0001 | Main Condensate Piping - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20LCA-CM-OMM-0001 | Main Condensate Piping - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20LCA-PI-SUP-0001 | Main Condensate Piping - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-20LCB-CM-MDB-0001 | Condensate Extraction Pumps - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20LCB-CM-OMM-0001 | Condensate Extraction Pumps - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20LCB-GE-RPT-0001 | Condensate Extraction Pumps - Technical Bid Evaluation | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-20LCB-ME-ITP-0001 | Condensate Extraction Pumps - Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-PO
ALP-EPC-20LCB-PI-SUP-0001 | Condensate Extraction Pumps - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-20MAA-CM-MDB-0001 | HP Turbine - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAB-CM-MDB-0001 | IP/LP Turbine - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAG-CM-MDB-0001 | Condensing System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAJ-CM-MDB-0001 | Condenser Vacuum System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAN-CM-MDB-0001 | Turbine Bypass Stations and Piping - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAN-CM-OMM-0001 | Turbine Bypass Stations and Piping - Operating Procedures | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAN-PI-SUP-0001 | Turbine Bypass Stations and Piping - Pipe Support Drawings | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-EPC-20MAV-CM-MDB-0001 | ST Lube Oil System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAW-CM-MDB-0001 | Gland Steam System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAX-CM-MDB-0001 | ST Control Fluid System - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-COM-SC-WS, G-OPS-HO-WS
ALP-EPC-20MAY-CM-MDB-0001 | ST Control and Protection - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-20MKA-CM-MDB-0001 | ST Generator - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-20MKC-CM-MDB-0001 | ST Excitation - System Turnover Dossier | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-COM-SC-FF, G-OPS-HO-FF
ALP-EPC-20UMB-CV-EFD-0001 | Steam Turbine Hall - Equipment Foundation Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-CV-RBR-0001 | Steam Turbine Hall - Reinforcement Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-EL-CBL-0001 | Power Block - ST and Condenser - Cable Schedule and Routing | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-EL-ELY-0002 | Power Block - ST and Condenser - Cable Routing, Tray and Trench Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-EL-ELY-0003 | Steam Turbine Hall - Earthing and Lightning Protection Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-HS-GAD-0001 | Steam Turbine Hall - Fire Fighting, Escape Route and Safety Signage Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-HV-GAD-0001 | Steam Turbine Hall - Building Services | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-IC-ELY-0002 | Steam Turbine Hall - Fire Detection and Alarm Layouts | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-IC-HUP-0001 | Power Block - ST and Condenser - Instrument Hook-Up Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-IC-LOP-0001 | Power Block - ST and Condenser - Loop and Connection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-EPC-20UMB-IC-LOP-0002 | Power Block - ST and Condenser - Junction Box and Cabinet Interconnection Diagrams | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-H01-00SAA-EL-WIR-0001 | HVAC Plant and Equipment - Supplier Electrical Schematics and Wiring Diagrams, Part 1 of 2 | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-H01-00SAA-EL-WIR-0002 | HVAC Plant and Equipment - Supplier Electrical Schematics and Wiring Diagrams, Part 2 of 2 | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-H01-00SAA-ME-CAL-0001 | HVAC Plant and Equipment - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-H01-00SAA-ME-DSH-0001 | HVAC Plant and Equipment - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-H01-00SAA-ME-GAD-0001 | HVAC Plant and Equipment - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-H01-00SAA-ME-ITP-0001 | HVAC Plant and Equipment - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-H01-00SAA-ME-MDB-0001 | HVAC Plant and Equipment - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-H01-00SAA-ME-OMM-0001 | HVAC Plant and Equipment - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-H01-00SAA-ME-PRC-0001 | HVAC Plant and Equipment - Supplier Installation and Erection Manual | 0 | 0 | 0 | 3 | G-CON-CWP
ALP-H01-00SAA-ME-TRP-0001 | HVAC Plant and Equipment - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-H01-00SAA-ME-TST-0001 | HVAC Plant and Equipment - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-H01-00SAA-PR-PID-0001 | HVAC Plant and Equipment - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-I01-00CJA-EL-WIR-0001 | Plant DCS - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-I01-00CJA-ME-CAL-0001 | Plant DCS - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I01-00CJA-ME-DSH-0001 | Plant DCS - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I01-00CJA-ME-GAD-0001 | Plant DCS - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-I01-00CJA-ME-ITP-0001 | Plant DCS - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I01-00CJA-ME-MDB-0001 | Plant DCS - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I01-00CJA-ME-OMM-0001 | Plant DCS - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-I01-00CJA-ME-PRC-0001 | Plant DCS - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-I01-00CJA-ME-TRP-0001 | Plant DCS - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I01-00CJA-ME-TST-0001 | Plant DCS - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-I02-00CQA-EL-WIR-0001 | Continuous Emission Monitoring System - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-I02-00CQA-ME-CAL-0001 | Continuous Emission Monitoring System - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I02-00CQA-ME-DSH-0001 | Continuous Emission Monitoring System - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I02-00CQA-ME-GAD-0001 | Continuous Emission Monitoring System - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-I02-00CQA-ME-ITP-0001 | Continuous Emission Monitoring System - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I02-00CQA-ME-MDB-0001 | Continuous Emission Monitoring System - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I02-00CQA-ME-OMM-0001 | Continuous Emission Monitoring System - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-I02-00CQA-ME-PRC-0001 | Continuous Emission Monitoring System - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-I02-00CQA-ME-TRP-0001 | Continuous Emission Monitoring System - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I02-00CQA-ME-TST-0001 | Continuous Emission Monitoring System - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-I03-00QUA-EL-WIR-0001 | Steam/Water Analysis System - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-I03-00QUA-ME-CAL-0001 | Steam/Water Analysis System - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I03-00QUA-ME-DSH-0001 | Steam/Water Analysis System - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I03-00QUA-ME-GAD-0001 | Steam/Water Analysis System - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-I03-00QUA-ME-ITP-0001 | Steam/Water Analysis System - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I03-00QUA-ME-MDB-0001 | Steam/Water Analysis System - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I03-00QUA-ME-OMM-0001 | Steam/Water Analysis System - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-I03-00QUA-ME-PRC-0001 | Steam/Water Analysis System - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-I03-00QUA-ME-TRP-0001 | Steam/Water Analysis System - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I03-00QUA-ME-TST-0001 | Steam/Water Analysis System - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-I03-00QUA-PR-PID-0001 | Steam/Water Analysis System - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-I04-00000-ME-MDB-0001 | Field Instruments - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I05-00000-ME-MDB-0001 | Control Valves - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I06-00SGY-EL-WIR-0001 | Fire Detection and Alarm System - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-I06-00SGY-ME-CAL-0001 | Fire Detection and Alarm System - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I06-00SGY-ME-DSH-0001 | Fire Detection and Alarm System - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I06-00SGY-ME-GAD-0001 | Fire Detection and Alarm System - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-I06-00SGY-ME-ITP-0001 | Fire Detection and Alarm System - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I06-00SGY-ME-MDB-0001 | Fire Detection and Alarm System - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I06-00SGY-ME-OMM-0001 | Fire Detection and Alarm System - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-I06-00SGY-ME-PRC-0001 | Fire Detection and Alarm System - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-I06-00SGY-ME-TRP-0001 | Fire Detection and Alarm System - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I06-00SGY-ME-TST-0001 | Fire Detection and Alarm System - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-I07-00CYA-EL-WIR-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-I07-00CYA-ME-CAL-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I07-00CYA-ME-DSH-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I07-00CYA-ME-GAD-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-I07-00CYA-ME-ITP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I07-00CYA-ME-MDB-0001 | Telecom, CCTV, Access Control and Perimeter Security - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I07-00CYA-ME-OMM-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-I07-00CYA-ME-PRC-0001 | Telecom, CCTV, Access Control and Perimeter Security - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-I07-00CYA-ME-TRP-0001 | Telecom, CCTV, Access Control and Perimeter Security - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I07-00CYA-ME-TST-0001 | Telecom, CCTV, Access Control and Perimeter Security - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-I08-00CJG-EL-WIR-0001 | BOP Safety Instrumented System - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-I08-00CJG-ME-CAL-0001 | BOP Safety Instrumented System - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I08-00CJG-ME-DSH-0001 | BOP Safety Instrumented System - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I08-00CJG-ME-GAD-0001 | BOP Safety Instrumented System - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-I08-00CJG-ME-ITP-0001 | BOP Safety Instrumented System - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I08-00CJG-ME-MDB-0001 | BOP Safety Instrumented System - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I08-00CJG-ME-OMM-0001 | BOP Safety Instrumented System - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-I08-00CJG-ME-PRC-0001 | BOP Safety Instrumented System - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-I08-00CJG-ME-TRP-0001 | BOP Safety Instrumented System - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I08-00CJG-ME-TST-0001 | BOP Safety Instrumented System - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-I09-00CKA-EL-WIR-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-I09-00CKA-ME-CAL-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I09-00CKA-ME-DSH-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I09-00CKA-ME-GAD-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-I09-00CKA-ME-ITP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-I09-00CKA-ME-MDB-0001 | Operator Training Simulator, Historian and Performance Monitoring - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I09-00CKA-ME-OMM-0001 | Operator Training Simulator, Historian and Performance Monitoring - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-I09-00CKA-ME-TRP-0001 | Operator Training Simulator, Historian and Performance Monitoring - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-I09-00CKA-ME-TST-0001 | Operator Training Simulator, Historian and Performance Monitoring - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-I10-00000-ME-MDB-0001 | Instrument Installation Materials - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10BAT-CM-CMP-0001 | Generator Step-Up Transformers - Supplier Commissioning Procedures | 0 | 0 | 0 | 2 | G-COM-SC-EL
ALP-IEC-10BAT-EL-DSH-0001 | Generator Step-Up Transformers - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10BAT-EL-WIR-0001 | Generator Step-Up Transformers - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-EL, G-CON-CWP, G-CON-IWP
ALP-IEC-10BAT-ME-CAL-0001 | Generator Step-Up Transformers - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10BAT-ME-ITP-0001 | Generator Step-Up Transformers - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10BAT-ME-MDB-0001 | Generator Step-Up Transformers - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10BAT-ME-OMM-0001 | Generator Step-Up Transformers - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-EL, G-OPS-HO-EL
ALP-IEC-10BAT-ME-PRC-0001 | Generator Step-Up Transformers - Supplier Installation and Erection Manual | 0 | 0 | 0 | 2 | G-CON-CWP
ALP-IEC-10BAT-ME-TRP-0001 | Generator Step-Up Transformers - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10BAT-ME-TST-0001 | Generator Step-Up Transformers - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-IEC-10HAA-CM-CMP-0001 | HRSG incl. SCR - Supplier Commissioning Procedures | 0 | 0 | 0 | 3 | G-COM-SC-FF
ALP-IEC-10HAA-EL-WIR-0001 | HRSG incl. SCR - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-IEC-10HAA-ME-CAL-0001 | HRSG incl. SCR - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10HAA-ME-DSH-0001 | HRSG incl. SCR - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10HAA-ME-ITP-0001 | HRSG incl. SCR - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10HAA-ME-MDB-0001 | HRSG incl. SCR - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10HAA-ME-OMM-0001 | HRSG incl. SCR - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 6 | G-COM-SC-FF, G-OPS-HO-FF
ALP-IEC-10HAA-ME-PRC-0001 | HRSG incl. SCR - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-IEC-10HAA-ME-TRP-0001 | HRSG incl. SCR - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10HAA-ME-TST-0001 | HRSG incl. SCR - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-IEC-10MBA-CM-CMP-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Commissioning Procedures | 0 | 0 | 0 | 6 | G-COM-SC-FF
ALP-IEC-10MBA-EL-WIR-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Electrical Schematics and Wiring Diagrams, Part 1 of 2 | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-IEC-10MBA-EL-WIR-0002 | Gas Turbine Package incl. Auxiliaries - Supplier Electrical Schematics and Wiring Diagrams, Part 2 of 2 | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-IEC-10MBA-ME-CAL-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10MBA-ME-DSH-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10MBA-ME-ITP-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10MBA-ME-MDB-0001 | Gas Turbine Package incl. Auxiliaries - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10MBA-ME-OMM-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 12 | G-COM-SC-FF, G-OPS-HO-FF
ALP-IEC-10MBA-ME-PRC-0001 | Gas Turbine Package incl. Auxiliaries - Supplier Installation and Erection Manual | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-IEC-10MBA-ME-TRP-0001 | Gas Turbine Package incl. Auxiliaries - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10MBA-ME-TST-0001 | Gas Turbine Package incl. Auxiliaries - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-IEC-10MBY-CM-CMP-0001 | Turbine Control System - Supplier Commissioning Procedures | 0 | 0 | 0 | 2 | G-COM-SC-FF
ALP-IEC-10MBY-EL-WIR-0001 | Turbine Control System - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-IEC-10MBY-ME-CAL-0001 | Turbine Control System - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10MBY-ME-DSH-0001 | Turbine Control System - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10MBY-ME-GAD-0001 | Turbine Control System - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-IEC-10MBY-ME-ITP-0001 | Turbine Control System - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10MBY-ME-MDB-0001 | Turbine Control System - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10MBY-ME-OMM-0001 | Turbine Control System - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-FF, G-OPS-HO-FF
ALP-IEC-10MBY-ME-PRC-0001 | Turbine Control System - Supplier Installation and Erection Manual | 0 | 0 | 0 | 2 | G-CON-CWP
ALP-IEC-10MBY-ME-TRP-0001 | Turbine Control System - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10MBY-ME-TST-0001 | Turbine Control System - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-IEC-10MKA-CM-CMP-0001 | Generators, Excitation, GCB and Busducts - Supplier Commissioning Procedures | 0 | 0 | 0 | 9 | G-COM-SC-EL, G-COM-SC-FF
ALP-IEC-10MKA-EL-WIR-0001 | Generators, Excitation, GCB and Busducts - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-IEC-10MKA-ME-CAL-0001 | Generators, Excitation, GCB and Busducts - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10MKA-ME-GAD-0001 | Generators, Excitation, GCB and Busducts - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-IEC-10MKA-ME-ITP-0001 | Generators, Excitation, GCB and Busducts - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-10MKA-ME-MDB-0001 | Generators, Excitation, GCB and Busducts - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10MKA-ME-OMM-0001 | Generators, Excitation, GCB and Busducts - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 18 | G-COM-SC-EL, G-COM-SC-FF, G-OPS-HO-EL, G-OPS-HO-FF
ALP-IEC-10MKA-ME-PRC-0001 | Generators, Excitation, GCB and Busducts - Supplier Installation and Erection Manual | 0 | 0 | 0 | 2 | G-CON-CWP
ALP-IEC-10MKA-ME-TRP-0001 | Generators, Excitation, GCB and Busducts - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-10MKA-ME-TST-0001 | Generators, Excitation, GCB and Busducts - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-IEC-10MKA-PR-PID-0001 | Generators, Excitation, GCB and Busducts - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-IEC-20MAA-CM-CMP-0001 | Steam Turbine and Condenser - Supplier Commissioning Procedures | 0 | 0 | 0 | 7 | G-COM-SC-WS
ALP-IEC-20MAA-EL-WIR-0001 | Steam Turbine and Condenser - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-IEC-20MAA-ME-CAL-0001 | Steam Turbine and Condenser - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-20MAA-ME-DSH-0001 | Steam Turbine and Condenser - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-20MAA-ME-ITP-0001 | Steam Turbine and Condenser - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-IEC-20MAA-ME-MDB-0001 | Steam Turbine and Condenser - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-20MAA-ME-OMM-0001 | Steam Turbine and Condenser - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 14 | G-COM-SC-WS, G-OPS-HO-WS
ALP-IEC-20MAA-ME-PRC-0001 | Steam Turbine and Condenser - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-IEC-20MAA-ME-TRP-0001 | Steam Turbine and Condenser - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-IEC-20MAA-ME-TST-0001 | Steam Turbine and Condenser - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M01-10LAC-EL-WIR-0001 | Boiler Feed Pumps - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-M01-10LAC-ME-CAL-0001 | Boiler Feed Pumps - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M01-10LAC-ME-DSH-0001 | Boiler Feed Pumps - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M01-10LAC-ME-GAD-0001 | Boiler Feed Pumps - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M01-10LAC-ME-ITP-0001 | Boiler Feed Pumps - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M01-10LAC-ME-MDB-0001 | Boiler Feed Pumps - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M01-10LAC-ME-OMM-0001 | Boiler Feed Pumps - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-M01-10LAC-ME-PRC-0001 | Boiler Feed Pumps - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M01-10LAC-ME-TRP-0001 | Boiler Feed Pumps - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M01-10LAC-ME-TST-0001 | Boiler Feed Pumps - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M01-10LAC-PR-PID-0001 | Boiler Feed Pumps - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M02-20LCB-EL-WIR-0001 | Condensate Extraction Pumps - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-M02-20LCB-ME-CAL-0001 | Condensate Extraction Pumps - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M02-20LCB-ME-DSH-0001 | Condensate Extraction Pumps - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M02-20LCB-ME-GAD-0001 | Condensate Extraction Pumps - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M02-20LCB-ME-ITP-0001 | Condensate Extraction Pumps - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M02-20LCB-ME-MDB-0001 | Condensate Extraction Pumps - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M02-20LCB-ME-OMM-0001 | Condensate Extraction Pumps - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-M02-20LCB-ME-PRC-0001 | Condensate Extraction Pumps - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M02-20LCB-ME-TRP-0001 | Condensate Extraction Pumps - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M02-20LCB-ME-TST-0001 | Condensate Extraction Pumps - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M02-20LCB-PR-PID-0001 | Condensate Extraction Pumps - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M03-00PAC-EL-WIR-0001 | CW Pumps - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M03-00PAC-ME-CAL-0001 | CW Pumps - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M03-00PAC-ME-DSH-0001 | CW Pumps - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M03-00PAC-ME-GAD-0001 | CW Pumps - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M03-00PAC-ME-ITP-0001 | CW Pumps - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M03-00PAC-ME-MDB-0001 | CW Pumps - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M03-00PAC-ME-OMM-0001 | CW Pumps - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M03-00PAC-ME-PRC-0001 | CW Pumps - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M03-00PAC-ME-TRP-0001 | CW Pumps - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M03-00PAC-ME-TST-0001 | CW Pumps - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M03-00PAC-PR-PID-0001 | CW Pumps - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M04-00PAA-EL-WIR-0001 | Travelling Band Screens and Trash Rakes - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M04-00PAA-ME-CAL-0001 | Travelling Band Screens and Trash Rakes - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M04-00PAA-ME-DSH-0001 | Travelling Band Screens and Trash Rakes - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M04-00PAA-ME-GAD-0001 | Travelling Band Screens and Trash Rakes - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M04-00PAA-ME-ITP-0001 | Travelling Band Screens and Trash Rakes - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M04-00PAA-ME-MDB-0001 | Travelling Band Screens and Trash Rakes - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M04-00PAA-ME-OMM-0001 | Travelling Band Screens and Trash Rakes - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M04-00PAA-ME-PRC-0001 | Travelling Band Screens and Trash Rakes - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M04-00PAA-ME-TRP-0001 | Travelling Band Screens and Trash Rakes - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M04-00PAA-ME-TST-0001 | Travelling Band Screens and Trash Rakes - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M04-00PAA-PR-PID-0001 | Travelling Band Screens and Trash Rakes - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M05-00PBA-EL-WIR-0001 | Electro-Chlorination Package - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M05-00PBA-ME-CAL-0001 | Electro-Chlorination Package - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M05-00PBA-ME-DSH-0001 | Electro-Chlorination Package - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M05-00PBA-ME-GAD-0001 | Electro-Chlorination Package - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M05-00PBA-ME-ITP-0001 | Electro-Chlorination Package - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M05-00PBA-ME-MDB-0001 | Electro-Chlorination Package - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M05-00PBA-ME-OMM-0001 | Electro-Chlorination Package - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M05-00PBA-ME-PRC-0001 | Electro-Chlorination Package - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M05-00PBA-ME-TRP-0001 | Electro-Chlorination Package - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M05-00PBA-ME-TST-0001 | Electro-Chlorination Package - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M05-00PBA-PR-PID-0001 | Electro-Chlorination Package - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M06-00PAH-EL-WIR-0001 | Condenser Tube Cleaning System - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M06-00PAH-ME-CAL-0001 | Condenser Tube Cleaning System - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M06-00PAH-ME-DSH-0001 | Condenser Tube Cleaning System - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M06-00PAH-ME-GAD-0001 | Condenser Tube Cleaning System - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M06-00PAH-ME-ITP-0001 | Condenser Tube Cleaning System - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M06-00PAH-ME-MDB-0001 | Condenser Tube Cleaning System - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M06-00PAH-ME-OMM-0001 | Condenser Tube Cleaning System - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M06-00PAH-ME-PRC-0001 | Condenser Tube Cleaning System - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M06-00PAH-ME-TRP-0001 | Condenser Tube Cleaning System - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M06-00PAH-ME-TST-0001 | Condenser Tube Cleaning System - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M06-00PAH-PR-PID-0001 | Condenser Tube Cleaning System - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M07-00PGA-EL-WIR-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M07-00PGA-ME-CAL-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M07-00PGA-ME-DSH-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M07-00PGA-ME-GAD-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M07-00PGA-ME-ITP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M07-00PGA-ME-MDB-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M07-00PGA-ME-OMM-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M07-00PGA-ME-PRC-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M07-00PGA-ME-TRP-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M07-00PGA-ME-TST-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M07-00PGA-PR-PID-0001 | Closed Cooling Water Heat Exchangers, Pumps, Tank - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M08-00QEA-EL-WIR-0001 | Air Compressors and Dryers - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M08-00QEA-ME-CAL-0001 | Air Compressors and Dryers - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M08-00QEA-ME-DSH-0001 | Air Compressors and Dryers - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M08-00QEA-ME-GAD-0001 | Air Compressors and Dryers - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M08-00QEA-ME-ITP-0001 | Air Compressors and Dryers - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M08-00QEA-ME-MDB-0001 | Air Compressors and Dryers - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M08-00QEA-ME-OMM-0001 | Air Compressors and Dryers - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M08-00QEA-ME-PRC-0001 | Air Compressors and Dryers - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M08-00QEA-ME-TRP-0001 | Air Compressors and Dryers - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M08-00QEA-ME-TST-0001 | Air Compressors and Dryers - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M08-00QEA-PR-PID-0001 | Air Compressors and Dryers - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M09-00QHA-EL-WIR-0001 | Auxiliary Boiler - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M09-00QHA-ME-CAL-0001 | Auxiliary Boiler - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M09-00QHA-ME-DSH-0001 | Auxiliary Boiler - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M09-00QHA-ME-GAD-0001 | Auxiliary Boiler - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M09-00QHA-ME-ITP-0001 | Auxiliary Boiler - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M09-00QHA-ME-MDB-0001 | Auxiliary Boiler - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M09-00QHA-ME-OMM-0001 | Auxiliary Boiler - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M09-00QHA-ME-PRC-0001 | Auxiliary Boiler - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M09-00QHA-ME-TRP-0001 | Auxiliary Boiler - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M09-00QHA-ME-TST-0001 | Auxiliary Boiler - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M09-00QHA-PR-PID-0001 | Auxiliary Boiler - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M10-00QJA-EL-WIR-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M10-00QJA-ME-CAL-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M10-00QJA-ME-DSH-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M10-00QJA-ME-GAD-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M10-00QJA-ME-ITP-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M10-00QJA-ME-MDB-0001 | Nitrogen, Hydrogen and CO2 Supply - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M10-00QJA-ME-OMM-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M10-00QJA-ME-PRC-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M10-00QJA-ME-TRP-0001 | Nitrogen, Hydrogen and CO2 Supply - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M10-00QJA-ME-TST-0001 | Nitrogen, Hydrogen and CO2 Supply - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M10-00QJA-PR-PID-0001 | Nitrogen, Hydrogen and CO2 Supply - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M11-00QCA-EL-WIR-0001 | Chemical Dosing Skid - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M11-00QCA-ME-CAL-0001 | Chemical Dosing Skid - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M11-00QCA-ME-DSH-0001 | Chemical Dosing Skid - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M11-00QCA-ME-GAD-0001 | Chemical Dosing Skid - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M11-00QCA-ME-ITP-0001 | Chemical Dosing Skid - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M11-00QCA-ME-MDB-0001 | Chemical Dosing Skid - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M11-00QCA-ME-OMM-0001 | Chemical Dosing Skid - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M11-00QCA-ME-PRC-0001 | Chemical Dosing Skid - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M11-00QCA-ME-TRP-0001 | Chemical Dosing Skid - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M11-00QCA-ME-TST-0001 | Chemical Dosing Skid - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M11-00QCA-PR-PID-0001 | Chemical Dosing Skid - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M12-00GBA-EL-WIR-0001 | Water Treatment Package - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M12-00GBA-ME-CAL-0001 | Water Treatment Package - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M12-00GBA-ME-DSH-0001 | Water Treatment Package - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M12-00GBA-ME-GAD-0001 | Water Treatment Package - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M12-00GBA-ME-ITP-0001 | Water Treatment Package - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M12-00GBA-ME-MDB-0001 | Water Treatment Package - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M12-00GBA-ME-OMM-0001 | Water Treatment Package - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 6 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M12-00GBA-ME-PRC-0001 | Water Treatment Package - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M12-00GBA-ME-TRP-0001 | Water Treatment Package - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M12-00GBA-ME-TST-0001 | Water Treatment Package - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M12-00GBA-PR-PID-0001 | Water Treatment Package - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M13-00GHA-EL-WIR-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M13-00GHA-ME-CAL-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M13-00GHA-ME-DSH-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M13-00GHA-ME-GAD-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M13-00GHA-ME-ITP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M13-00GHA-ME-MDB-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M13-00GHA-ME-OMM-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M13-00GHA-ME-PRC-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier Installation and Erection Manual | 0 | 0 | 0 | 2 | G-CON-CWP
ALP-M13-00GHA-ME-TRP-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M13-00GHA-ME-TST-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M13-00GHA-PR-PID-0001 | Shop-Built Tanks and Demin Forwarding Pumps - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M14-00GNA-EL-WIR-0001 | Waste Water and Sanitary Treatment Packages - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M14-00GNA-ME-CAL-0001 | Waste Water and Sanitary Treatment Packages - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M14-00GNA-ME-DSH-0001 | Waste Water and Sanitary Treatment Packages - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M14-00GNA-ME-GAD-0001 | Waste Water and Sanitary Treatment Packages - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M14-00GNA-ME-ITP-0001 | Waste Water and Sanitary Treatment Packages - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M14-00GNA-ME-MDB-0001 | Waste Water and Sanitary Treatment Packages - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M14-00GNA-ME-OMM-0001 | Waste Water and Sanitary Treatment Packages - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 6 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M14-00GNA-ME-PRC-0001 | Waste Water and Sanitary Treatment Packages - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M14-00GNA-ME-TRP-0001 | Waste Water and Sanitary Treatment Packages - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M14-00GNA-ME-TST-0001 | Waste Water and Sanitary Treatment Packages - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M14-00GNA-PR-PID-0001 | Waste Water and Sanitary Treatment Packages - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M15-00EKA-EL-WIR-0001 | Gas Receiving and Metering Station - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M15-00EKA-ME-CAL-0001 | Gas Receiving and Metering Station - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M15-00EKA-ME-DSH-0001 | Gas Receiving and Metering Station - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M15-00EKA-ME-GAD-0001 | Gas Receiving and Metering Station - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M15-00EKA-ME-ITP-0001 | Gas Receiving and Metering Station - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M15-00EKA-ME-MDB-0001 | Gas Receiving and Metering Station - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M15-00EKA-ME-OMM-0001 | Gas Receiving and Metering Station - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M15-00EKA-ME-PRC-0001 | Gas Receiving and Metering Station - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M15-00EKA-ME-TRP-0001 | Gas Receiving and Metering Station - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M15-00EKA-ME-TST-0001 | Gas Receiving and Metering Station - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M15-00EKA-PR-PID-0001 | Gas Receiving and Metering Station - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M16-00EGA-EL-WIR-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M16-00EGA-ME-CAL-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M16-00EGA-ME-DSH-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M16-00EGA-ME-GAD-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M16-00EGA-ME-ITP-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M16-00EGA-ME-MDB-0001 | LDO Unloading and Forwarding / Treatment Skids - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M16-00EGA-ME-OMM-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M16-00EGA-ME-PRC-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M16-00EGA-ME-TRP-0001 | LDO Unloading and Forwarding / Treatment Skids - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M16-00EGA-ME-TST-0001 | LDO Unloading and Forwarding / Treatment Skids - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M16-00EGA-PR-PID-0001 | LDO Unloading and Forwarding / Treatment Skids - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M18-10HSB-EL-WIR-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M18-10HSB-ME-CAL-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M18-10HSB-ME-DSH-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M18-10HSB-ME-GAD-0001 | Aqueous Ammonia Storage and Forwarding - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M18-10HSB-ME-ITP-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M18-10HSB-ME-MDB-0001 | Aqueous Ammonia Storage and Forwarding - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M18-10HSB-ME-OMM-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M18-10HSB-ME-PRC-0001 | Aqueous Ammonia Storage and Forwarding - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M18-10HSB-ME-TRP-0001 | Aqueous Ammonia Storage and Forwarding - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M18-10HSB-ME-TST-0001 | Aqueous Ammonia Storage and Forwarding - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M18-10HSB-PR-PID-0001 | Aqueous Ammonia Storage and Forwarding - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M19-10HAN-EL-WIR-0001 | HRSG Blowdown and Drain Tanks - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP
ALP-M19-10HAN-ME-CAL-0001 | HRSG Blowdown and Drain Tanks - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M19-10HAN-ME-DSH-0001 | HRSG Blowdown and Drain Tanks - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M19-10HAN-ME-GAD-0001 | HRSG Blowdown and Drain Tanks - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-WS, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M19-10HAN-ME-ITP-0001 | HRSG Blowdown and Drain Tanks - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M19-10HAN-ME-MDB-0001 | HRSG Blowdown and Drain Tanks - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M19-10HAN-ME-OMM-0001 | HRSG Blowdown and Drain Tanks - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-WS, G-OPS-HO-WS
ALP-M19-10HAN-ME-PRC-0001 | HRSG Blowdown and Drain Tanks - Supplier Installation and Erection Manual | 0 | 0 | 0 | 1 | G-CON-CWP
ALP-M19-10HAN-ME-TRP-0001 | HRSG Blowdown and Drain Tanks - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M19-10HAN-ME-TST-0001 | HRSG Blowdown and Drain Tanks - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M19-10HAN-PR-PID-0001 | HRSG Blowdown and Drain Tanks - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M20-00SGA-EL-WIR-0001 | Fire Pumps and Fire Protection Systems - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M20-00SGA-ME-CAL-0001 | Fire Pumps and Fire Protection Systems - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M20-00SGA-ME-DSH-0001 | Fire Pumps and Fire Protection Systems - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M20-00SGA-ME-GAD-0001 | Fire Pumps and Fire Protection Systems - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M20-00SGA-ME-ITP-0001 | Fire Pumps and Fire Protection Systems - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M20-00SGA-ME-MDB-0001 | Fire Pumps and Fire Protection Systems - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M20-00SGA-ME-OMM-0001 | Fire Pumps and Fire Protection Systems - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 4 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M20-00SGA-ME-PRC-0001 | Fire Pumps and Fire Protection Systems - Supplier Installation and Erection Manual | 0 | 0 | 0 | 2 | G-CON-CWP
ALP-M20-00SGA-ME-TRP-0001 | Fire Pumps and Fire Protection Systems - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M20-00SGA-ME-TST-0001 | Fire Pumps and Fire Protection Systems - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-M20-00SGA-PR-PID-0001 | Fire Pumps and Fire Protection Systems - Supplier P&IDs | 0 | 0 | 0 | 2 | G-OPS-AB, G-PRC-FAB
ALP-M21-00SMA-EL-WIR-0001 | EOT Cranes - Supplier Electrical Schematics and Wiring Diagrams | 0 | 0 | 0 | 3 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP
ALP-M21-00SMA-ME-CAL-0001 | EOT Cranes - Supplier Design Calculations | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M21-00SMA-ME-DSH-0001 | EOT Cranes - Supplier Certified Datasheets and Performance Curves | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M21-00SMA-ME-GAD-0001 | EOT Cranes - Supplier GA Drawings | 0 | 0 | 0 | 4 | G-COM-MC-FF, G-CON-CWP, G-CON-IWP, G-PRC-FAB
ALP-M21-00SMA-ME-ITP-0001 | EOT Cranes - Supplier Inspection and Test Plan | 0 | 0 | 0 | 1 | G-PRC-FAB
ALP-M21-00SMA-ME-MDB-0001 | EOT Cranes - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M21-00SMA-ME-OMM-0001 | EOT Cranes - Supplier Operation and Maintenance Manual | 0 | 0 | 0 | 2 | G-COM-SC-FF, G-OPS-HO-FF
ALP-M21-00SMA-ME-PRC-0001 | EOT Cranes - Supplier Installation and Erection Manual | 0 | 0 | 0 | 2 | G-CON-CWP
ALP-M21-00SMA-ME-TRP-0001 | EOT Cranes - Factory Acceptance Test Report | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-M21-00SMA-ME-TST-0001 | EOT Cranes - Factory Acceptance Test Procedure | 0 | 0 | 0 | 1 | G-PRC-FAT
ALP-P01-00000-ME-MDB-0001 | Piping Bulk Materials - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-P02-10LBA-ME-MDB-0001 | Alloy Piping P91 / P22 - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-P03-00000-ME-MDB-0001 | Valves - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-P04-00PAB-ME-MDB-0001 | GRP CW Pipes and Fittings - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-P05-00000-ME-MDB-0001 | Pipe Supports, Spring Hangers and Snubbers - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-P06-00000-ME-MDB-0001 | Piping Specialty Items - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-P07-00000-ME-MDB-0001 | Safety and Relief Valves - Manufacturing Record Book and Conformity Certificates | 0 | 0 | 0 | 1 | G-PRC-SHP
ALP-S01-00UAC-SS-STL-0001 | GIS Building - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UBA-SS-STL-0001 | Electrical Building - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UBF-SS-STL-0001 | Transformer Bays - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UCA-SS-STL-0001 | Control Building - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UEG-SS-STL-0001 | LDO Tank Farm Structures - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UEK-SS-STL-0001 | Gas Station Structures - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UGA-SS-STL-0001 | Water Treatment Building and Basins - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UPC-SS-STL-0001 | CW Pump House - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UQA-SS-STL-0001 | Utility Building - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00USA-SS-STL-0001 | Workshop and Warehouse - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UYA-SS-STL-0001 | Administration Building - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UZD-SS-STL-0001 | Pipe Racks and Pipe Sleepers - Steel Fabrication and Erection Drawings, Part 1 of 2 | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UZD-SS-STL-0002 | Pipe Racks and Pipe Sleepers - Steel Fabrication and Erection Drawings, Part 2 of 2 | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-00UZF-SS-STL-0001 | Temporary Barge Landing - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-10UMA-SS-STL-0001 | Gas Turbine Hall - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP
ALP-S01-20UMB-SS-STL-0001 | Steam Turbine Hall - Steel Fabrication and Erection Drawings | 0 | 0 | 0 | 2 | G-CON-CWP, G-CON-IWP

## Gate rules
Alpilla 600 MW Combined Cycle Power Plant - Gate rules (gate_rule records)
engine release_control v1.2.0 ¦ generated 2026-09-29T02:52:27Z by SETUP ¦ data 6d73bc5813f68e2b ¦ planned dates from the levelled workflow network and the CPM (working days)
Gate | Process | Scope | Title | Description | Requires | Need | Offset wd | Filter | Basis | Status
G-COM-MC-EL | Commissioning / acceptance | system | Mechanical Completion of the System before Back-Feed | electrical systems; need: back-feed energisation KD-010 - 60 wd | construction? IFC rule:DL-CM-TOD IFR | activity:KD-010 | -60 | electrical_hv electrical_mv_lv common | decision:DEC-EPCE-0013 requirement:ER-16.01 | agreed
G-COM-MC-FF | Commissioning / acceptance | system | Mechanical Completion of the System before GT First Fire | fuel, GT and auxiliary systems; need: GT first fire KD-020 - 60 wd | construction? IFC rule:DL-CM-TOD IFR | activity:KD-020 | -60 | fuel_gas gas_turbine generator auxiliary_mechanical cooling water_treatment fire_protection i_and_c hvac hrsg other | decision:DEC-EPCE-0013 requirement:ER-16.01 | agreed
G-COM-MC-WS | Commissioning / acceptance | system | Mechanical Completion of the System before First Synchronisation | water-steam cycle systems; need: first CC synchronisation KD-030 - 60 wd | construction? IFC rule:DL-CM-TOD IFR | activity:KD-030 | -60 | water_steam_cycle condensate_feedwater steam_turbine | decision:DEC-EPCE-0013 requirement:ER-16.01 | agreed
G-COM-SC-EL | Commissioning / acceptance | system | Start of System Commissioning before Back-Feed | need: KD-010 - 40 wd | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR rule:DL-CM-TOD IFR | activity:KD-010 | -40 | electrical_hv electrical_mv_lv common | decision:DEC-EPCE-0013 requirement:ER-16.01 requirement:ER-17.04 | agreed
G-COM-SC-FF | Commissioning / acceptance | system | Start of System Commissioning before GT First Fire | need: KD-020 - 40 wd | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR rule:DL-CM-TOD IFR | activity:KD-020 | -40 | fuel_gas gas_turbine generator auxiliary_mechanical cooling water_treatment fire_protection i_and_c hvac hrsg other | decision:DEC-EPCE-0013 requirement:ER-16.01 requirement:ER-17.04 | agreed
G-COM-SC-WS | Commissioning / acceptance | system | Start of System Commissioning before First Synchronisation | need: KD-030 - 40 wd | rule:DL-CM-CMP¦rule:DL-V-CMP@mr? ACCEPTED rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFR rule:DL-CM-TOD IFR | activity:KD-030 | -40 | water_steam_cycle condensate_feedwater steam_turbine | decision:DEC-EPCE-0013 requirement:ER-16.01 requirement:ER-17.04 | agreed
G-CON-CWP | Construction | cwp | CWP Release | documents of the first IWPs IFC, installation manuals issued | ewp-first? IFC any:ewp-all IFC rule:DL-V-ERC@mr? IFR | cwp_start |  |  | clarification:TQ-037 decision:DEC-EPCE-0013 | agreed
G-CON-IWP | Construction | cwp | Progressive IWP Documents Issued for Construction | isometrics, supports, schematics, loops | ewp-all IFC | cwp_mid |  |  | clarification:TQ-037 decision:DEC-EPCE-0013 | agreed
G-OPS-AB | Operations | plant | As-Built Documentation, 3D Model and Engineering Database | 3 months after Taking-Over | type:PID AB type:SLD AB type:ISO AB rule:DL-PI-LAY AB type:M3D@plant AB | activity:KD-040 | 65 |  | decision:DEC-EPCE-0013 requirement:ER-17.03 | agreed
G-OPS-HO-EL | Operations | system | Handover of the System to Operations | electrical systems | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC rule:DL-CM-TOD IFC | activity:KD-040 |  | electrical_hv electrical_mv_lv common | decision:DEC-EPCE-0013 requirement:ER-17.04 | agreed
G-OPS-HO-FF | Operations | system | Handover of the System to Operations | fuel, GT and auxiliary systems | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC rule:DL-CM-TOD IFC | activity:KD-040 |  | fuel_gas gas_turbine generator auxiliary_mechanical cooling water_treatment fire_protection i_and_c hvac hrsg other | decision:DEC-EPCE-0013 requirement:ER-17.04 | agreed
G-OPS-HO-WS | Operations | system | Handover of the System to Operations | water-steam cycle systems | rule:DL-CM-OPR¦rule:DL-V-OMM@mr? IFC rule:DL-CM-TOD IFC | activity:KD-040 |  | water_steam_cycle condensate_feedwater steam_turbine | decision:DEC-EPCE-0013 requirement:ER-17.04 | agreed
G-OWN-BDP | Owner acceptance | plant | Basic Design Package Batch 1 Approved | payment milestone MS-02 (TQ-038) | bdp:1 ACCEPTED | milestone:MS-02 |  |  | decision:DEC-EPCE-0013 requirement:ER-17.01 | agreed
G-OWN-BDP2 | Owner acceptance | plant | Basic Design Package Batch 2 Approved | payment milestone MS-13 (TQ-038) | bdp:2 ACCEPTED | milestone:MS-13 |  |  | clarification:TQ-038 decision:DEC-EPCE-0013 | agreed
G-OWN-TO | Owner acceptance | plant | Taking-Over | test reports accepted, O&M manual, spares and special tools lists, punch list | type:TRP@plant ACCEPTED id:ALP-EPC-00000-CM-OMM-0001 IFC id:ALP-EPC-00000-CM-LST-0002 IFC type:LST@plant IFR | activity:KD-040 |  |  | contract_clause:ALP-EPC-001_11.1 decision:DEC-EPCE-0013 requirement:ER-17.06 | agreed
G-OWN-TOC | Owner acceptance | plant | Tests on Completion Procedures Approved | 90 days before the tests | id:ALP-EPC-00000-CM-CMP-0001 ACCEPTED id:ALP-EPC-00000-CM-CMP-0002 ACCEPTED id:ALP-EPC-00000-CM-CMP-0003 ACCEPTED id:ALP-EPC-00000-CM-CMP-0004 ACCEPTED id:ALP-EPC-00000-CM-CMP-0005 ACCEPTED id:ALP-EPC-00000-CM-CMP-0006 ACCEPTED | activity:KD-030 | -65 |  | contract_clause:ALP-EPC-001_10.1 decision:DEC-EPCE-0013 requirement:ER-16.04 | agreed
G-PRC-ENQ | Procurement | mr | Enquiry Issued to Bidders |  | type:SPC@epc IFR type:MRQ@epc IFR | enquiry |  | equipment bulk subcontract | decision:DEC-EPCE-0013 requirement:ER-15.02 | agreed
G-PRC-FAB | Procurement | mr | Manufacturing Release | certified supplier data accepted | rule:DL-V-GAD¦rule:DL-V-DSH? ACCEPTED rule:DL-V-PID? ACCEPTED rule:DL-V-CAL? ACCEPTED rule:DL-V-FDL? ACCEPTED rule:DL-V-ITP? ACCEPTED | fabrication |  | equipment iec_supply | decision:DEC-EPCE-0013 requirement:ER-15.02 | agreed
G-PRC-FAT | Procurement | mr | Factory Acceptance Test | procedure approved | rule:DL-V-FAT ACCEPTED | shipment | -20 | equipment iec_supply | decision:DEC-EPCE-0013 requirement:ER-15.03 | agreed
G-PRC-PO | Procurement | mr | Purchase Order Award |  | type:SPC@epc IFC type:MRQ@epc IFC rule:DL-MR-TBE IFR type:ITP@epc? IFR | po |  | equipment bulk subcontract | decision:DEC-EPCE-0013 requirement:ER-15.02 | agreed
G-PRC-SHP | Procurement | mr | Release for Shipment |  | rule:DL-V-FTR? ACCEPTED rule:DL-V-MDB IFR | shipment |  | equipment iec_supply bulk | decision:DEC-EPCE-0013 requirement:ER-15.03 requirement:ER-15.04 | agreed